2006 Reliability Study Scope Document

# Purpose of Study

The purpose of this study is to assess the Progress Energy Carolinas (PEC) and Duke transmission systems’ reliability and develop a single reliability transmission plan for North Carolina that ensures reliability of service in accordance with NERC, SERC, PEC and Duke requirements.

Overview of the Study Process Scope

The scope of the proposed reliability study process will include the following steps:

- Assumptions

- Study assumptions selected

- Study Criteria

- Establish the criteria by which the study results will be measured

- Case Development

- Determine the different resource supply scenarios to evaluate

- Methodology

- Determine the methodologies that will be used to carry out the study

- Technical Analysis and Study Results

- Perform the study analysis (thermal, voltage, stability and short circuit) and produce the results

- Assessment and Problem Identification

- Evaluate the results to identify problems / issues

- Solution Development

- Identify potential solutions to the problems / issues

- Test the effectiveness of the potential solutions through additional studies (thermal, voltage, stability, short circuit) and modify the solutions as necessary such that all reliability criteria are met

- Perform financial analysis and rough scheduling estimate for each of the proposed solutions (e.g., cost, cash flow, present value, incremental impacts on transmission rates)

#### Selection of Preferred Reliability Plan

- Compare alternatives and select the preferred solution alternatives – balancing cost / benefit / risk

- Select a preferred set of transmission improvements that provide a reliable transmission system to customers most cost effectively while prudently managing the associated risks

- Report on the Study Results

- Prepare a report on the recommended final plan

- Each of these study steps is described in more specific detail below.

# Assumptions

The specific assumptions selected for this study are:

- The year to be studied (study year) will be 2011 Summer and 2010/2011 Winter (winter as needed).

- Each Load Serving Entity (LSE) will provide a resource dispatch order for each of its Designated Network Resources in PEC and Duke. Generation will be dispatched for each LSE in the cases to meet that LSE’s peak load in accordance with the designated dispatch order. LSEs will also include generation down scenarios for their resources, if applicable (e.g., generation outage with description of how generation will be replaced, such as by that LSE’s dispatch order).

- PSS/E and/or MUST will be used for the study.

- Load growth assumptions will be in accordance with each LSE’s practice.

- Generation, interchange and other assumptions will be coordinated between Participants as needed.

- For a variety of reasons (such as load growth, generation retirements, or power purchase agreements expiring), some LSEs may wish to evaluate other resource supply options to meet future load demand. In this case, the Planning Working Group (PWG) will solicit input from the Participants for different scenarios on where to include other supply resources to meet their load demand forecasts in the study. These resource supply options can be either in the form of transactions or some “fictitious” generators which are added to meet the resource adequacy requirements for this study. The PWG will analyze the proposed interchange transactions and/or the location of the fictitious generators to determine if those transactions or generators create any reliability criteria violations. Based on this analysis, the PWG will provide feedback to the Participants on the viability of the proposed interchange transactions or fictitious generator locations for meeting future load requirements.

# Study Criteria

The study criteria with which results will be evaluated will be established, promoting consistency in the planning criteria used across the systems of the Participants, while recognizing differences between individual systems. This study criteria will include the following reliability elements:

- NERC Reliability Standards

- SERC requirements

- Individual company criteria (voltage, thermal, stability, short circuit, and phase angle)

# Case Development

- The most current MMWG or VSTE model will be used for the systems external to Duke and PEC as a starting point for the Base Case to be used by both PEC and Duke in their analyses.

- The Base Case will include the detailed internal models for PEC and Duke and will include current transmission additions planned for in-service for the given year. (i.e. in-service by summer 2011 for 2011S cases and in-service by the winter for 2010/2011 for  2010/2011W cases.)

- An “All Firm Transmission” Case(s) will be developed which will include all confirmed long term firm transmission reservations with roll-over rights applicable to the study year

- Duke and PEC will each create their respective generation down cases from the common Base Case) and share the relevant cases with each other.

- Additional cases will be developed as required for different scenarios to evaluate other options to meet load demand forecasts in the study.

# Methodology

- Initially, load flow analyses will be performed based on the assumption that thermal limits will be the controlling limit for the reliability plan. Voltage, stability, short circuit and phase angle studies may be performed if circumstances warrant.

- PEC and Duke will exchange contingency and monitored element files so that each can test the impact of contingencies on the other’s transmission system.

# Technical Analysis and Study Results

The technical analysis will be performed in accordance with the study methodology. Results from the technical analysis will be reported throughout the study area to identify transmission elements approaching their limits such that all Participants are aware of potential issues and appropriate steps can be identified to correct these issues, including the potential of identifying previously undetected problems.

PEC and Duke will report results throughout the study area based on:

- Thermal loadings greater than 90%.

- Voltages less than 100% for 500 kV and less than 95% for 230 kV buses; pre- to post-contingency voltage drops of 5% or more; voltages outside of requirements at nuclear facilities.

- Post-contingency voltage angle difference of Richmond-Newport 500 kV Line or other selected facilities.

# Assessment and Problem Identification

Duke and PEC will each run their own assessments. Duke reliability criteria will be used for Duke’s transmission facilities, and PEC reliability criteria will be used for PEC’s transmission facilities.  Duke and PEC will each document the reliability problems resulting from their assessments.

# Solution Development

- The PWG will develop potential solution alternatives to the identified reliability problems.

- Duke and PEC will test the solution alternatives using the same cases, methodologies, assumptions and criteria described above to test the effectiveness of the potential solutions.

- Duke and PEC will develop rough, planning level cost estimates and construction schedules for the solution alternatives.

#### Selection of Preferred Reliability Plan

- The PWG will compare alternatives and select the preferred solution alternatives, balancing cost / benefit / risk.

- The PWG will select a preferred set of transmission improvements that provide a reliable and the most cost effective transmission solution to meet customers’ needs while prudently managing the associated risks

# Report on the Study Results

The PWG will compile all the study results and prepare a recommended final plan for the OSC review and approval. The report should include a comprehensive summary of all the study activities as well as the recommended transmission improvements including estimates of costs and construction schedules.