2006

Collaborative

Transmission

Plan

DRAFT 11/22/06

Table of Contents

I.	Executive Summary	1

II.	North Carolina Transmission Planning Collaborative Process	1

II.A.	Overview of the Process	1

II.B.	Reliability Planning Process	2

II.C.	Enhanced Transmission Access Planning Process	2

II.D.	Collaborative Transmission Plan	4

III.	2006 Reliability Planning Study Scope & Methodology	4

III.A.	Assumptions	7

III.B.	Study Criteria	8

III.C.	Case Development	8

III.D.	Transmission Reliability Margin	9

III.E.	Technical Analysis and Study Results	9

III.F.	Assessment and Problem Identification	11

III.G.	Solution Development	11

III.H.	Selection of Preferred Reliability Solutions	11

III.I.	Contrast NCTPC report to other regional transfer assessments	12

IV.	Reliability Study Results	12

IV.A.	Phase Angle Richmond-Newport 500 kV Line	12

IV.B.	Base Reliability Study	13

IV.C.	600 MW Resource Supply Option Studies	13

IV.D.	1200 MW Resource Supply Option Studies	15

V.	Reliability Plan	16

V.A.	Base Reliability Plan	16

V.B.	Resource Supply Options Summary	17

VI.	Collaborative Transmission Plan	17

VII.	Conclusions	18

Appendix A:	Interchange Tables

Appendix B:	Collaborative Transmission Plan Project Listing

Appendix C:	Collaborative Transmission Plan Project Descriptions

Appendix D:	Projects Investigated for Resource Supply Options Studied

Appendix E:	List of Acronyms

# Executive Summary

[NOTE:  To be developed.]

# North Carolina Transmission Planning Collaborative Process

## Overview of the Process

The North Carolina Transmission Planning Collaborative (“NCTPC”) Process was established by Duke Energy Carolinas, Progress Energy Carolinas, Inc., North Carolina Electric Membership Corporation and ElectriCities of North Carolina (the “Participants”) to:

- provide the Participants and other stakeholders an opportunity to participate in the electric transmission planning process for the state of North Carolina;

- preserve the integrity of the current reliability and least-cost planning processes;

- expand the transmission planning process to include analysis of increasing transmission access to supply resources inside and outside the control areas of Duke Energy Carolinas (“Duke”) and Progress Energy Carolina (“Progress”); and

- develop a single coordinated transmission plan for North Carolina that includes reliability and enhanced transmission access considerations while appropriately balancing costs, benefits and risks associated with the use of transmission and generation resources.

- The overall NCTPC Process includes the Reliability Planning and Enhanced Transmission Access Planning (“ETAP”) processes, whose studies are intended to be concurrent and iterative in nature.  The NCTPC Process is designed such that there will be considerable feedback and iteration between the two processes as each effort’s solution alternatives affect the other’s solutions.

The Oversight Steering Committee (“OSC”) manages the NCTPC Process.  The Planning Working Group (“PWG”) supports the development of the NCTPC Process and coordinates the study development.  The Transmission Advisory Group (“TAG”) provides advice and makes recommendations regarding the development of the NCTPC Process and the study results.

The purpose of the NCTPC Process is more fully described in the Participation Agreement which is posted at http://www.nctpc.org/nctpc/listDocument.do?catId=REF.  Figure 1 illustrates the major steps associated with the NCTPC Process.

## Reliability Planning Process

- The Reliability Planning Process is the transmission planning process that has traditionally been used by the transmission owners to provide safe and reliable transmission service at the lowest reasonable cost.  This transmission planning process is being expanded to include the active participation of the Participants and input from other stakeholders through the TAG.

The Reliability Planning Process is designed to follow the steps outlined in Figure 1.  The OSC approves the scope of the reliability study, oversees the study analysis being performed by the PWG, evaluates the study results, and approves the final reliability study results.  The Reliability Planning Process begins with the incumbent transmission owners’ most recent reliability planning studies and planned transmission upgrade projects.

In addition, the PWG solicits input from the Participants for different scenarios on where to include alternative supply resources to meet their load demand forecasts in the study.  This step provides the opportunity for the Participants to propose the evaluation of other resource supply options to meet future load demand due to load growth, generation retirements, or purchase power agreement expirations.  The PWG will analyze the proposed interchange transactions and/or the location of generators to determine if those transactions or generators create any reliability criteria violations.  Based on this analysis, the PWG will provide feedback to the Participants on the viability of the proposed interchange transactions or generator locations for meeting future load requirements.  The PWG coordinates the development of the reliability studies and the resource supply option studies based upon the OSC-approved scope and prepares a report with the recommended transmission reliability solutions.

The final results of the Reliability Planning Process includes summaries of the estimated costs and schedules to provide any transmission upgrades and/or additions: (i) needed to maintain a sufficient level of reliability necessary to serve the native load of all Participants; and (ii) needed to reliably support the resource supply options studied.  The reliability study results are reviewed with the TAG.

## Enhanced Transmission Access Planning Process

The ETAP Process evaluates the means to increase transmission access for Load Serving Entities (“LSEs”) in North Carolina to potential network resources inside and outside the control areas of Duke and Progress.  The ETAP Process follows the steps outlined in Figure 1.  The OSC approves the scope of the ETAP study (including any changes in the assumptions and study from those used in the reliability analysis), oversees the study analysis being coordinated by the PWG, evaluates the study results, and approves the final ETAP study results.

Figure 1

NCTPC Process Flow Chart

PWG evaluates reliability problems and current transmission upgrade plans

PWG develops and the OSC approves the reliability study scope

PWG coordinates the study analysis, identifies reliability problems, develops solutions with estimates of costs and schedules

Participants and TAG recommend scenarios and interfaces.   The OSC selects interface and scenario studies for analysis

PWG coordinates the study analysis, identifies access problems, develops solutions with estimates of costs and schedules

Reliability Planning

Enhanced Transmission Access Planning

OSC selects reliability and enhanced access solutions; checks for improved reliability through enhanced access solutions

OSC creates final draft Collaborative Plan

Feedback and Iterative Studies

Participants and TAG review the reliability study results

Participants’ resource planning processes

Participants and TAG review the enhanced access study results

TAG feedback on final draft Collaborative Plan

OSC approves final Collaborative Plan

PWG develops and the OSC approves the  enhanced access study scope

The ETAP Process begins with the Participants and TAG members proposing scenarios and interfaces to be studied.  The proposed scenarios and interfaces are compiled by the PWG and then evaluated by the OSC to determine which ones will be included for analysis in the current planning cycle.  The PWG coordinates the development of the enhanced transmission access studies based upon the OSC-approved scope and prepares a report which identifies recommended transmission solutions that could increase transmission access.

The final results of the ETAP Process include the estimated costs and schedules to provide the increased transmission capabilities.  The enhanced transmission access study results are reviewed with the TAG.

## Collaborative Transmission Plan

Once the reliability and ETAP studies are completed, the OSC evaluates the results and the PWG recommendations to determine if any proposed enhanced transmission access projects and/or resource supply option projects will be incorporated into the final plan.  If so, the initial reliability plan is modified accordingly.  This process results in a single Collaborative Transmission Plan being developed that appropriately balances the costs, benefits and risks associated with the use of transmission and generation resources.  The final plan is reviewed with the TAG.

The Collaborative Transmission Plan information is available for Participants to identify any alternative least cost resources to include with their respective Integrated Resource Plans.  Other stakeholders can similarly use this information for their resource planning purposes.

# 2006 Reliability Planning Study Scope & Methodology

The 2006 Reliability Planning Process included a base reliability study and analysis of resource supply options.  The base reliability study assessed the reliability of the transmission systems of both Duke and Progress in order to develop a single base reliability plan for the Duke and Progress transmission systems that ensures reliability of service in accordance with NERC, SERC, Duke and Progress requirements.  The purpose of the base reliability study was to evaluate the transmission system’s ability to meet load growth with existing resource plans and the Participants’ Designated Network Resources projected for 2011.

The purpose of the resource supply analysis was to evaluate transmission system impacts for various uncommitted resource supply options to meet future native load requirements.  The PWG developed resource supply scenarios based on Participant input from NCMPA1, NCEMPA, Fayetteville Public Works Commission, NCEMC, Waynesville, Stantonsburg, Lucama, Black Creek, Forest City/Dallas and Concord.  The analysis of these scenarios identified transmission issues and investigated solutions using the proposed alternative supply resources to serve the Participants’ load.  Table 1 is a list of the resource supply option scenarios studied.

Table 1

List of Resource Supply Options Studied

| Resource From | Sink | Sink | Net Requests (MW) | Test Level (MW) |
| --- | --- | --- | --- | --- |
| NORTH – PJM (AEP) | Duke |  | 473 | 600 |
| WEST – TVA | Duke |  | 464 | 600 |
| SOUTH – SOCO | Duke |  | 564 | 600 |
| SOUTH – SCEG | Duke |  | 464 | 600 |
| SOUTH – SCPSA | Duke |  | 464 | 600 |
| EAST – Progress | Duke |  | 464 | 600 |
| NORTH – PJM (AEP) |  | Progress (CPLE) | 535 | 600 |
| NORTH – PJM (DVP) |  | Progress (CPLE) | 535 | 600 |
| SOUTH – SCEG |  | Progress (CPLE) | 600 | 600 |
| SOUTH – SCPSA |  | Progress (CPLE) | 500 | 600 |
| WEST – Duke |  | Progress (CPLE) | 464 | 600 |
| NORTH – PJM (AEP/AEP) | Duke | Progress (CPLE) | 1,008 | 600 / 600 |
| NORTH – PJM (AEP/DVP) | Duke | Progress (CPLE) | 1,008 | 600 / 600 |
| NORTH – PJM (AEP) |  | Progress (CPLW) | 20 | 20 |

As shown in Table 1, optional imports requested by the Participants totaled between 450 MW and 600 MW above base case imports from each neighboring interface with either Duke’s control area or Progress’ eastern control area (CPLE).  The last row of Table 1 shows one request to study an additional 20 MW of imports above the base case into Progress’ western control area (CPLW).  Each row in Table 1 represents a single scenario.  For simplicity, the net requests were rounded to 600 MW for all scenarios except the scenario importing into CPLW.  The PWG decided to study a scenario with simultaneous 600 MW transfers from PJM to both Duke and CPLE because of concern that the possibility of such a large transfer from north to south could potentially stress the transmission system.  Two different scenarios were run for PJM since Duke ties directly to PJM via AEP while Progress ties to PJM via both AEP and DVP.

The 2006 NCTPC Process did not include enhanced transmission access studies.  At the TAG meeting in February 2006, the OSC presented the TAG stakeholders with an overview of the ETAP Process.  One of the initial steps in the ETAP Process was to solicit input from stakeholders on what scenarios and interfaces they would recommend to be studied as part of the development of the 2006 NC Collaborative Transmission Plan.  The OSC did not receive any input from the TAG stakeholders. As a result, the OSC decided that for the development of the 2006 NC Collaborative Transmission Plan it would focus all its resources on the Reliability Planning Process.  The ETAP Process will still be included as part of the development of the 2007 NC Collaborative Transmission Plan; and input will be solicited from the stakeholders as part of the 2007 NCTPC Process.  Figure 2 illustrates the revised steps for the 2006 NCTPC Process.

Figure 2

2006 NCTPC Process Flow Chart - Revised

PWG evaluates reliability problems and current transmission upgrade plans

PWG develops and the OSC approves the reliability study scope

PWG coordinates the study analysis, identifies reliability problems, develops solutions with estimates of costs and schedules

Reliability Planning

OSC selects reliability and enhanced access solutions; checks for improved reliability through enhanced access solutions

OSC creates final draft Collaborative Plan

Feedback and Iterative Studies

Participants and TAG review the reliability study results

Participants’ resource planning processes

TAG feedback on final draft Collaborative Plan

OSC approves final Collaborative Plan

## Assumptions

### Study Year and Planning Horizon

The plan addresses a 10 year planning horizon.  The study year chosen for the 2006 NCTPC study was 2011.  Results were extrapolated from the results of the analysis performed on the 2011 cases by increasing flows by 2% per year on Duke facilities and 2.5% per year on Progress facilities to estimate the results through 2016, the end of the planning horizon.

Progress operates and plans for two separate control areas: (i) CPL-East (summer peaking) and (ii) CPL-West (winter peaking).  Studies of Duke and CPL-East systems were performed on 2011 summer cases.  Studies for CPL-West were performed on 2010/2011 winter case.

### Network Modeling

The load, generation and transmission system configuration included as part of the Duke and Progress system model represents the current transmission plan for the 2011 summer and 2010/2011 winter periods.  Duke and Progress control area load will be served by a combination of native generation and imported power.  Duke’s generation capacity and transmission facility additions planned for development at Cliffside Steam Station by 2011 were included in the models.  Future generation in the Progress model includes Anson (2007), Richmond (2007) and Wayne County (2008), all combustion turbines.

### Interchange and Generation Dispatch

- Each Participant provided a resource dispatch order for each of its Designated Network Resources for the Duke and Progress control areas.  Generation was dispatched for each Participant to meet that Participant’s peak load in accordance with the designated dispatch order.

- Interchange in the summer and winter base cases were set according to the resources identified outside the Duke and Progress control areas.  Interchange tables for the summer and winter base cases and the summer and winter Progress Transmission Reliability Margin cases, discussed in Section III.D, are in Appendix A.  For resource supply option cases, the sink and source control area interchange was modified to accommodate the import from the prescribed control area.  The source control area’s generation was scaled to allow the export and the Duke and/or Progress control area was economically re-dispatched to accept the import of energy.

## Study Criteria

The results of the base reliability study and the resource supply option study were evaluated using established planning criteria, while recognizing differences between the systems of Duke and Progress.  The planning criteria used to evaluate the results include:

- NERC Reliability Standards;

- SERC requirements; and

- Individual company criteria.

As part of the NCTPC Process, the planning criteria and reliability assumptions used by Duke and Progress were compared to determine the similarities and differences between their individual transmission planning processes.  For the 2006 NCTPC Process, Duke criteria was used to evaluate the Duke transmission system, and Progress criteria was used to evaluate the Progress transmission system.  For the 2007 NCTPC Process, the PWG will again review the differences between the individual planning criteria and reliability assumptions and may recommend changes as the NCTPC Process goes forward.

## Case Development

The base case for the base reliability study was developed using the most current 2005 VSTE model for the systems external to Duke and Progress.  Detailed internal models of the Duke and Progress East/West systems were merged into the base case, including Duke and Progress transmission additions planned to be in-service by the period under study.  In the base cases, all confirmed long term firm transmission reservations with roll-over rights were modeled, as applicable.

It should be noted that the external VSTE model follows the NERC MMWG criteria regarding the inclusion of transmission reservations which includes modeling known long term firm reservations.

The base case was the starting point for creating resource supply option cases.  Resource supply option cases for the scenarios in Table 1 were modeled as an incremental import to the base cases developed.  Cases were developed for:

Summer 2011

- With an incremental import of 600 MW to the Duke system;

- With an incremental import of 600 MW to the Progress east system; and

- With both an incremental import of 600 MW to Duke and an incremental import of 600 MW to the Progress east system.

Winter 2010/2011

- With an incremental import of 20 MW to the Progress west system.

## Transmission Reliability Margin

NERC defines Transmission Reliability Margin (“TRM”) as:

The amount of transmission transfer capability necessary to provide reasonable assurance that the interconnected transmission network will be secure.  TRM accounts for the inherent uncertainty in system conditions and the need for operating flexibility to ensure reliable system operation as system conditions change.

Progress’ reliability planning studies model all confirmed transmission obligations for its control area in its base case.  Included in this is TRM for use by all LSEs and utilized in generation down studies.  TRM is composed of contracted reserve sharing, parallel path flow, and system inrush response to the sudden loss of generation.  Progress models the import of TRM by scheduling the reserved amount on actual reserved interfaces as posted on OASIS.

Duke ensures VACAR reserve sharing requirements can be met through set aside of transmission capacity when performing ATC calculations.  Sufficient capacity is maintained on all Duke-VACAR interfaces to allow both export and import of the required VACAR reserves in addition to the capacity reserved for transmission service.

## Technical Analysis and Study Results

Duke and Progress performed contingency screenings on the base case and on the resource supply option cases using PSS/E power flow.  Each company simulated its own transmission and generation down contingencies on its own transmission system.

Generator contingencies for Duke assumed generation maintenance.  Duke creates generator maintenance cases that assume a major unit is removed from service and the system is economically re-dispatched to make up for the loss of generation.

The generator contingency cases developed are:

Allen 4			Allen 5			Bad Creek 1

Belews Creek 1		Buck 5			Catawba 1

Cliffside 3			Cliffside 5		Dan River 3

Jocassee 1		Lee 3			Marshall 3

McGuire 1			McGuire 2		Oconee 1

Oconee 3			Riverbend 6		Riverbend 7

This creates a portfolio of cases to allow testing the transmission system under stressed conditions.  Progress generation down case studies include the use of TRM, as discussed in Section III.D, simulated with different large generator outages.  Generation down cases were developed from the base case and from the resource supply option cases.  The following Progress generation down cases were developed from the base case:

- Harris nuclear unit;

- Brunswick nuclear unit;

- Anson combustion turbine plant;

- Blewett and Tillery hydro plants;

- Roxboro coal unit; and

- Asheville coal unit (for Progress west system studies).

The generation down cases that were developed from the resource supply option cases were limited to backing down those units that had the most significant impact on the results of the base case, typically a Harris or Brunswick unit.

To understand regional impacts on each other’s systems, Duke and Progress also exchanged their transmission contingency and monitored element files in order for each to simulate the impact of the other company’s contingencies on its own transmission system.  Also, each company simulated its own transmission contingencies with the other company generation down scenario to understand the impact of major unit outages.

The technical analysis was performed in accordance with the study methodology.  The results from the technical analysis for the Duke and Progress systems were shared with all Participants.  Solutions of known issues within Duke and Progress were discussed.  New or emerging issues identified in the 2006 NCTPC Reliability Study were also discussed with all Participants so that all are aware of potential issues.  Appropriate solutions were jointly developed and tested.

Progess and Duke reported results throughout the study area based on:

- 1)  Thermal loadings greater than 90% for base reliability, and greater than 70% for resource supply options to allow evaluation of project acceleration.

- 2)  Voltages less than 100% for 500 kV buses and less than 95% for 230 kV buses; pre- to post-contingency voltage drops of 5% or more; voltages outside of requirements at nuclear facilities.

- 3)  Post-contingency phase angle difference of Richmond-Newport 500 kV line.

Line loading results for 2011 were extrapolated into the future assuming a 2% per year growth in line loading for Duke facilities and 2.5% per year growth in line loading for Progress facilities.  This allowed assessment of transmission needs throughout the planning horizon.

In order to monitor the post-contingency phase angle difference of the Richmond-Newport 500 kV line in the analysis, the A, B, and C ratings of the line were set to 1350 MVA, the estimated flow that results in post contingency phase angle violations.

## Assessment and Problem Identification

Duke and Progress each performed their own assessments.  Duke’s reliability criteria were used for Duke’s transmission facilities; and Progress’ reliability criteria were be used for Progress’ transmission facilities.  Duke and Progress each documented the reliability problems resulting from their assessments of both the base reliability cases and the resource supply option scenarios.

## Solution Development

The studies performed by the PWG confirmed base reliability problems already identified by Duke and Progress in company specific planning studies performed individually by Duke and Progress.  The PWG participated in the development of potential solution alternatives to the identified base reliability problems, if appropriate, and to the issues identified in the resource supply option analysis.  Duke and Progress simulated the solution alternatives using the same assumptions, criteria and cases described in Sections III.A through III.C, and developed rough, planning cost estimates and construction schedules for the solution alternatives.

## Selection of Preferred Reliability Solutions

For the base reliability plan, the PWG compared solution alternatives and selected the preferred solution, balancing cost, benefit and risk.  The PWG selected a preferred set of transmission improvements that provide a reliable and cost effective transmission solution to meet customers’ needs while prudently managing the associated risks.

For the resource supply options, alternatives were identified for each interface import scenario.  Additional analysis would be required to determine the optimal set of projects that best meet system needs for each scenario.  While it is still up to all of the Participants in the study process to develop their own resource supply plans for the future, the NCTPC process offers a valuable way to assess the transmission impacts of these resource supply options in conjunction with other Participants [and stakeholders] for the time period being studied.  The primary transmission solution alternatives resulting from this process will help complement each LSE’s planning process and provide valuable system information related to future resource supply needs.  Although transmission service for these resources must still be requested and obtained via the Open Access Same-time Information System (“OASIS”), the LSEs will have a much better idea of what to expect regarding potential transmission upgrades that may be required for resource scenarios before the transmission service request is made and the study results are provided.

## Contrast NCTPC report to other regional transfer assessments

For both the Duke and Progress control areas, the results of the PWG study are consistent with VSTE studies performed for similar time frames.  VSTE studies have recently been performed for 2008, 2011, and 2013 summer time frames.  The limiting facilities identified in the PWG study have been previously identified in the VSTE studies for similar scenarios, with the exception that is noted below.  These facilities have also been identified in Duke’s internal assessments required by NERC reliability standards.  The same is true for Progress with the exception that the phase angle issue on the Richmond-Newport 500 kV Line has not been identified through the VSTE process.  This issue will be described in detail below.

# Reliability Study Results

## Phase Angle Richmond-Newport 500 kV Line

The base reliability study confirmed the existence of a phase angle problem during periods of high import into the Progress Energy Carolinas eastern control area.  The angle problem develops when trying to close or open this approximately 80 mile long Richmond-Newport 500 kV interconnection between Duke and Progress.  It is imperative that the line be capable of being promptly reclosed after normal and fault operations in order to meet applicable reliability standards.  Synch-check relays on the line breakers are currently set to block reclosing when the angular difference across the breaker reaches 30 degrees.  Progress has determined through dynamic studies that closing the line with phase angles larger than 30 degrees creates an unacceptable sudden change of power on the generating units in the electrical vicinity of the Richmond 500 kV Substation.

Progress completed a study in April 2004 which described this issue and estimated the scope, schedule, and cost of a potential solution to this issue.  The study describes a traditional solution alternative of building additional 500 kV lines to mitigate the phase angle issue.  The study is posted on the Progress OASIS.

After confirming the existence of the phase angle issue, the PWG brainstormed an extensive list of possible solutions to the issue.  The list was developed for discussion purposes and for further follow-up.  At the June 27th OSC meeting Progress shared with the group that Progress had contacted KEMA, a local utility consultant, to gain an understanding of some technologies that were included in the PWG brainstorm list.  Several of the options in the brainstorm list utilized static series capacitors or reactors at various locations of the transmission system.  KEMA provided input on these and other alternatives including the use of FACTS devices.  KEMA focused on technology with the ability to address the switching issues on the 500 kV system under high power flow.  KEMA preliminarily recommended the use of a Thyristor Controlled Series Reactor (“TCSR”) due to its ability to quickly impact line flow on closing and opening switching operations.  While other TCSRs are in use in other parts of the country, none appear to be used for the switching issue Progress is seeking to address.  Progress stated its plans to further utilize KEMA in a Phase II effort to focus on the TCSR with regard to feasibility of solution, size, schedule, operation, and initial and ongoing cost.

The Phase II study report was released by KEMA on November 21, 2006.  After detailed study under normal and various fault operations the recommendation was made to pursue 500 kV manually-controlled reactors at the Richmond 500 kV Substation to mitigate the angle issue.  Progress is pursuing this project and currently plans to have the reactors in service by June of 2010.

## Base Reliability Study

The 2006 NCTPC Study verified that Duke and Progress have projects in place to address reliability concerns for the planning horizon.  For Progress, the 2006 study did identify the need for Progress to establish one new project to install a second Falls 230/115 kV transformer at its Falls 230 kV Substation in the Raleigh area.  This project has been included in Progress’ plans for 2013.  The study also indicated that Progress could delay its transformer upgrade in the Laurinburg area by 1-2 years.  Progress has delayed the project in its plans by one year.

Appendix B includes major projects planned by Duke and Progress.  Included for Progress is the Durham 500 kV project.  This project addresses increased contingency loading on the 500/230 kV banks at the Wake 500 kV Substation.  Progress is underway with this project which establishes 500 kV at the Durham 230 kV Substation.  To do this the Mayo-Wake 500kV line will be looped into Durham and one 500/230 kV bank will be installed reducing loading on the Wake banks.  Progress also has several projects in its plan for the Rockingham/Biscoe/Asheboro area.  The Cape Fear-Siler City 230 kV line will provide additional contingency voltage support for the Asheboro area. Projects associated with the Rockingham-West End 230 kV line and the new Rockingham-West End 230 kV East address issues with increased imports on Progress’ southern interface.

## 600 MW Resource Supply Option Studies

Prior to additional imports into Progress, the 500kV phase angle issue described in Section IV.A has to be resolved.  Once the phase angle is resolved, additional thermal issues will need to be addressed.  The PWG reviewed the thermal results for the 600 MW resource supply option studies.  The cost and projected in-service dates associated with projects required to enable each of the 600 MW resource supply options are provided in Table 2.   Appendix D provides detailed information on the estimated cost and schedule for transmission infrastructure needed to support these imports.  The results show that it may be difficult to meet a 2011 in-service date for the 600 MW resource supply option projects given the lead time to complete these projects. [NOTE:  Need to complete summary in Table 2 based on details in Appendix D.]

Table 2

Summary of Resource Supply Option Results

| Transfer From | Transfer To | Capacity (MW) | Earliest In-Service Date | Cost (2007$M) |
| --- | --- | --- | --- | --- |
| PJM (AEP) | Duke | 600 |  |  |
| TVA | Duke | 600 |  |  |
| SOCO | Duke | 600 |  |  |
| SCEG | Duke | 600 |  |  |
| SCPSA | Duke | 600 |  |  |
| CPLE | Duke | 600 |  |  |
| Duke | CPLE | 600 |  |  |
| SCEG | CPLE | 600 |  |  |
| SCPSA | CPLE | 600 |  |  |
| SOCO | CPLE | 600 |  |  |
| TVA | CPLE | 600 |  |  |
| PJM (AEP) | CPLE | 600 |  |  |
| PJM (DVP) | CPLE | 600 |  |  |
| PJM (AEP/AEP) | Duke/ CPLE | 600/600 |  |  |
| PJM (AEP/DVP) | Duke/ CPLE | 600/600 |  |  |
| PJM (AEP) | CPLW | 20 |  |  |

Highlights of the results show for Progress and Duke:

PEC Imports from the North (PJM-AEP and PJM-DVP):

- Problem: Overload of the Wake 500/230kV banks

Solution: Install 3rd Wake 500/230 kV transformer bank by 2011.

- Problem: Overload 230 kV lines in Durham/Cary area

Solution: Construction new Harris-Durham 230 kV line by 2011.

- Problem: Overload 230 kV lines in the Rockingham/Cape Fear and Asheboro/Biscoe areas

Solution: Construct new Buck-Asheboro 230 kV tie to Duke Energy by 2011.

PEC Imports from the South (SC and SCEG):

- Problem: Overload of the Wake 500/230kV banks

Solution: Install 3rd Wake 500/230 kV transformer bank by 2012.

- Problem: Overload 230 kV lines in Durham/Cary area

Solution: Construction new Harris-Durham 230 kV line by 2012.

- Problem: Overload 230 kV lines in the Rockingham/Cape Fear and Asheboro/Biscoe areas-

Solution: Construct new Buck-Asheboro 230 kV tie to Duke Energy 2011.

PEC Imports from West (Duke):

- Problem: Overload of the Wake 500/230kV banks

Solution: Install 3rd Wake 500/230 kV transformer bank by 2012.

- Problem: Overload 230 kV lines in Durham/Cary area

Solution: Construction new Harris-Durham 230 kV line by 2011.

- Problem: Overload 230 kV lines in the Rockingham/Cape Fear and Asheboro/Biscoe areas

Solution: Construct new Buck-Asheboro 230 kV tie to Duke Energy 2011.

- Problem: Overload of Duke’s Parkwood 500/230 kV transformers

Solution: Accelerate capacity upgrade

Duke Imports from North (PJM-AEP)

- Duke will continue to monitor the timing of the future transformer upgrades at the Antioch substation.

- Transformer replacement schedule would be advanced from 2014 if higher imports from the North occur.

Duke Imports from West (TVA)

- Planning model included an upgrade to the Nantahala-Robbinsville-Santeetlah 161 kV tie line and increased capacity to 596 MVA .

- No thermal limits were identified at the levels tested.

Duke Imports from South (SC, SCEG, SOCO)

- No thermal limits were identified at the levels tested.

## 1200 MW Resource Supply Option Studies

In August 2006, in response to emergent OASIS queue requests, the PWG recommended and the OSC approved incorporation of the emergent requests received by Progress and Duke as additional resource supply option studies.  The PWG scoped out the following approach to study the impact of the requests.  Using the previously created 2011 case with a 600 MW import from Duke to Progress East, the PWG created a 1,200 MW import case from Duke to Progress East.  The 1,200 MW import represents the following resource supply options from Duke into Progress East:

- 500 MW for Fayetteville;

- 400 MW for Progress; and

- 200 MW for NCEMC.

### A 100 MW redirect OASIS request by NCEMC for changing the source from AEP to Duke was also added to the models thus creating a 1,200 MW Duke to Progress East import case.

The PWG has commenced the 1200 MW Duke to Progress East studies but was not able to complete the analysis in time for this report.  The PWG plans to submit a supplement to this report in the first quarter of 2007.

# Reliability Plan

[NOTE:  The PWG has performed the base reliability study and the 600 MW resource supply options and has determined that there are 3 projects that are possibilities for incorporating into the final Collaborative Plan that were not in the base plan.  These projects are:

Buck-Asheboro 230 kV Interconnection

Harris – Durham 230 kV Line

Wake 500 kV Substation, Add #3 500/230 kV transformer

Sections V and VI of the attached report and Appendix B are currently written to include these 3 projects in the Collaborative Plan but the PWG believes that further analysis will be needed before it is ready to finalize this recommendation.

These 3 projects would address issues that had not been completely addressed in the 6 to 10 year time horizon of the base reliability plan and would be beneficial toward creating additional import capability as identified in the resource supply option studies.  At this time, however, the PWG has not had sufficient opportunity to fully explore the impact of these projects on reliability of both Progress and Duke nor have we determined what other projects could be eliminated from the base plan if these projects were incorporated.  In order to form a sufficient business case for support of these 3 projects we believe that a full reliability and cost impact analysis must be developed so that the OSC will have adequate data to make a decision on whether to include these projects in the Collaborative Plan.  The PWG is committed to gathering this data by December 15 for this purpose at which time it will be provided to the OSC.  The outcome of this analysis will assist the OSC in making the decision on whether or not to add these projects and on their proposed in-service dates.  It may also affect Sections V and VI of the report and Appendix B.]

## Base Reliability Plan

The 2006 NCTPC Study verified that Duke and Progress have projects in place to address reliability concerns for the planning horizon particularly in the 1 to 5 year period.  Some issues were identified on the Progress system that may need to be addressed in the 6 to 10 year period either with more aggressive operating procedures or new projects.  It should be noted that there is a significant amount of uncertainty in this time period as to the location of new generation sources.

## Resource Supply Options Summary

The issues identified and solutions investigated for the 600 MW resource supply option scenarios studied are listed in Appendix D.  The tables in Appendix D are intended to give an estimate of the cost and schedule impact in order to accommodate a new request to increase imports into either Progress or Duke by 600 MW in 2011.  The cost estimates provided reflect either the total cost of new projects needed solely for the import or the acceleration of an existing project already identified. The need date and lead time determine the estimated year the request could be accommodated.

# Collaborative Transmission Plan

Once the reliability and 600 MW resource supply options studies were completed, the PWG evaluated the results to determine if any proposed resource supply option projects would be incorporated into the final plan.  The PWG chose to include 3 projects that were identified during the resource supply option studies into the collaborative plan.  The 3 proposed projects are listed below:

- Buck-Asheboro 230 kV Interconnection

- Harris-Durham 230 kV Line

- Wake 500 kV Substation, Add #3 500/230 kV transformer

These 3 projects were not in the base reliability plan but they will address issues that had not been addressed in the 6 to 10 year time horizon of the reliability plan and will be beneficial toward creating additional import capability as identified in the resource supply option studies.

The collaborative transmission plan is currently comprised of the 14 projects with an estimated cost of $10M or more each.  These projects are listed in Appendix B.  The list will continue to be modified on an ongoing basis as new improvements are identified through the NCTPC process and projects are completed or eliminated from the list.  The list provides the following information for each project:

- Reliability Project:  Description of the project.

- Issue Resolved:  Specific driver for project.

- Status:  Status of development of the project as described below:

  - In Service – transmission facility is commissioned and in-service

  - Under Construction – the Transmission Owner has completed ROW acquisition, siting and permitting; the Transmission Owner is in the process of ordering equipment and hiring a contractor; or the transmission facility is actually under construction.

  - Committed – the project has some money in the budget for the current fiscal year for ROW acquisition, detailed design, surveys, geotechnical studies, siting and permitting efforts.

  - Planned – the project is in the base reliability plan within the first 5 year window of the 10 year planning horizon (or the project is a 500 kV line project that has a longer lead time in the base reliability plan), but is not in the Transmission Owner’s  budget for the current fiscal year yet. Subject to change, but, more confidence in the plan.

  - Proposed – the project is within the 6-10 year window of the 10 year planning horizon in the base reliability plan and is not budgeted yet, and is subject to significant change.

  - Concept – the project is not in the base reliability plan, but is a concept for addressing issues related to resource supply options, or issues beyond the 10 year planning horizon.

- Transmission Owner:  Responsible equipment owner designated to design and implement the project.

- Projected In-Service Date:  The date the project is expected to be placed in service.

- Estimated Cost:  Best estimate of the cost available.  The estimate accuracy may vary dependent on the maturity of the project.

- Projected Lead Time:  Number of years needed to complete project.

A detailed description of each of the 14 projects is provided in Appendix C.

This process results in a single Collaborative Transmission Plan being developed that appropriately balances the costs, benefits and risks associated with the use of transmission and generation resources.

# Conclusions

The benefits to be gained from a collaborative transmission planning process stem from the interdependent nature of adjoining network systems in terms of performance impacts, as well as the interdependent nature of transmission and resource planning.  For a transmission owner, a collaborative effort that provides information about a neighboring system is directly relevant to issues and potential issues in ones own system.  From a planning perspective, a collaborative effort that includes all LSEs, both transmission-owning and transmission-dependent, provides valuable information about projected loads and resources for transmission planning and information about transmission requirements for resource planning.  Through the course of implementing this collaborative planning process, the Participants’ PWG representatives confirmed the benefits of such joint planning.

First, the collaborative process was an educational process for PWG representatives.  Transmission planning practices, including similarities and differences in reliability planning assumptions, along with reliability results were shared and discussed within the group.  The working group became a forum for sharing technical and planning expertise to achieve a common goal.  For example, as reliability problems were documented and shared with the group, the PWG held brainstorming sessions to propose solutions to the problems identified.  Through this collaboration, potentially promising solutions that had not been considered previously by a transmission owner were identified and explored in greater detail.

Bringing all Participants together to address North Carolina’s transmission issues resulted in a more comprehensive model and analysis of the Duke and Progress transmission networks.  The PWG built a combined detailed model that incorporated improved generation dispatch assumptions relative to the assumptions that either transmission owner had available to them when they planned individually.  Duke and Progress exchanged contingency and monitored elements files such that each could test the impact of the neighboring system’s transmission and generation outages on their own systems.  Each owner’s generation down cases included modeling outages of key generators on the neighboring system.  A specific example of this showed how an outage of the largest Roxboro unit on Progress’ system could advance the need for a previously identified transmission project on Duke’s system.  This type of information is a direct result of the collaborative process, because it had not and would not have been identified in the separate transmission planning studies typically conducted.

A primary objective for the PWG in this planning process was to compare transmission solution alternatives and select the preferred alternatives, while appropriately balancing associated costs, benefits, and risks.  As a joint effort, this process took into consideration the costs, benefits, and risks to all LSEs, and therefore, delivered solution alternatives that benefited a larger mix of stakeholders than individual planning processes would have otherwise.  For example, solutions were evaluated not only in terms of whether they corrected the identified problem on one system, but also on whether they negatively impacted the adjoining system.  Scenarios were studied that not only addressed reliability for the base case resource options, but also for alternative resource options that could benefit LSEs otherwise limited in their choices of resource suppliers.  PWG representatives looked for comprehensive solutions that would best benefit multiple stakeholders, rather than piecemeal fixes that only satisfy the reliability requirements of the separate transmission systems.  The work of the PWG in this planning process provided concrete examples for Participants, both transmission-owning and transmission-dependent, of the benefits of collaboration.