Appendix D

Projects Investigated for Resource Supply Options Studied

DRAFT 11/22/06

| Projects Investigated for Increasing Imports Into PEC |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Duke 600 MW |  | SCEG 600 MW |  | SCPSA 600 MW |  | DVP 600 MW |  | SOCO 600 MW |  | TVA 600 MW |  | AEP 600 MW |  | AEP/AEP 1200 MW |  | AEP/DVP 1200 MW |  |
| Buck-Asheboro 230 kV line, Construct 50 mile line (2014 TAP Project-$50M) | Biscoe-Asheboro East 115 kV Rockingham - Anson 230 kV Blk Tillery-Biscoe 115 kV | PEC | 5 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 | 6/1/2011 | $25.00 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 | 6/1/2011 | $15.00 |
| Camden 230 kV Sub, Install 230 kV reactor on (SC) Lugoff terminal | Camden-Camden Junction 115 kV | PEC | 3 |  |  | 6/1/2012 | $5.10 | 6/1/2012 | $5.10 |  |  |  |  |  |  |  |  |  |  |  |  |
| Falls 230 kV Sub, Install #2 230/115 kV bank (2013 TAP project-$5.2M) | Falls 230/115 kV | PEC | 3 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2013 | $0.00 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2013 |  |
| Fayetteville 230 kV Sub, Replace 2-200 MVA 230/115 kV banks with 2-300 MVA (2012 TAP project-$4.2M) | Fayetteville 230/115 kV 1/2 | PEC | 5 | 6/1/2013 |  | 6/1/2013 |  | 6/1/2013 |  | 6/1/2014 |  | 6/1/2013 |  | 6/1/2015 |  | 6/1/2013 |  | 6/1/2014 |  | 6/1/2014 |  |
| Fay-Fay East 230kV Line, Replace CB, wavetrap, line switches (2014 TAP project-$425,000) | Fay-Fay East 230 kV | PEC | 3 | 6/1/2012 | $0.09 | 6/1/2011 | $0.13 | 6/1/2011 | $0.13 | 6/1/2012 | $0.09 | 6/1/2011 | $0.13 | 6/1/2011 | $0.13 | 6/1/2012 | $0.09 | 6/1/2012 | $0.09 | 6/1/2013 | $0.04 |
| Fay-Ft. Bragg Woodruff St 230kV Line, Replace line switch (2012 TAP project-$250,000) | Fay-Fay Ft. Bragg Woodruff 230 kV | PEC | 3 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2012 |  |
| Harris-Durham 230 kV Line, Convert & construct new 230 kV line (2014 TAP Project-$77M) | Durham-Cary Reg Pk 230 kV | PEC | 5 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2011 | $23.00 | 6/1/2012 | $15.00 |
| Laurinburg 230 kV Sub, Replace 2-200 MVA 230/115 kV banks with 2-300 MVA (2013 TAP project-$4.2M) | Laurinburg 230/115 kV Bank 1 / 2 | PEC | 3 | 6/1/2014 |  | 6/1/2014 |  | 6/1/2013 |  | 6/1/2015 |  | 6/1/2014 |  | 6/1/2014 |  | 6/1/2014 |  | 6/1/2014 |  | 6/1/2015 |  |
| Method 230 kV Sub, Utilize 65 degree rise rating up to 109% | Method 230/115 kV 1 & 2 | PEC |  | 6/1/2018 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method-E. Durham 230 kV Line, Rebuild Blue Ridge-E. Durham section & replace line switches | Method-E. Durham 230 kV | PEC | 3 | 6/1/2013 | $6.20 |  |  | 6/1/2014 | $6.20 |  |  |  |  |  |  |  |  |  |  |  |  |
| Method-E. Durham 230 kV Line, Rebuild Method-Blue Ridge section & replace line switches | Method-E. Durham 230 kV | PEC | 4 | 6/1/2013 | $7.30 |  |  | 6/1/2014 | $7.30 |  |  |  |  |  |  |  |  |  |  |  |  |
| Person-Milburnie 230 kV line, Uprate Rox Cog-Falls section | Milburnie-Person 230 kV | PEC | 3 | 6/1/2013 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2013 | $2.50 |
| Wake 500 kV Sub, Install #3-500/230 kV bank (2016 TAP Project - $21M) | Wake 500/230 kV Bank 1 / 2 | PEC | 4 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2011 | $11.00 | 6/1/2011 | $11.00 |
| West End 230 kV Sub, Install 230 kV reactor on Cape Fear terminal | Rockingham-West End 230 kV Line West End-Cape Fear 230 kV | PEC | 3 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 | 6/1/2011 | $5.00 |
| Harrisburg-Oakboro 230 kV line bundling | Harrisburg-Oakboro 230 kV overload | Duke | 3 | 6/1/2013 (TRM case) | $4.00 |  |  |  |  |  |  | Not studied |  | Not studied |  |  |  | 6/1/2015 (TRM case) | $2.00 | 6/1/2016 (TRM case) | $1.00 |
| Projects Investigated for Increasing Imports Into PEC (Continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Duke 600 MW |  | SCEG 600 MW |  | SCPSA 600 MW |  | DVP 600 MW |  | SOCO 600 MW |  | TVA 600 MW |  | AEP 600 MW |  | AEP/AEP 1200 MW |  | AEP/DVP 1200 MW |  |
| Antioch 500/230 kV transformers replacement | Antioch 500/230 kV transformers overload | Duke | 5 | 6/1/2014 | $0.00 | 6/1/2014 | $0.00 | 6/1/2014 | $0.00 | 6/1/2012 | $2.00 | Not studied |  | Not studied |  | 6/1/2012 | $2.00 | 6/1/2011 | $3.00 | 6/1/2011 | $3.00 |
| Eno-Parkwood 230 kV line bundling | Eno-Parkwood 230 kV line overload | Duke | 3 | 6/1/2014 (TRM case) | $14.00 |  |  |  |  |  |  | Not studied |  | Not studied |  |  |  |  |  |  |  |
| London Creek 230 kV line bundling | London Creek 230 kV line overload | Duke | 3 | 6/1/2015 | $0.00 |  |  |  |  |  |  | Not studied |  | Not studied |  |  |  |  |  |  |  |
|  |  |  |  | 2012 | $86.02 | 2012 | $59.66 | 2012 | $73.16 | 2012 | $56.02 | 2012 | $64.56 | 2012 | $54.56 | 2012 | $56.52 | 2011 | $62.12 | 2011 | $52.54 |

| Projects Investigated for Increasing Imports Into Duke |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | CPLE 600 MW |  | SCEG 600 MW |  | SCPSA 600 MW |  | DVP 600 MW |  | SOCO 600 MW |  | TVA 600 MW |  | AEP 600 MW |  | AEP/AEP 1200 MW |  | AEP/DVP 1200 MW |  |
| Antioch 500/230 kV transformers replacement | Antioch 500/230 kV transformers overload | Duke | 5 | 2013 | $1.00 | 2013 | $1.00 | 2013 | $1.00 | Not Studied |  | 2012 | $2.00 | 2012 | $2.00 | 2011 | $3.00 | 2011 | $3.00 | 2011 | $3.00 |
|  |  |  |  |  | $1.00 | 2012 | $1.00 | 2012 | $1.00 | 2012 | $0.00 | 2012 | $2.00 | 2012 | $2.00 | 2012 | $3.00 | 2011 | $3.00 | 2011 | $3.00 |