Appendix D

Projects Investigated for Resource Supply Options Studied

DRAFT 12/14/06

| 600 MW Resource Supply Options Studied Projects to Increase Progress East Imports, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Duke 600 MW (M) |  | SCEG 600 MW (M) |  | SCPSA 600 MW (M) |  | DVP 600 MW (M) |  | SOCO 600 MW (M) |  | TVA 600 MW (M) |  | AEP 600 MW (M) |  | AEP/AEP 1200 MW (M) |  | AEP/DVP 1200 MW (M) |  |
| Buck-Asheboro 230 kV Line, Construct 50 mile line (2014 TAP Project-$40M) | Address loadings on Badin-Tillery-Biscoe-Asheboro 115 kV corridor and Rockingham-Lilesville 230 kV Lines. Delays need for Cape Fear-Siler City 230 kV and Harris-Durham 230 kV lines. | Progress & Duke | 5 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 | 6/1/2011 | $12.00 |
| Camden 230 kV Sub, Install 230 kV reactor on (SC) Lugoff terminal | Camden-Camden Junction 115 kV | Progress | 3 |  |  | 6/1/2012 | $5.10 | 6/1/2012 | $5.10 |  |  |  |  |  |  |  |  |  |  |  |  |
| Falls 230 kV Sub, Install #2 230/115 kV bank (2013 TAP project-$5.2M) | Falls 230/115 kV | Progress | 3 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2013 | $0.00 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 | 6/1/2012 | $0.50 |  |  |
| Fay-Fay East 230 kV Line, Replace CB, wavetrap, line switches (2014 TAP project-$425,000) | Fay-Fay East 230 kV | Progress | 3 | 6/1/2012 | $0.09 | 6/1/2011 | $0.13 | 6/1/2011 | $0.13 | 6/1/2012 | $0.09 | 6/1/2011 | $0.13 | 6/1/2011 | $0.13 | 6/1/2012 | $0.09 | 6/1/2012 | $0.09 | 6/1/2013 | $0.04 |
| Fay-Ft. Bragg Woodruff St 230 kV Line, Replace line switch (2012 TAP project-$250,000) | Fay-Fay Ft. Bragg Woodruff 230 kV | Progress | 3 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 | 6/1/2011 | $0.03 |  |  |
| Harris-Durham 230 kV Line, Convert & construct new 230 kV line (2016 TAP Project-$88M) | Durham-Cary Regency Park 230 kV | Progress | 5 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2014 | $17.60 | 6/1/2015 | $8.80 |
| Method-E. Durham 230 kV Line, Rebuild Blue Ridge-E. Durham section & replace line switches | Method-E. Durham 230 kV | Progress | 3 | 6/1/2014 | $6.20 |  |  | 6/1/2015 | $6.20 |  |  |  |  |  |  |  |  |  |  |  |  |
| Method-E. Durham 230 kV Line, Rebuild Method-Blue Ridge section & replace line switches | Method-E. Durham 230 kV | Progress | 4 | 6/1/2014 | $7.30 |  |  | 6/1/2015 | $7.30 |  |  |  |  |  |  |  |  |  |  |  |  |
| Person-Milburnie 230 kV Line, Uprate Rox Cog-Falls section | Milburnie-Person 230 kV | Progress | 3 | 6/1/2013 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2014 | $2.50 | 6/1/2013 | $2.50 |
| Wake 500 kV Sub, Install #3-500/230 kV bank (2016 TAP Project - $21M) | Wake 500/230 kV Bank 1 / 2 | Progress | 4 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2012 | $8.40 | 6/1/2011 | $11.00 | 6/1/2011 | $11.00 |
| West End 230 kV Sub, Install 230 kV reactor on Cape Fear terminal | Rockingham-West End 230 kV Line West End-Cape Fear 230 kV | Progress | 3 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 | 6/1/2011 | $5.00 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 | 6/1/2013 | $5.00 |
| Harrisburg-Oakboro 230 kV Line bundling | Harrisburg-Oakboro 230 kV Line overload | Duke | 3 | 6/1/2013 | $24.00 |  |  |  |  |  |  | Not studied |  | Not studied |  |  |  | 6/1/20153 | $24.00 | 6/1/20163 | $24.00 |

| 600 MW Resource Supply Options Studied Projects to Increase Progress East Imports (Continued) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Duke 600 MW (M) |  | SCEG 600 MW (M) |  | SCPSA 600 MW (M) |  | DVP 600 MW (M) |  | SOCO 600 MW (M) |  | TVA 600 MW (M) |  | AEP 600 MW (M) |  | AEP/AEP 1200 MW (M) |  | AEP/DVP 1200 MW (M) |  |
| Antioch 500/230 kV transformers replacement | Antioch 500/230 kV transformers overload | Duke | 5 |  |  |  |  |  |  | 6/1/2012 | $2.00 | Not studied |  | Not studied |  | 6/1/2012 | $2.00 | 6/1/2011 | $3.00 | 6/1/2011 | $3.00 |
| Eno-Pleasant Garden 230 kV line bundling | Eno-Pleasant Garden 230 kV Line overload | Duke | 3 | 6/1/20143 | $47.00 |  |  |  |  |  |  | Not studied |  | Not studied |  |  |  |  |  |  |  |
| Estimated Incremental Cost (Nominal $M) |  |  |  |  | $130.62 |  | $51.26 |  | $64.76 |  | $47.62 |  | $46.16 |  | $46.16 |  | $48.12 |  | $75.72 |  | $66.34 |

| 600 MW Resource Supply Options Studied Projects to Increase Duke Imports, |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | CPLE 600 MW (M) |  | SCEG 600 MW (M) |  | SCPSA 600 MW (M) |  | DVP 600 MW (M) |  | SOCO 600 MW (M) |  | TVA 600 MW (M) |  | AEP 600 MW (M) |  | AEP/AEP 1200 MW (M) |  | AEP/DVP 1200 MW (M) |  |
| Antioch 500/230 kV transformers replacement | Antioch 500/230 kV transformers overload | Duke | 5 | 2013 | $1.00 | 2013 | $1.00 | 2013 | $1.00 | Not Studied |  | 2012 | $2.00 | 2012 | $2.00 | 2011 | $3.00 | 2011 | $3.00 | 2011 | $3.00 |
| Estimated Incremental Cost (Nominal $M) |  |  |  |  | $1.00 |  | $1.00 |  | $1.00 |  | $0.00 |  | $2.00 |  | $2.00 |  | $3.00 |  | $3.00 |  | $3.00 |

.The tables in Appendix D reflect the date the project is needed in order to implement the resource supply option studied.

The tables in Appendix D contain the estimated incremental costs of the transmission upgrades required to import an additional 600 MW or 1200 MW into the Progress East and/or Duke systems.  The costs are incremental to the total transmission capital plans of Progress and Duke.  Project costs represent either: (i) the estimated acceleration cost of an existing project within the 10-year planning horizon; or (ii) the estimated total cost of a new project that would be needed in the 10-year planning horizon to support the increased import.  The costs are expressed in nominal dollars.

The project date is based on Progress TRM case study results.  Results based on Duke planning criteria result in a later project date.

The tables in Appendix D reflect the date the project is needed in order to implement the resource supply option studied.

The tables in Appendix D contain the estimated incremental costs of the transmission upgrades required to import an additional 600 MW or 1200 MW into the Progress East and/or Duke systems.  The costs are incremental to the total transmission capital plans of Progress and Duke.  Project costs represent either: (i) the estimated acceleration cost of an existing project within the 10-year planning horizon; or (ii) the estimated total cost of a new project that would be needed in the 10-year planning horizon to support the increased import.  The costs are expressed in nominal dollars.

3 The project date is based on Progress TRM case study results.  Results based on Duke planning criteria result in a later project date.