Appendix D

Projects Investigated for Resource Supply Options Studied

January 8, 2008

| Resource Supply Options – 2016 Hypothetical Import Scenarios Studied Imports to Progress East |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Duke 600 MW Date Needed ($M) |  | Duke 1,200 MW Date Needed ($M) |  | PJM 200 MW Date Needed ($M) |  | SCPSA 400 MW Date Needed ($M) |  | SCEG 600 MW Date Needed ($M) |  |
| N/A | None. | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Resource Supply Options – 2016 Hypothetical Import Scenarios Studied Imports to Duke |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | CPLE 100 MW Date Needed ($M) |  | SOCO 600 MW Date Needed ($M) |  | PJM 600 MW Date Needed ($M) |  | TVA 600 MW Date Needed ($M) |  | SCEG 600 MW Date Needed ($M) |  |
| N/A | None. | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| Resource Supply Options – 2016 Hypothetical Generation Scenarios Studied In Progress East1,2 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Scotland County 450 MW Date Needed ($M) |  | Cumberland County 450 MW Date Needed ($M) |  | Wilson County 450 MW Date Needed ($M) |  | Johnston County 450 MW Date Needed ($M) |  | Robeson County 600 MW Date Needed ($M) |  |
| Construct Weatherspoon-Cumberland 230 kV line and Cumberland-Fayetteville East 230 kV line | Thermal loadings on Fayetteville-Fayetteville East 230 kV line and Weatherspoon Plant-Fayetteville DuPont 115 kV line | Progress | 5 | --- | --- | --- | --- | --- | --- | --- | --- | 2016 | 65 |
| Install 115 kV series reactor on Weatherspoon Plant-Fayetteville Dupont 115 kV line and Weatherspoon-Raeford 115 kV line | Thermal load on Weatherspoon-Raeford 115 kV line | Progress | 4 | --- | --- | --- | --- | --- | --- | --- | --- | 2016 | 5 |
| Install 115 kV series reactor at Weatherspoon on Wagram 115 kV terminal | Thermal loading on Raeford-Wagram 115 kV line | Progress | 4 | 2016 | 2 | --- | --- | --- | --- | --- | --- | --- | --- |

| Resource Supply Options – 2016 Hypothetical Generation Scenarios Studied In Duke |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Primary Alternative Investigated | Issue Identified | TO | Lead Time (years) | Guilford County 150 MW Date Needed ($M) |  | Davidson County 150 MW Date Needed ($M) |  | Union County 150 MW Date Needed ($M) |  | Gaston County 150 MW Date Needed ($M) |  | Rockingham County 800 MW Date Needed ($M) |  |
| N/A | None. | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

The tables in Appendix D reflect the date the project is needed in order to implement the resource supply option studied.

2 The estimated cost is in nominal dollars which reflects the sum of the estimated annual cash flows over the expected development period for the specific project (typically 2 – 5 years), including direct costs, loadings and overheads; but not including AFUDC.

Each year’s cash flow is escalated to the year of the expenditures.  The sum of the expected cash flows is the estimated cost.  Also, the projects required to accommodate each resource supply option were determined independently.  Therefore, the projects

and cost estimates do not reflect the requirements for simultaneously accommodating two or more resource supply options.