## Calendar
Contrast & Compare Planning Process
NCStakeholders - PWG
CALENDAR
|  | Duke | Progress | Comments
Planning Calendar
| Modeling/ Assessment/ Solutions/ Budget | Dec-Jan: Finalize models Feb-Mar: Perform screen Apr-Jun: Develop solutions Jul-Aug: Prioritize projects & develop budget September: Finalize budget Oct-Nov: Compile input data & develop models | Dec-Jan: Finalize models Feb-Mar: Perform Near-term(NT) project review Apr-Jun: Prioritize projects & submit budget Jul-Aug: Perform Long-term(LT) screen Sep-Nov: Develop solutions Oct-Nov: Compile input data & develop models Oct-Mar: Develop estimates for LT projects Dec: Budget approved - plan released

## CaseDevelopment
Contrast & Compare Planning Process
NCStakeholders - PWG
CASE DEVELOPMENT
|  | Duke | Progress | Comments
Reduced External Area Model
| Database cycle | January to June (VSTE Data Bank Process) Companies within VSTE combine new reduced models of their areas coordinating data within VSTE areas. June to December (MMWG Process) Regions combine reduced models of their areas to develop an eastern interconnection model. SERC provides the VSTE Data Bank Cases to the MMWG for this effort. Data is coordinated among regions. | January to June (VSTE Data Bank Process) Companies within VSTE combine new reduced models of their areas coordinating data within VSTE areas. June to December (MMWG Process) Regions combine reduced models of their areas to develop an eastern interconnection model. SERC provides the VSTE Data Bank Cases to the MMWG for this effort. Data is coordinated among regions. | Same
| Assumptions | Model long-term firm transmission in model. No partial path reservations modeled. | Model long-term firm transmission in model. No partial path reservations modeled. | Same
Detailed Internal Model ("on-the-shelf cases")
| Cases developed | Summer Peak (for current and next 10 years) Winter Peak (for current and next 10 years) Spring/Fall Peak (for current and next 2 years) Spring Valley (for current and next 3 years) | Summer Peak (for current and next 10 years) Winter Peak (for current and next 10 years)
| Loads | Utilize data from EMS. Loads plus losses at the transmission level will be scaled to match the system forecast for each load level. If conditions warrant, additional cases may be generated to examine the impact of other load levels. Load is not reduced by load management. | Corporate provides PEC load forecast data. PEC distribution organization provides NCPs for all PEC substations for model. Obtains Network Customer's CP forecasts via Network Operating Agreement. Scales PEC area to meet annual forecast without scaling Network Customer data. Load is not reduced by load management.
| Interchange | Long term firm transmission and LSE's DNR projections are modeled in the base case | Models all firm transmission reservations on its OASIS including partial path reservations.
| Behind Meter Gen | Netted with load. | Netted with load. | Same
| Duke/PEC Generation | Modeled in detail. Duke's resources dispatched economically. External area dispatch is generally left as in MMWG. All on line generation resources are scaled in the affected control area if interchange adjustments are needed | Modeled in detail. PEC's resources dispatched economically. External area dispatch is generally left as in MMWG. Load of external area is scaled if PEC import adjustments are needed.
| Network Customer Resources | Network customers provide dispatch priority for use in dispatching their resources to their load. | On system generation is modeled based on transmission reservation. Imports are modeled based on transmission reservation.
| Other Non-Duke/PEC Generation | Modeled in detail. IPPs must have an LGIA executed to be in model and they are dispatched at level of approved firm transmission service. | Modeled in detail. IPPs must have an LGIA executed to be in model and they are dispatched at level of approved firm transmission service. | Same
| Future Generation | Uses dummy generation in future cases only when additional load serving resources are needed. Dummy generation generally modeled based on generator interconnection queue locations. | Uses dummy generation in future cases only when additional load serving resources are needed. Dummy generation typically modeled on Wake 500 kV bus and named DUMGEN .
| Ratings | Use several different continuous and time-limited emergency line ratings. Rate A - Continuous rating Rate B - 12 hour emergency rating Rate C - Long term emergency rating (based on acceptable loss of life) | Rate A = Rate B = Continuous rating Lines modeled at continuous conductor rating unless ground clearence limited or other equipment (switches, traps, etc.) Transformers modeled at 55 deg rise rating.

## Reliability-and-DNR-Practices
Contrast & Compare Planning Process
NCStakeholders - PWG
RELIABILITY ASSESSMENT PRACTICES
|  | Duke | Progress | Comments
Limits Voltage
| 500kV | Maintain minimum of 100% | Maintain minimum of 100% | Same
| 230kV | Maintain minimum of 95% | Maintain minimum of 90%
| Allowed Contingency Drop | 5% | 8%
Limits Thermal
| Lines Transformers | Do not exceed 100 % of: Rate A for continuous loading, (Category A below.) Rate B for line or 500/230 kV transformer contingencies, (Subset of Category B below.) Rate C for all other transformer, generator and capacitor contingencies. (Remainder of Category B below.) and Base cases + L + L,+ L + Tx,+ Tx + Tx,+ Gm + Gc,+ Gm + L,+ Gm + Tx contingencies Do not exceed 125 % of Rate A for Category D and bus section/breaker Category C contingencies | Do not exceed 100 % of line rating. (Rate A=Rate B) under normal or contingency conditions (Category A, B, & C below) Do not exceed 100 % transformer 55 deg rise rating (Rate A=Rate B) unless a 65 deg rise rating is available under normal and contingency conditions (Category A, B, & C below.) . Will allow 109% loading of the 55 deg rating under Category B & C conditions if a 65 degree rise rating is available and the bank is determined to be in good condition.
Other Limits
| Phase Angle | Criteria under evaluation. | Do not exceed 30 degrees phase angle difference across an open terminal.
Cases Developed
| Years | Screen 3 years out & develop and assess transmission projects. | Assess projects 3 years out to support budget process. Screen 6 years out & develop and assess transmission projects.
| Cases | All generation available (Genration up) base case T case is all generation up case with all firm transmission reservations included Generation maintenance (Gm) cases with a large unit out of service for maintenance and the remainder of Duke's reseources dispatched economically to maintain supply / demand balance | All generation available (Genration up) base case.
TRM/CBM
| TRM | VACAR reserve sharing amounts reserved | Total of all VACAR reserve sharing plus parallel path bias is reserved (approx 1820 MW). PEC interconnects with all VACAR utilities and studies the import of the full reserved amount on top of other import obgliations.
| CBM | CBM equals 0, therefore none reserved | CBM equals 0, therefore none reserved | Same
NERC Table I
| Cat A | Base cases {includes the Generation up case, all generator maintenance outage permutations (Gm cases) and one case with all long term firm reservations included (T case)} | Generation up | Both Duke and PEC build for this.
| Cat B | Base cases + generator contingency (Gc) with the amount of Gc lost MW's imported equally among 6 interfaces with appropriate adjustments to Net Interchanges Base cases + line outage Base cases + transformer outage Base cases + capacitor outage | Generation up + line outage or transformer Generator contingency (Gc) with import of TRM (representative of the Gc along with other unit derations) divided in accordance to TRM allocations to individual interfaces with appropriate adjustments to Net Interchanges | Both Duke and PEC build for this.
| Cat C | Generation up + bus section Generation up + breaker failure Base cases + Line + Line Base cases + Line + Tx Base cases + Tx + Tx Base cases (except T) + Gc + Gc Base cases (except T) + Gm + Line Base cases (except T) + Gm + Tx | Generation up + common tower outages Gc with TRM (as above) + line or transformer outage Gc with TRM (as above) + common tower line outages Periodic assessment of bus outges. | PEC builds for listed Cat C contingencies. Both assess Cat C contingencies for cascading
| Cat D | Generation up + Common ROW Generation up + substation (one voltage level plus tx's) Generation up + all generation at a station | Beyond scope of CTPP | Both assess bounding of cascading.
Transient/Dynamic Stability , Short Circuit, Voltage Stability
| Stability | Typically, Duke will complete the list of studies scheduled for the year. This list is based upon a 5 year cycle for generation stations and a 10 year cycle for tie stations. Highest priority is placed upon Duke’s larger MVA generating units, followed by higher voltage interconnections and then higher voltage tie stations. At a minimum, applicable worst-case contingency scenarios from NERC Table 1 are assessed for each station under study. | Design for LLG Fault with delayed clearing to simulate breaker failure.
| Short Circuit | Faults are evaluated for each breaker location to find the highest available fault current for worst case configuration. All generation in service. Maximum system operating voltage. | All faults considered with worst case configuration for highest available fault current. Generation in the area at full output.
| Voltage Stability | Steady-state PV analysis on near and long-term cases. Comprehensive voltage stability analysis using detailed dynamic load models. | N/A
Tools
| Thermal | PSS/E Software | PSS/E Software
| Stability | PSS/E Software | PSS/E Software
| Short Circuit | ASPEN Software | ASPEN Software

## CBM-TRM
Comparison of Duke Energy and Progress Energy Carolinas' CBM/TRM Methodologies
|  |  | Duke Energy | Progress Energy Carolinas
| CBM | Definition | Same as NERC | Same as NERC
|  | Value | Zero on all interfaces | Zero on all interfaces
(Imports Only)
Reason
|  |  | - No significant transfer limits | -PEC has determined that additional transmission reserves above those operating reserves in TRM are not necessary
|  |  | - TTC calculations use reduced line ratings (12 hr vs. 1 hr when operating the system) | - Loss-of Load Expectation (LOLE) of 1 day in 10 years suggest availability of 1500 MW to 1800 MW of resources external to the PEC system.
- TTC calculations are based on single worst transmission contingency and adverse generation participation
| TRM | Definition | Same as NERC | Same as NERC
Value
|  | (Imports) | - Opposing control area’s share of the VACAR reserve sharing requirement | - Compopnent is the larger of reserve obligation on an interface or the inrush response due to a sudden loss of generation. - Component to account for parallel path flow
|  | Value | - Reserve obligation to meet the VACAR Reserve Sharing Agreement | - Reserve obligation to meet the VACAR Reserve Sharing Agreement
(Exports)
Reason
|  |  | - To declare TRM there should be a contractual obligation for reserves, such as the VACAR Reserve Sharing Agreement | - Account for variations in generator dispatch, parallel path flows, and operating reserves, such as the VACAR Reserve Sharing Agreement
Selling
|  |  | - Not sold on a firm or non-firm basis, as doing so would degrade system security | - Not sold on a firm or non-firm basis, as doing so would degrade system security
| CBM/TRM | Availability to LSEs
|  |  | - Not available for use on a firm basis by market entities, including Duke Energy’s affiliated marketer | TRM available for:
- Loss of firm resource invoking an Emergency Reserve Sharing Agreement
- In response to a generation emergency, the System Operating Center uses TRM for VACAR reserve sharing purposes to benefit all control area LSEs
- Declaration of an Energy Emergency Alert (EEA) due to insufficient resources
- LSE has exhausted all other options and can no longer provide its customers’ expected load requirements.
2005 VACAR Reserve Sharing Obligations
| 2005 Reserves | Adjusted | Largest Resource (MW) | Contingency Reserve % | Contingency Reserve Commitment (MW)
Peak Load
(MW)
| Duke | 17926 | 1135 | 0.2971 | 506
| PEC | 11699 | 900 | 0.2129 | 363
| SCPSA | 4781 | 590 | 0.1136 | 193
| SCE&G | 4574 | 636 | 0.1172 | 200
| DVP | 16507 | 925 | 0.2592 | 441
| Total | 55487 | 4186 | 1.0000 | 1703
Current Duke Energy and Progress Energy Carolina CBM/TRM Values
| Control Area | From | To | CBM | TRM or | TRM (APPFI or Inrush)
TRM (RS)
| Duke Imports | PJM | Duke | 0 | 0 | N/A
|  | PEC East | Duke | 0 | 363 | N/A
|  | PEC West | Duke | 0 | 0 | N/A
|  | SCE&G | Duke | 0 | 200 | N/A
|  | SCPSA | Duke | 0 | 193 | N/A
|  | TVA | Duke | 0 | 0 | N/A
|  | Southern | Duke | 0 | 0 | N/A
|  | SEPA | Duke | 0 | 0 | N/A
|  | Yadkin | Duke | 0 | 0 | N/A
| Duke Exports | Duke | PJM | - | 0 | N/A
|  | Duke | PEC East | - | 306 | N/A
|  | Duke | PEC West | - | 200 | N/A
|  | Duke | SCE&G | - | 506 | N/A
|  | Duke | SCPSA | - | 506 | N/A
|  | Duke | TVA | - | 0 | N/A
|  | Duke | Southern | - | 0 | N/A
|  | Duke | SEPA | - | 0 | N/A
|  | Duke | Yadkin | - | 0 | N/A
| PEC East Imports | PJM | PECE | 0 | 441 | 487
|  | Duke | PECE | 0 | 506 | 0
|  | SCE&G | PECE | 0 | 200 | 0
|  | SCPSA | PECE | 0 | 193 | 0
| PEC East Exports | PEC East | PJM | - | 363 | 0
|  | PEC East | Duke | - | 363 | 0
|  | PEC East | SCE&G | - | 363 | 0
|  | PEC East | SCPSA | - | 363 | 0
| PEC West Imports | PJM | PEC West | 0 | 0 | 42
|  | Duke | PEC West | 0 | 0 | 200
|  | TVA | PEC West | 0 | 0 | 0
| PEC West Exports | PEC West | PJM | - | 0 | 0
|  | PEC West | Duke | - | 0 | 0
|  | PEC West | TVA | - | 0 | 0

## Ratings
Comparison of Duke and PEC Line Rating Assumptions and Methodologies
|  | Duke | PEC
| Calculation Method | Not stated | Not stated
| Line Altitude | 700 ft. | Regional
| Line Latitude | 35 degrees N | 35 degrees N
| Line Orientation | Not stated | Not stated
| Coefficient of Emissivity | 0.7 | 0.5
| Coefficient of Absorption | 0.9 | 0.5
| Atmospheric Quality | Clear (100%) | Clear (100%)
| Time of Day | 14:00 EDT | 12:00 EDT
| Ambient Air Temperature | 40o C (104o F) | 35o C (95o F)
| Ambient Wind Speed | 5.0 ft/sec | 2.0 ft/sec 3.0 ft/sec Coastal
| Relative Wind Conductor Angle | 45o | 90o