## Summary
2006 Reliability Study-Resource Options
Recommended Scenarios
AGREED
| Alternatives |  |  | NET | TEST | CASE
| Source | Sink | Sink | CHANGE | LEVEL | DEVELOPED | SCREENING | NCMPA |  | Concord |  |  | NCEMC |  | FC/Dallas |  |  | Fayetteville |  | Tri-Towns |  |  | Waynesville
1 | PJM (AEP) | DUKE |  | 473 | 600 | Base Case | Duke | 150 | PV down (in Duke) | 274 | drop Duke generation | could be 232 |  |  | 49 | drop Duke generation | load is NCP value
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
2 | SOCO | DUKE |  | 564 | 600 | Base Case | Duke | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232 | 100 | Swap 100 MW from SCEG to SOCO
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
3 | TVA | DUKE |  | 464 | 600 | Base Case | Duke | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
4 | SCEG | DUKE |  | 464 | 600 | Base Case | Duke | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
5 | SC | DUKE |  | 464 | 600 | Base Case | Duke | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
6 | CPLE | DUKE |  | 464 | 600 | Base Case | Duke | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232
[6 empty] | Roxboro outage | Duke
[6 empty] | Tillery/Blewett outage | Duke
[6 empty] | Anson (NCEMC) outage | Duke
7 | PJM (AEP) |  | CPLE | 535 | 600 | Base Case | Duke/Progress | [10 empty] | 500 | drop CPLE generation | 35 | drop CPLE generation | could be 20
[6 empty] | Marshall Gm | Progress
[6 empty] | MNS 1 Gm | Progress
[6 empty] | MNS 2 Gm | Progress
[6 empty] | Belews Creek Gm | Progress
[6 empty] | CNS 1 Gm | Progress
8 | PJM (VP) |  | CPLE | 535 | 600 | Base Case | Duke/Progress | [10 empty] | 500 | drop CPLE generation | 35 | drop CPLE generation | could be 20
[6 empty] | Marshall Gm | Progress
[6 empty] | MNS 1 Gm | Progress
[6 empty] | MNS 2 Gm | Progress
[6 empty] | Belews Creek Gm | Progress
[6 empty] | CNS 1 Gm | Progress
9 | SCEG |  | CPLE | 600 | 600 | Base Case | Duke/Progress | [5 empty] | 100 | Swap 100 MW from AEP to SCEG |  |  |  | 500 | drop CPLE generation
[6 empty] | Marshall Gm | Progress
[6 empty] | MNS 1 Gm | Progress
[6 empty] | MNS 2 Gm | Progress
[6 empty] | Belews Creek Gm | Progress
[6 empty] | CNS 1 Gm | Progress
10 | SC |  | CPLE | 500 | 600 | Base Case | Duke/Progress | [10 empty] | 500 | drop CPLE generation
[6 empty] | Marshall Gm | Progress
[6 empty] | MNS 1 Gm | Progress
[6 empty] | MNS 2 Gm | Progress
[6 empty] | Belews Creek Gm | Progress
[6 empty] | CNS 1 Gm | Progress
11 | DUKE |  | CPLE | 500 | 600 | Base Case | Duke/Progress | [10 empty] | 500 | drop CPLE generation
[6 empty] | Marshall Gm | Progress
[6 empty] | MNS 1 Gm | Progress
[6 empty] | MNS 2 Gm | Progress
[6 empty] | Belews Creek Gm | Progress
[6 empty] | CNS 1 Gm | Progress
12 | PJM(AEP/AEP) | DUKE | CPLE | 1008 | 600/600 | Base Case | Duke/Progress | 150 | PV down only, PJM already source for 40 MW | 274 | drop Duke generation | could be 232 |  |  | 49 | drop Duke generation | load is NCP value | 500 | drop CPLE generation | 35 | drop CPLE generation | could be 20
[6 empty] | Marshall Gm | Duke/Progress
[6 empty] | MNS 1 Gm | Duke/Progress
[6 empty] | MNS 2 Gm | Duke/Progress
[6 empty] | Belews Creek Gm | Duke/Progress
[6 empty] | CNS 1 Gm | Duke/Progress
[6 empty] | Roxboro outage | Duke/Progress
[6 empty] | Tillery/Blewett outage | Duke/Progress
[6 empty] | Anson (NCEMC) outage | Duke/Progress
13 | PJM(AEP/VP) | DUKE | CPLE | 1008 | 600/600 | Base Case | Duke/Progress | 150 | PV down only, PJM already source for 40 MW | 274 | drop Duke generation | could be 232 |  |  | 49 | drop Duke generation | load is NCP value | 500 | drop CPLE generation | 35 | drop CPLE generation | could be 20
[6 empty] | Marshall Gm | Duke/Progress
[6 empty] | MNS 1 Gm | Duke/Progress
[6 empty] | MNS 2 Gm | Duke/Progress
[6 empty] | Belews Creek Gm | Duke/Progress
[6 empty] | CNS 1 Gm | Duke/Progress
[6 empty] | Roxboro outage | Duke/Progress
[6 empty] | Tillery/Blewett outage | Duke/Progress
[6 empty] | Anson (NCEMC) outage | Duke/Progress
14 | PJM (AEP) |  | CPLW | 20 | 20 | Base Case | Progress | [15 empty] | 20 | drop CPLW generation
Not studied
| SCEG | DUKE | CPLE | 1064 | 600/600 |  |  | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232 | 100 | Swap 100 MW from AEP to SCEG |  |  |  | 500 | drop CPLE generation
| SC | DUKE | CPLE | 964 | 600/600 |  |  | 190 | PV down and drop 40 MW of PJM | 274 | drop Duke generation | could be 232 | [5 empty] | 500 | drop CPLE generation

## Sheet2
ALTERNATE RESOURCE REQUEST SUMMARY
| LSE | AGENCY | MW | SINK | ORIGINAL | ALTERNATE | Comments
1 | Stantonsburg, Sharpsburg, Lucama, Black Creek | NCMPA | 35 | CPLE | VP | PJM | Study for POR =PJM and POR=DUKE
2 | Concord | NCMPA | 274 | DUKE | DUKE | PJM | Original is in base model
3 |  |  | 274 | DUKE | DUKE | SOCO | Original is in base model
4 |  |  | 274 | DUKE | DUKE | TVA | Original is in base model
5 |  |  | 274 | DUKE | DUKE | SCEG | Original is in base model
6 |  |  | 274 | DUKE | DUKE | SC | Original is in base model
7 |  |  | 274 | DUKE | DUKE | CPLE | Original is in base model
8 | Fayetteville | NCMPA | 500 | CPLE | CPLE | PJM | Original is in base model
9 |  |  | 500 | CPLE | CPLE | DUKE | Original is in base model
10 |  |  | 500 | CPLE | CPLE | SCEG | Original is in base model
11 |  |  | 500 | CPLE | CPLE | SC | Original is in base model
12 | NCMPA | NCMPA | 150 | DUKE | PV-Duke | PJM | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
13 |  |  | 150 | DUKE | PV-Duke | SOCO | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
14 |  |  | 150 | DUKE | PV-Duke | TVA | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
15 |  |  | 150 | DUKE | PV-Duke | SCEG | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
16 |  |  | 150 | DUKE | PV-Duke | SC | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
17 |  |  | 150 | DUKE | PV-Duke | CPLE | NCMPA only has 50 MW contracted in 2011, but need to dispatch 100 more in base case
18 | NCMPA | NCMPA | 40 | DUKE | PJM | PJM | Original will be in base model
19 |  |  | 40 | DUKE | PJM | SOCO | Original will be in base model
20 |  |  | 40 | DUKE | PJM | TVA | Original will be in base model
21 |  |  | 40 | DUKE | PJM | SCEG | Original will be in base model
22 |  |  | 40 | DUKE | PJM | SC | Original will be in base model
23 |  |  | 40 | DUKE | PJM | CPLE | Original will be in base model
24 | NCMPA | NCMPA | 40 | DUKE | SOCO | PJM | Original will be in base model
25 |  |  | 40 | DUKE | SOCO | SOCO | Original will be in base model
26 |  |  | 40 | DUKE | SOCO | TVA | Original will be in base model
27 |  |  | 40 | DUKE | SOCO | SCEG | Original will be in base model
28 |  |  | 40 | DUKE | SOCO | SC | Original will be in base model
29 |  |  | 40 | DUKE | SOCO | CPLE | Original will be in base model
30 | NCEMC | NCEMC | 100 | CPLE | AEP | SCEG | Original is in base model
31 |  |  | 100 | DUKE | SCEG | SOCO | Original is in base model
32 | Waynesville | NCMPA | 20 | CPLW | CPLW | PJM | Replaces PEC Gen (Full req)
[5 empty] | CPLE | DUKE
|  |  |  | PJM | 500 | 504
|  |  |  | SOCO |  | 604
|  |  |  | TVA |  | 504
|  |  |  | SCEG | 600 | 504
|  |  |  | SC | 500 | 504
|  |  |  | CPLE |  | 504
|  |  |  | DUKE | 500 |  | CPLE replacement