## Duke Summary
Transmission Facility | Worst-Case Information | Base | Anson | Roxboro | Tillery-Blewett | 1200ImportDukeCPLE_AEP | 1200ImportDukeCPLE_AEPVP | COMMENTS
| Post-Contingency Loading (MVA) | 70.9 | 81.8 | 87.5 | 73.1 | 64.8 | 65.8 | Cont Rating 58.5 MVA - Should use 12 Hour Rating 71.2 MVA
Wateree 100 kV Line | % Facility Rating | 113.3% | 130.7% | 139.7% | 116.8% | 111.5% | 105.3% | (75°, 90° Hot Line Crossing) 2/0 Cu Conductor Limited
(Wateree-Great Falls) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | Hot Line Crossing Correction Only 78.1 MVA
| Contingency | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Reconductor Required - Operating Guide Available
| Post-Contingency Loading (MVA) | 503.2 | 499.5 | 522.7 | 503.7 | 496 | 492.8 | 12 Hour Rating 478 MVA
Westport 230 kV Line | % Facility Rating | 103.2% | 102.6% | 107.4% | 103.3% | 101.9% | 101.1% | CT/5-M Ratio Limited
(Marshall-McGuire) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 1272 ACSR Conductor 617.5 MVA
| Contingency | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | CT Upgrade pushes out to 2021
| Post-Contingency Loading (MVA) | 758.7 | 763.8 | 761 | 761.3 | 838.2 | 824.9 | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 90.3% | 90.9% | 90.6% | 90.6% | 99.8% | 98.2% | Transformer Limited
Transformer Bank 1 | Year Upgrade Required | 2017 | 2016 | 2016 | 2016 | 2012 | 2012 | Transformer 840 MVA
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Increased Transformer Capacity Required in 2012
| Post-Contingency Loading (MVA) | 801.2 | 806.6 | 803.6 | 804 | 885.3 | 871.2 | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 95.4% | 96% | 95.7% | 95.7% | 105.4% | 103.7% | Transformer Limited
Transformer Bank 2 | Year Upgrade Required | 2014 | 2014 | 2014 | 2014 | 2011 | 2011 | Transformer 840 MVA
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Increased Transformer Capacity Required in 2011
| Post-Contingency Loading (MVA) | 1862.7 | 1859.4 | 1913.2 | 1862.8 | 1825.8 | 1802.2 | 12 Hour Rating 1904.3 MVA
Godbey 500 kV Line | % Facility Rating | 95.1% | 95% | 98.3% | 95.1% | 93.4% | 92% | CT/5 Ratio Limited
(Woodleaf-Pleasant Garden) | Year Upgrade Required | 2014 | 2014 | 2012 | 2014 | 2015 | 2016 | 2-2515 ACSR Conductor 4718 MVA
| Contingency | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | CT Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | 101.5 | 103.1 | 100.5 | 101.6 | 109.3 | 107.8 | LTE Rating 108.3 MVA
Horseshoe 115/100 kV | % Facility Rating | 93.8% | 95.2% | 92.8% | 93.8% | 100.9% | 99.5% | 300 Cu Limited
Transformer | Year Upgrade Required | 2015 | 2014 | 2015 | 2015 | 2011 | 2012 | Transformer 134.5 MVA
| Contingency | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | 300 Cu, 1/2" Cu Pipe, 600 Cu Switch Upgrades pushes to 2022
| Post-Contingency Loading (MVA) | - | - | 783.4 | - | - | - | 12 Hour Rating 840 MVA
Parkwoood 500/230 kV | % Facility Rating | < 90% | < 90% | 93.3% | < 90% | < 90% | < 90% | Transformer Limited
Transformer Bank 5 | Year Upgrade Required | - | - | 2015 | - | - | - | Transformer 840 MVA
| Contingency | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | - | - | Increased Transformer Capacity Required in 2015
| Post-Contingency Loading (MVA) | 745 | 737.8 | 790.2 | 741.5 | 721.5 | - | 12 Hour Rating 796.7 MVA
Parkwoood 500/230 kV | % Facility Rating | 93.5% | 92.6% | 99.2% | 93.1% | 90.6% | < 90% | CT/5 Ratio Limited
Transformer Bank 6 | Year Upgrade Required | 2015 | 2015 | 2012 | 2015 | 2016 | - | Transformer 1152.7 MVA
| Contingency | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | CT Upgrade pushes out to 2025
| Post-Contingency Loading (MVA) | 419.2 | 412.9 | 414.5 | 417.7 | - | - | 12 Hour Rating 452.5 MVA
London Creek 230 kV | % Facility Rating | 92.1% | 90.8% | 91.1% | 91.8% | < 90% | < 90% | 795 ACSR Conductor Limited
(Peach Valley-Riverview) | Year Upgrade Required | 2016 | 2016 | 2016 | 2016 | - | - | Reconductor Required in 2016
| Contingency | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | - | -
| Post-Contingency Loading (MVA) | 438.6 | 438.8 | 437.4 | 439.6 | 446.8 | 445.6 | 12 Hour Rating 478 MVA
Dooley 230 kV Line | % Facility Rating | 90.7% | 90.8% | 90.5% | 90.9% | 92.7% | 92.4% | CT/5-M Ratio Limited
(Marshall-Winecoff) | Year Upgrade Required | 2016 | 2016 | 2017 | 2016 | 2015 | 2015 | 1272 ACSR Conductor 617.5 MVA
| Contingency | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | CT Upgrade pushes out to 2024
| Post-Contingency Loading (MVA) | 380.8 | 393.5 | 379.2 | 382.9 | 391.4 | 388.3 | Cont Rating 436.9 MVA - Should use 12 Hour Rating 478 MVA
Sandy Ridge 230 kV Line | % Facility Rating | 90.4% | 93.9% | 90% | 90.9% | 93.2% | 92.4% | CT/5 Ratio, CT/5-M Ratio, and 51XYZ Relay Limited
(Newport-Morning Star) | Year Upgrade Required | 2017 | 2015 | 2017 | 2016 | 2015 | 2015 | 954 ACSR Conductor 506.7 MVA
| Contingency | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | 12 Hour Rating pushes out to 2019
| Post-Contingency Loading (MVA) | - | 421.8 | - | - | - | - | Cont Rating 437 MVA - Should use 12 Hour Rating 482 MVA
Harrisburg 230 kV Line | % Facility Rating | < 90% | 96.4% | < 90% | < 90% | < 90% | < 90% | 750 Cu and 1" Cu Pipe Limited
(Harrisburg-Oakboro) | Year Upgrade Required | - | 2013 | - | - | - | - | 954 ACSR Conductor 506.7 MVA
| Contingency | - | Oco3Gm w/ Harrisburg 230 kV Line | - | - | - | - | 12 Hour Rating pushes out to 2018
| Post-Contingency Loading (MVA) | - | 87.1 | 88.7 | - | - | - | 12 Hour Rating 96 MVA
Clark Hill 115/100 kV | % Facility Rating | < 90% | 90.7% | 92.4% | < 90% | < 90% | < 90% | 336 ACSR Limited
Transformer | Year Upgrade Required | - | 2016 | 2015 | - | - | - | Transformer 173.3 MVA
| Contingency | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | - | 336 ACSR Upgrade pushes out to 2027
| Post-Contingency Loading (MVA) | - | - | 822.9 | - | - | - | 12 Hour Rating 889 MVA
Stamey 230 kV Line | % Facility Rating | < 90% | < 90% | 90.5% | < 90% | < 90% | < 90% | 1600 Al Switch Limited
(Marshall-Stamey) | Year Upgrade Required | - | - | 2017 | - | - | - | 2-954 ACSR Conductor 1176 MVA
| Contingency | - | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | 1600 Al Switch Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | - | - | - | - | 723.3 | 709.9 | 12 Hour Rating 717 MVA
Clingman 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 99.8% | 97.7% | CT/5 Ratio Limited
(Antioch-Mitchell River) | Year Upgrade Required | - | - | - | - | 2012 | 2013 | 2-954 ACSR Conductor 1176 MVA
| Contingency | - | - | - | - | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | CT Upgrade pushes out to 2026
| Post-Contingency Loading (MVA) | - | - | - | - | 95.5 | 95 | Cont Rating 108.3 MVA - Should use 12 Hour Rating 118.6 MVA
Rugby 100 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 91.8% | 91.2% | 300 Cu Limited
(Horseshoe-Pisgah) | Year Upgrade Required | - | - | - | - | 2016 | 2016 | 477 ACSR Conductor 139.4 MVA
| Contingency | - | - | - | - | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | 12 Hour Rating pushes out to 2020

## Base
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 133 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 56 | Not in original screening
[25 empty] | 189 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
DAN3GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.1 | 161.3 | 542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.4 | 164.1 | 136.8 | 129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 247.2 | 120 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 74.6 | 118.5 | 110.8 | 49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96 | 214.3 | 105.4 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.2 | 112.4 | 105.1 | 51 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.2 | 503.2 | 103.2 | 68 | 478 | 250.2 | 388 | 79 | 1 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.2 | 503.2 | 103.2 | 69 | 478 | 250.2 | 388 | 79 | 2 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.3 | 306.1 | 102 | 1886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.2 | 314.8 | 96.9 | 423 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2013 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 501.2 | 801.2 | 95.4 | 82 | 840 | 457.1 | 731.3 | 87.1 | 44 | -8.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 69.9 | 8.3
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 111 | -14.8 | 2014 | 2019 | 5 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.1 | 14.8
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.9 | 189.9 | 95 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.2 | 156 | 94.6 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 435 | 745 | 93.5 | 87 | 796.7 | 390.3 | 670 | 84.1 | 44 | -9.4 | 2015 | 2016 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 75 | 9.4
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.5 | 364.5 | 93.5 | 554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.5 | 139.4 | 93.2 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 71 | 188.2 | 92.9 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 452.5 | 277.7 | 420.8 | 91.4 | 45 | -0.7 | 2016 | 2012 | -4 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -1.6 | 0.7
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 43.5 | 86.2 | 91.6 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.2 | 438.6 | 90.7 | 252 | 478 | 313 | 411.3 | 84.6 | 44 | -6.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.3 | 6.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 478 | 330.1 | 367.5 | 78.9 | 1124 | -11.5 | 2017 | 2015 | -2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 13.3 | 11.5
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 418 | 758.7 | 90.3 | 44 | 840 | 381.2 | 692.7 | 82.5 | 40 | -7.8 | 2017 | 2017 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 66 | 7.8
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.3 | 963.3 | 90.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.1 | 165.2 | 90.3 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 27 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 3 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 30 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening
[25 empty] | 34 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 65.9 | 112.6 | 910 | 58.5 | - | 52.1 | 89.1 | 706 | -23.5 | 2011 | 2013 | 2 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 13.8 | 23.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464 | 97.1 | 232 | 478 | - | 380.4 | 79.6 | 100 | -17.5 | 2013 | 2019 | 6 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 83.6 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1804.3 | 94.8 | 910 | 1904.3 | - | 1541.1 | 80.9 | 868 | -13.9 | 2014 | 2018 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.2 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976.7 | 91.5 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.3 | 91.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 11 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 6 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Base Case
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.3 | 94.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.1 | 91.6 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976.7
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.8 | 91.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.3 | #N/A | 973.3
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Anson
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.4 | 1657.6 | 201.7 | 5292 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 511 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 110.3 | 220.4 | 147 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 109.7 | 220.4 | 147 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.9 | 163.8 | 136.8 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 617 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 660 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 244 | 120.2 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 80 | 124.6 | 116.3 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -5.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 65.2 | 116.7 | 109.1 | 87 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.8 | 214.2 | 105.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 328.9 | 499.5 | 102.6 | 61 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 328.9 | 499.5 | 102.6 | 62 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.9 | 305.8 | 101.9 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 49.2 | 92.5 | 98.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -6.6 | 2012 | 2016 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 299.9 | 315.1 | 97 | 429 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 285.6 | 421.8 | 96.4 | 171 | 437 | 249.4 | 367.6 | 83.9 | 85 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 676 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 285.6 | 421.8 | 96.4 | 215 | 437 | 248.6 | 366.8 | 83.9 | 128 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 71.9 | 24.2
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.2 | 192.2 | 96.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.4 | 192 | 96 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 504.6 | 806.6 | 96 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.6 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 75.3 | 8.9
OCO3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1039.7 | 1319 | 95.1 | 8318 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1685.2 | 1859.4 | 95 | 7802 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.1 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 258.8 | 14.7
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76 | 155.8 | 94.4 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 146.4 | 187.9 | 94 | 54 | 200 | 140 | 176.3 | 88.1 | 12 | -5.9 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 351.8 | 393.5 | 93.9 | 1999 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -3.5 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 26 | 15
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 188.1 | 93 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 430.8 | 737.8 | 92.6 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.9 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 67.8 | 8.5
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.7 | 97.9 | 91.5 | 34 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.1 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420.8 | 763.8 | 90.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.6 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 71.1 | 8.4
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.4 | 438.8 | 90.8 | 258 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.5 | 6.2
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 279 | 412.9 | 90.8 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -7.9 | -0.6
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.7 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 53 | 90.6 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -12.1 | 2016 | 2024 | 8 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 73.3 | 125.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -12.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 21.2 | 36.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 459.8 | 96.2 | 232 | 478 | - | 464 | 97.1 | 232 | 0.9 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 79.4 | 16.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1800.2 | 94.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 259.1 | 13.6
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.4 | 91.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.2 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Anson
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CLI5GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
CLI5GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.1 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.4
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLI5GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 974.2
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.1 | 90.7 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.4 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.6 | 14.1 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 7 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 14 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
NANTGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1656.4 | 201.5 | 5676 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.3 | 161.4 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 765 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 808 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.8 | 163.2 | 136.2 | 94 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.5 | 243.2 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 82 | 126.3 | 117.9 | 68 | 108 | 74.6 | 118.5 | 110.8 | 49 | -7.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.8 | 117.5 | 109.9 | 89 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345 | 522.7 | 107.4 | 94 | 478 | 333.2 | 503.2 | 103.2 | 68 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345 | 522.7 | 107.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 69 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.5 | 213.6 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51.5 | 94.4 | 100.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -8.6 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76 | 134.1 | 100 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 461.7 | 790.2 | 99.2 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -5.7 | 2012 | 2015 | 3 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 120.2 | 15.1
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213 | 296.2 | 98.7 | 1830 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.3 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1751.8 | 1913.2 | 98.3 | 7908 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -3.2 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 312.6 | 18
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.9 | 195.4 | 97.7 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.2 | 195.1 | 97.6 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.8 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 304.2 | 314.8 | 96.9 | 614 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 148 | 193.3 | 96.7 | 62 | 200 | 140 | 176.3 | 88.1 | 12 | -8.6 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 343.3 | 373.9 | 95.9 | 726 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 502.8 | 803.6 | 95.7 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.3 | 8.6
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 446 | 783.4 | 93.3 | 52 | 840 | 420.2 | 738.3 | 87.9 | 44 | -5.4 | 2015 | 2018 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 119.4 | 14.2
DAN3GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 251.1 | 438.8 | 93.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -4.7 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.3 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.2 | 153.9 | 93.1 | 174 | 170 | 76.2 | 156 | 94.6 | 172 | 1.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1001.9 | 1289.2 | 93.1 | 5946 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 320.2 | 426.8 | 92.8 | 1162 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.4 | 187.5 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.3 | 98.7 | 92.3 | 39 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 132 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 88.1 | 109.8 | 92 | 644 | 119 | 72.3 | 93 | 77.8 | 192 | -14.2 | 2016 | 2024 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 280.2 | 414.5 | 91.1 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -6.3 | -0.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.3 | 761 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.3 | 8.1
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 494.3 | 822.9 | 90.5 | 49 | 889 | 486.6 | 810.2 | 89 | 44 | -1.5 | 2017 | 2017 | 0 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 67.8 | 8.9
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.3 | 437.4 | 90.5 | 235 | 478 | 334.2 | 438.6 | 90.7 | 252 | 0.2 | 2017 | 2016 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.1 | 5.9
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.5 | 379.2 | 90 | 2133 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 0.4 | 2017 | 2017 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 11.7 | 11.1
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 56.7 | 96.9 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -18.4 | 2013 | 2024 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.5 | 94.4 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77 | 131.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -19 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 24.9 | 42.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 99.9 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 476.2 | 99.6 | 244 | 478 | - | 464 | 97.1 | 232 | -2.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.8 | 20
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1873.1 | 98.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -3.6 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 332 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 68.4 | 96.1 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -15.7 | 2014 | 2023 | 9 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 24.6 | 34.5 | 87.5 | 56.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.2 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.9
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.7 | 92.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -4.1 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15.2 | 15.8 | #N/A | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.7 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960 | 983
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## Tillery-Blewett
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 10 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1657.7 | 201.7 | 5099 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 529 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.3 | 216.5 | 144.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.6 | 216.5 | 144.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48 | 164.1 | 137.1 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | -0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126.2 | 244.3 | 120.4 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 231 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 274 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 75.8 | 119.8 | 112 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.5 | 113.3 | 106 | 52 | 108 | 64.2 | 112.4 | 105.1 | 51 | -0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96.1 | 214.7 | 105.8 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.8 | 503.7 | 103.3 | 69 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.8 | 503.7 | 103.3 | 70 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.1 | 306 | 102 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 423 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 503 | 804 | 95.7 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.7 | 8.6
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1690 | 1862.8 | 95.1 | 7752 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.2 | 14.8
TURNGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.8 | 189.7 | 94.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1035.9 | 1319.7 | 94.8 | 8025 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.6 | 155.9 | 94.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.2 | 365.7 | 93.8 | 580 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.9 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.8 | 188.3 | 93.1 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 433 | 741.5 | 93.1 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.4 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 71.5 | 9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 44.7 | 87.6 | 93 | 8 | 95 | 43.5 | 86.2 | 91.6 | 5 | -1.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 282.3 | 417.7 | 91.8 | 46 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.1 | 0.4
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.9 | 382.9 | 90.9 | 2162 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.5 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.4 | 12
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335 | 439.6 | 90.9 | 261 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 28.3 | 6.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.5 | 761.3 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.6 | 8.1
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.1 | 963.1 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CLIFGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 67.4 | 115.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -2.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 15.3 | 26.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464.7 | 97.2 | 232 | 478 | - | 464 | 97.1 | 232 | -0.1 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 84.3 | 17.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1805 | 94.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.9 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976 | 91.5 | 910 | 1067 | - | 976.7 | 91.5 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972.8 | 91.2 | 910 | 1067 | - | 973.3 | 91.2 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Tillery-Blewett
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.6
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLIFGM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.3 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976
CAT1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.8 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.1 | #N/A | 972.8
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 660.6 | 1675.7 | 203.9 | 5399 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.7 | 161.1 | 476 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.8 | 158.6 | 132.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.9 | 238.9 | 117.8 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 77 | 122.7 | 115 | 116 | 108 | 74.6 | 118.5 | 110.8 | 49 | -4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 96 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67 | 116.7 | 109.4 | 95 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 554.2 | 885.3 | 105.4 | 140 | 840 | 501.2 | 801.2 | 95.4 | 82 | -10 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 154 | 18.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 309.6 | 103.2 | 1772 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.8 | 209.3 | 103.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 335.2 | 496 | 101.9 | 49 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 335.2 | 496 | 101.9 | 50 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 434.9 | 723.3 | 99.8 | 124 | 717 | 386.2 | 643 | 88 | 44 | -11.8 | 2012 | 2018 | 6 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 138.6 | 20.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 462.1 | 838.2 | 99.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -9.5 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 145.5 | 17.3
OXFDGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303.7 | 315.1 | 97 | 567 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.5 | 90.2 | 96.1 | 24 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.5 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1052.8 | 1325.7 | 95.5 | 8925 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.6 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83 | 105.6 | 95.2 | 455 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 347.1 | 371.4 | 95.2 | 928 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 71.8 | 155.6 | 94.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.3 | 189 | 94.5 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.6 | 188.7 | 94.4 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.7 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1650.3 | 1825.8 | 93.4 | 7950 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1.7 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 225.2 | 13.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.6 | 391.4 | 93.2 | 2219 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.8 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 23.9 | 14.3
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 340.5 | 446.8 | 92.7 | 283 | 478 | 334.2 | 438.6 | 90.7 | 252 | -2 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 35.5 | 8.1
MCG2GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.6 | 97.4 | 91.7 | 25 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.3 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318 | 419.2 | 91.2 | 1241 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 52.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 421.5 | 721.5 | 90.6 | 52 | 796.7 | 435 | 745 | 93.5 | 87 | 2.9 | 2016 | 2015 | -1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 51.5 | 6.5
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.5 | 182.9 | 90.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.4 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 106.8 | 180.8 | 90.4 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -4.8 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 107 | 180.9 | 90.4 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -4.7 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 237.1 | 422.8 | 90.4 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -1.9 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 469.9 | 98.3 | 248 | 478 | - | 464 | 97.1 | 232 | -1.2 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 89.5 | 18.7
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1761.8 | 92.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.3 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 220.7 | 11.6
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.9 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.1 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.3 | 92.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.1 | 982.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980.5 | 91.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEPVP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 3 | Not in original screening
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
THALGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 654.2 | 1666.6 | 202.8 | 5402 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.5 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.4 | 157.7 | 131.7 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 5.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.3 | 237.9 | 117.3 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 76.9 | 122.3 | 114.6 | 125 | 108 | 74.6 | 118.5 | 110.8 | 49 | -3.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.7 | 116.3 | 109 | 100 | 108 | 64.2 | 112.4 | 105.1 | 51 | -3.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 94 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 545.3 | 871.2 | 103.7 | 133 | 840 | 501.2 | 801.2 | 95.4 | 82 | -8.3 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 139.9 | 16.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 208.9 | 308.3 | 102.8 | 1720 | 300 | 213.3 | 306.1 | 102 | 1886 | -0.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.2 | 208.3 | 102.7 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 334 | 492.8 | 101.1 | 41 | 478 | 333.2 | 503.2 | 103.2 | 68 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 334 | 492.8 | 101.1 | 42 | 478 | 333.2 | 503.2 | 103.2 | 69 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 454.7 | 824.9 | 98.2 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -7.9 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 132.2 | 15.7
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 426.7 | 709.9 | 97.7 | 90 | 717 | 386.2 | 643 | 88 | 44 | -9.7 | 2013 | 2018 | 5 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 125.2 | 18.5
CLI5GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 558 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.4 | 89.9 | 95.7 | 25 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.1 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.1 | 372.2 | 95.4 | 743 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 82.4 | 105.6 | 95.2 | 348 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 103.7 | 187.8 | 93.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 1.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103 | 187.5 | 93.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.8 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 70.2 | 153.9 | 93.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1021.2 | 1293.1 | 92.9 | 8615 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.9 | 388.3 | 92.4 | 2188 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.8 | 13.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 339.5 | 445.6 | 92.4 | 255 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.7 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 34.3 | 7.8
OCO3GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 212 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1631 | 1802.2 | 92 | 7820 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 201.6 | 11.7
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.2 | 97 | 91.3 | 26 | 108 | 45.8 | 93.5 | 87.4 | 5 | -3.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 53.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 315.9 | 415.5 | 90.3 | 1016 | 478 | 315.6 | 414.1 | 89.8 | 696 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.1 | 182 | 90 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.9 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 62.9 | 107.5 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 5.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 10.8 | 18.4
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 468.2 | 97.9 | 248 | 478 | - | 464 | 97.1 | 232 | -0.8 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 87.8 | 18.3
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.2 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.9 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1740.1 | 91.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3.4 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 199 | 10.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.4 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.4 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 981.2
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 977.9
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet