## Duke Summary
Transmission Facility | Worst-Case Information | Base | Anson | Roxboro | Tillery-Blewett | 1200ImportDukeCPLE_AEP | Roxboro_1200ImportDukeCPLE_AEP | 1200ImportDukeCPLE_AEPVP | Roxboro_1200ImportDukeCPLE_AEPVP | 600ImportDuke_AEP | Roxboro_600ImportDuke_AEP | 600ImportDuke_SOCO | Roxboro_600ImportDuke_SOCO | 600ImportDuke_TVA | Roxboro_600ImportDuke_TVA | 600ImportDuke_SCEG | Roxboro_600ImportDuke_SCEG | 600ImportDuke_SCPSA | Roxboro_600ImportDuke_SCPSA | 600ImportDuke_CPLE | Roxboro_600ImportDuke_CPLE | 600ImportCPLE_AEP | 600ImportCPLE_VP | 600ImportCPLE_SCEG | 600ImportCPLE_SCPSA | 600ImportCPLE_Duke | COMMENTS | Transmission Facility
| Post-Contingency Loading (MVA) | 70.9 | 81.8 | 87.5 | 73.1 | 64.8 | 79.2 | 65.8 | 76.1 | 74.7 | 91.4 | 78.1 | 97.9 | 76.2 | 96 | 87.9 | 107.6 | 88.9 | 108.6 | 90.4 | 93 | 60 | 60.2 | 74.7 | 75.6 | 58.1 | Cont Rating 58.5 MVA - Should use 12 Hour Rating 71.2 MVA
Wateree 100 kV Line | % Facility Rating | 113.3% | 130.7% | 139.7% | 116.8% | 111.5% | 127.1% | 105.3% | 121.7% | 119.4% | 145.9% | 124.9% | 156.9% | 121.8% | 153.8% | 140.5% | 172.5% | 142.1% | 174.1% | 144.3% | 148.3% | 102.6% | 102.9% | 119.5% | 121.1% | 99.4% | (75°, 90° Hot Line Crossing) 2/0 Cu Conductor Limited | Wateree 100 kV Line
(Wateree-Great Falls) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2012 | Hot Line Crossing Correction Only 78.1 MVA | (Wateree-Great Falls)
| Contingency | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Catawba 2 Generator | Cat1Gm w/ Catawba 2 Generator | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Catawba 2 Generator | Reconductor Required - Operating Guide Available
| Post-Contingency Loading (MVA) | 503.2 | 499.5 | 522.7 | 503.7 | 496 | 509.6 | 492.8 | 506.5 | 494.7 | 514.1 | 504 | 529.7 | 501.5 | 519.8 | 505 | 530.7 | 504.5 | 530.3 | 498.8 | 506 | 504.8 | 501.3 | 514.3 | 513.8 | 453 | 12 Hour Rating 478 MVA
Westport 230 kV Line | % Facility Rating | 103.2% | 102.6% | 107.4% | 103.3% | 101.9% | 104.8% | 101.1% | 104.1% | 101.5% | 105.5% | 103.4% | 109% | 102.9% | 106.9% | 103.6% | 109.2% | 103.4% | 109.1% | 102.2% | 103.7% | 103.7% | 102.8% | 105.7% | 105.6% | 92.8% | CT/5-M Ratio Limited | Westport 230 kV Line
(Marshall-McGuire) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2015 | 1272 ACSR Conductor 617.5 MVA | (Marshall-McGuire)
| Contingency | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | CT Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | 758.7 | 763.8 | 761 | 761.3 | 838.2 | 840.9 | 824.9 | 827.6 | 803.3 | 805.4 | 783.6 | 791.7 | 791 | 793 | 771.7 | 779.8 | 770.9 | 779 | 767.2 | 767.8 | 794.7 | 780.8 | 763.1 | 762.2 | - | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 90.3% | 90.9% | 90.6% | 90.6% | 99.8% | 100.1% | 98.2% | 98.5% | 95.6% | 95.9% | 93.3% | 94.3% | 94.2% | 94.4% | 91.9% | 92.8% | 91.8% | 92.7% | 91.3% | 91.4% | 94.6% | 93% | 90.8% | 90.7% | < 90% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 1 | Year Upgrade Required | 2017 | 2016 | 2016 | 2016 | 2012 | 2011 | 2012 | 2012 | 2014 | 2014 | 2015 | 2014 | 2015 | 2014 | 2016 | 2015 | 2016 | 2015 | 2016 | 2016 | 2014 | 2015 | 2016 | 2016 | - | Transformer 840 MVA (Stray Flux Issues???) | Transformer Bank 1
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | - | Increased Transformer Capacity Required in 2011
| Post-Contingency Loading (MVA) | 801.2 | 806.6 | 803.6 | 804 | 885.3 | 888.1 | 871.2 | 874.1 | 848.3 | 850.7 | 827.6 | 836.2 | 835.4 | 837.5 | 815 | 823.6 | 814.2 | 822.7 | 810.3 | 810.8 | 839.3 | 824.6 | 805.9 | 805 | 796.6 | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 95.4% | 96% | 95.7% | 95.7% | 105.4% | 105.7% | 103.7% | 104.1% | 101% | 101.3% | 98.5% | 99.5% | 99.5% | 99.7% | 97% | 98% | 96.9% | 97.9% | 96.5% | 96.5% | 99.9% | 98.2% | 95.9% | 95.8% | 94.8% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 2 | Year Upgrade Required | 2014 | 2014 | 2014 | 2014 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2012 | 2012 | 2012 | 2012 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2012 | 2012 | 2014 | 2014 | 2014 | Transformer 840 MVA (Stray Flux Issues???) | Transformer Bank 2
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Increased Transformer Capacity Required in 2011
| Post-Contingency Loading (MVA) | 1862.7 | 1859.4 | 1913.2 | 1862.8 | 1825.8 | 1860.3 | 1802.2 | 1837.5 | 1792.4 | 1844.9 | 1813.8 | 1869.7 | 1809.1 | 1859.9 | 1806.1 | 1858.7 | 1800.3 | 1853.1 | 1772.5 | 1783.1 | 1896.2 | 1872.3 | 1909.8 | 1904.2 | 1971.6 | 12 Hour Rating 1904.3 MVA
Godbey 500 kV Line | % Facility Rating | 95.1% | 95% | 98.3% | 95.1% | 93.4% | 95.7% | 92% | 94.2% | 91.3% | 94.4% | 92.6% | 95.6% | 92.3% | 95.4% | 92.1% | 95.2% | 91.8% | 94.8% | 90% | 91% | 97.2% | 95.7% | 98.1% | 97.7% | 101.9% | CT/5 Ratio Limited | Godbey 500 kV Line
(Woodleaf-Pleasant Garden) | Year Upgrade Required | 2014 | 2014 | 2012 | 2014 | 2015 | 2014 | 2016 | 2015 | 2016 | 2014 | 2015 | 2014 | 2016 | 2014 | 2016 | 2014 | 2016 | 2014 | 2017 | 2016 | 2013 | 2014 | 2012 | 2013 | 2011 | 2-2515 ACSR Conductor 4718 MVA | (Woodleaf-Pleasant Garden)
| Contingency | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Cat1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | CT Upgrade pushes out to 2018
| Post-Contingency Loading (MVA) | 1320.5 | 1319 | 1289.2 | 1319.7 | 1325.7 | 1299 | 1293.1 | 1266.8 | - | - | 1272.4 | - | 1270.2 | - | - | - | - | - | - | - | 1393.7 | 1361.6 | 1385.8 | 1370 | 1448.3 | PEC Phase Angle Rating 1350 MVA
Richmond 500 kV Line | % Facility Rating | 94.9% | 95.1% | 93.1% | 94.8% | 95.5% | 93.7% | 92.9% | 91.1% | < 90% | < 90% | 91.3% | < 90% | 91.1% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 100.7% | 98.1% | 100.5% | 99.3% | 105.4% | PEC Phase Angle Requirement Limited | Richmond 500 kV Line
(Richmond-Newport) | Year Upgrade Required | 2014 | 2014 | 2015 | 2014 | 2014 | 2015 | 2015 | 2016 | - | - | 2016 | - | 2016 | - | - | - | - | - | - | - | 2011 | 2012 | 2011 | 2012 | 2011 | 3000 A Communication Trap at Richmond (PEC) 2598 MVA | (Richmond-Newport)
| Contingency | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | - | - | Mcg1Gm w/ Godbey 500 kV Line | - | Mcg1Gm w/ Godbey 500 kV Line | - | - | - | - | - | - | - | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Phase Angle Solution required in 2011
| Post-Contingency Loading (MVA) | 101.5 | 103.1 | 100.5 | 101.6 | 109.3 | 108.6 | 107.8 | 107.1 | 105.7 | 104.8 | 104.2 | 103.2 | 107.4 | 105.1 | 101.8 | 100.8 | 101.7 | 100.7 | 101.9 | 101.6 | 105 | 103.5 | 101.1 | 100.9 | 100.1 | LTE Rating 108.3 MVA
Horseshoe 115/100 kV | % Facility Rating | 93.8% | 95.2% | 92.8% | 93.8% | 100.9% | 100.3% | 99.5% | 98.9% | 97.6% | 96.7% | 96.2% | 95.3% | 99.2% | 97% | 94% | 93.1% | 93.9% | 93% | 94.1% | 93.8% | 96.9% | 95.6% | 93.3% | 93.2% | 92.4% | 300 Cu Limited | Horseshoe 115/100 kV
Transformer | Year Upgrade Required | 2015 | 2014 | 2015 | 2015 | 2011 | 2011 | 2012 | 2012 | 2013 | 2013 | 2013 | 2014 | 2012 | 2013 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2013 | 2014 | 2015 | 2015 | 2015 | Transformer 134.5 MVA | Transformer
| Contingency | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | 300 Cu, 1/2" Cu Pipe, 600 Cu Switch Upgrades pushes to 2022
| Post-Contingency Loading (MVA) | - | - | 783.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 760.2 | - | 770.8 | 767.7 | 804.1 | 12 Hour Rating 840 MVA
Parkwoood 500/230 kV | % Facility Rating | < 90% | < 90% | 93.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.5% | < 90% | 91.8% | 91.4% | 95.7% | Transformer Limited | Parkwoood 500/230 kV
Transformer Bank 5 | Year Upgrade Required | - | - | 2015 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2017 | - | 2016 | 2016 | 2014 | Transformer 840 MVA | Transformer Bank 5
| Contingency | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Increased Transformer Capacity Required in 2014
| Post-Contingency Loading (MVA) | 745 | 737.8 | 790.2 | 741.5 | 721.5 | 752.9 | - | 736.2 | - | 745 | - | 757.2 | - | 754.5 | - | 759.9 | - | 752.5 | - | - | 767.1 | 750.2 | 777.5 | 774.6 | 811.3 | 12 Hour Rating 796.7 MVA
Parkwoood 500/230 kV | % Facility Rating | 93.5% | 92.6% | 99.2% | 93.1% | 90.6% | 94.5% | < 90% | 92.4% | < 90% | 93.5% | < 90% | 95% | < 90% | 94.7% | < 90% | 95.4% | < 90% | 94.5% | < 90% | < 90% | 96.3% | 94.2% | 97.6% | 97.2% | 101.8% | CT/5 Ratio Limited | Parkwoood 500/230 kV
Transformer Bank 6 | Year Upgrade Required | 2015 | 2015 | 2012 | 2015 | 2016 | 2014 | - | 2014 | - | 2015 | - | 2014 | - | 2014 | - | 2014 | - | 2014 | - | - | 2013 | 2015 | 2013 | 2013 | 2011 | Transformer 1152.7 MVA | Transformer Bank 6
| Contingency | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | CT Upgrade pushes out to 2024
| Post-Contingency Loading (MVA) | 419.2 | 412.9 | 414.5 | 417.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 412.7 | 417.1 | - | - | 425.5 | 12 Hour Rating 452.5 MVA
London Creek 230 kV | % Facility Rating | 92.1% | 90.8% | 91.1% | 91.8% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.7% | 91.7% | < 90% | < 90% | 93.6% | 795 ACSR Conductor Limited | London Creek 230 kV
(Peach Valley-Riverview) | Year Upgrade Required | 2016 | 2016 | 2016 | 2016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 2016 | - | - | 2015 | Reconductor Required in 2015 | (Peach Valley-Riverview)
| Contingency | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | - | - | Oco1Gm w/ London Creek 230 kV Line
| Post-Contingency Loading (MVA) | 438.6 | 438.8 | 437.4 | 439.6 | 446.8 | 445.8 | 445.6 | 444.8 | 443 | 441.8 | 441.1 | 440 | 441 | 440.5 | 438.9 | 437.9 | 439.2 | 438 | 438.8 | 438.4 | 442.4 | 441.1 | 438.2 | 438.5 | 435.9 | 12 Hour Rating 478 MVA
Dooley 230 kV Line | % Facility Rating | 90.7% | 90.8% | 90.5% | 90.9% | 92.7% | 92.6% | 92.4% | 92.3% | 91.8% | 91.7% | 91.5% | 91.4% | 91.6% | 91.5% | 91% | 90.9% | 91.1% | 90.9% | 90.9% | 90.8% | 91.6% | 91.3% | 90.8% | 90.8% | 90.3% | CT/5-M Ratio Limited | Dooley 230 kV Line
(Marshall-Winecoff) | Year Upgrade Required | 2016 | 2016 | 2017 | 2016 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | 1272 ACSR Conductor 617.5 MVA | (Marshall-Winecoff)
| Contingency | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | CT Upgrade pushes out to 2024
| Post-Contingency Loading (MVA) | 380.8 | 393.5 | 379.2 | 382.9 | 391.4 | 389.7 | 388.3 | 386.6 | 384.5 | 382.9 | 388.2 | 384.3 | 387.4 | 385.7 | 387.6 | 383.6 | 384.8 | 380.9 | - | - | 387.8 | 384.7 | 391 | 388.2 | 390.1 | Cont Rating 436.9 MVA - Should use 12 Hour Rating 478 MVA
Sandy Ridge 230 kV Line | % Facility Rating | 90.4% | 93.9% | 90% | 90.9% | 93.2% | 92.9% | 92.4% | 92% | 91.4% | 91.1% | 92.4% | 91.4% | 92.2% | 91.8% | 92.2% | 91.3% | 91.5% | 90.6% | < 90% | < 90% | 92.2% | 91.4% | 93% | 92.3% | 93% | CT/5 Ratio, CT/5-M Ratio, and 51XYZ Relay Limited | Sandy Ridge 230 kV Line
(Newport-Morning Star) | Year Upgrade Required | 2017 | 2015 | 2017 | 2016 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | - | - | 2016 | 2016 | 2015 | 2016 | 2015 | 954 ACSR Conductor 506.7 MVA | (Newport-Morning Star)
| Contingency | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | - | - | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | 12 Hour Rating pushes out to 2019
| Post-Contingency Loading (MVA) | - | 421.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 398.8 | Cont Rating 437 MVA - Should use 12 Hour Rating 482 MVA
Harrisburg 230 kV Line | % Facility Rating | < 90% | 96.4% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 91.5% | 750 Cu and 1" Cu Pipe Limited | Harrisburg 230 kV Line
(Harrisburg-Oakboro) | Year Upgrade Required | - | 2013 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 954 ACSR Conductor 506.7 MVA | (Harrisburg-Oakboro)
| Contingency | - | Oco3Gm w/ Harrisburg 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Bel1Gm w/ Harrisburg 230 kV Line | 12 Hour Rating pushes out to 2018
| Post-Contingency Loading (MVA) | - | 87.1 | 88.7 | - | - | 86.7 | - | 86.8 | 86.5 | 90.4 | 89.2 | 93.1 | 87.3 | 91.2 | 97.5 | 101.4 | 92.5 | 96.4 | 90.3 | 91 | - | - | 93.5 | 88.5 | - | 12 Hour Rating 96 MVA - Should use 12 Hour Rating 109.3 MVA
Clark Hill 115/100 kV | % Facility Rating | < 90% | 90.7% | 92.4% | < 90% | < 90% | 90.3% | < 90% | 90.5% | 90.1% | 94.2% | 93% | 91% | 90.9% | 95% | 101.6% | 105.6% | 96.4% | 100.4% | 94% | 94.8% | < 90% | < 90% | 97.4% | 92.2% | < 90% | 556 ACSR Limited (Clearances to be measured) | Clark Hill 115/100 kV
Transformer | Year Upgrade Required | - | 2016 | 2015 | - | - | 2017 | - | 2017 | 2017 | 2015 | 2015 | 2013 | 2016 | 2014 | 2011 | 2011 | 2013 | 2011 | 2015 | 2014 | - | - | 2013 | 2016 | - | Transformer 173.3 MVA | Transformer
| Contingency | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | Oco1Gm w/ Whitewater 500 kV Line | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | 12 Hour Rating Correction pushes out to 2015
| Post-Contingency Loading (MVA) | - | - | 822.9 | - | - | - | - | - | - | - | - | 823.8 | - | 819.5 | - | 829.3 | - | 828.8 | - | - | - | - | - | - | - | 12 Hour Rating 889 MVA
Stamey 230 kV Line | % Facility Rating | < 90% | < 90% | 90.5% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.8% | < 90% | 90.3% | < 90% | 91.4% | < 90% | 91.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 1600 Al Switch Limited | Stamey 230 kV Line
(Marshall-Stamey) | Year Upgrade Required | - | - | 2017 | - | - | - | - | - | - | - | - | 2016 | - | 2017 | - | 2016 | - | 2016 | - | - | - | - | - | - | - | 2-954 ACSR Conductor 1176 MVA | (Marshall-Stamey)
| Contingency | - | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | - | - | - | - | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | - | - | - | - | 1600 Al Switch Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | - | - | - | - | 723.3 | 725.9 | 709.9 | 712.6 | 688 | 690.2 | 668.2 | 676.3 | 675.6 | 677.6 | 656.1 | 664.3 | - | 663.5 | - | - | 679.4 | 665.3 | - | - | - | 12 Hour Rating 717 MVA
Clingman 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 99.8% | 100.3% | 97.7% | 98.2% | 94.6% | 95% | 91.8% | 93% | 92.8% | 93.2% | 90% | 91.3% | < 90% | 91.1% | < 90% | < 90% | 93.3% | 91.2% | < 90% | < 90% | < 90% | CT/5 Ratio Limited | Clingman 230 kV Line
(Antioch-Mitchell River) | Year Upgrade Required | - | - | - | - | 2012 | 2011 | 2013 | 2012 | 2014 | 2014 | 2016 | 2015 | 2015 | 2015 | 2017 | 2016 | - | 2016 | - | - | 2015 | 2016 | - | - | - | 2-954 ACSR Conductor 1176 MVA | (Antioch-Mitchell River)
| Contingency | - | - | - | - | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | - | Mar3Gm w/ Clingman 230 kV Line | - | - | Bel1Gm w/ Clingman 230 kV Line | Bel1Gm w/ Clingman 230 kV Line | - | - | - | CT Upgrade pushes out to 2026
| Post-Contingency Loading (MVA) | - | - | - | - | 95.5 | 95.4 | 95 | 94.8 | 94.3 | 94.1 | 94.2 | 94 | 94.7 | 94.5 | - | - | - | - | - | - | 93.9 | - | - | - | - | Cont Rating 108.3 MVA - Should use 12 Hour Rating 118.6 MVA
Rugby 100 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 91.8% | 91.6% | 91.2% | 91.1% | 90.5% | 90.4% | 90.5% | 90.3% | 91% | 90.8% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.1% | < 90% | < 90% | < 90% | < 90% | 300 Cu Limited | Rugby 100 kV Line
(Horseshoe-Pisgah) | Year Upgrade Required | - | - | - | - | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2016 | 2016 | - | - | - | - | - | - | 2017 | - | - | - | - | 477 ACSR Conductor 139.4 MVA | (Horseshoe-Pisgah)
| Contingency | - | - | - | - | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | - | - | - | - | - | - | Cli5Gm w/ Asheville 115 kV Line | - | - | - | - | 12 Hour Rating pushes out to 2020
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 449 | 12 Hour Rating 478 MVA
Pleasant Garden 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 92.9% | CT/5 Ratio Limited | Pleasant Garden 230 kV Line
(Belews Creek-Bob White Tap) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2015 | 2156 ACSR Conductor 851.7 MVA | (Belews Creek-Bob White Tap)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ Godbey 500 kV Line | CT Upgrade pushes out to 2039
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 448.6 | 12 Hour Rating 478 MVA
Jocassee 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 91.3% | CT/5 Ratio Limited | Jocassee 230 kV Line
(Oconee-Jocassee) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 2156 ACSR Conductor 851.7 MVA | (Oconee-Jocassee)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ Katoma 500 kV Line | CT Upgrade pushes out to 2030

## Base
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 133 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 56 | Not in original screening
[25 empty] | 189 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
DAN3GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.1 | 161.3 | 542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.4 | 164.1 | 136.8 | 129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 247.2 | 120 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 74.6 | 118.5 | 110.8 | 49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96 | 214.3 | 105.4 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.2 | 112.4 | 105.1 | 51 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.2 | 503.2 | 103.2 | 68 | 478 | 250.2 | 388 | 79 | 1 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.2 | 503.2 | 103.2 | 69 | 478 | 250.2 | 388 | 79 | 2 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.3 | 306.1 | 102 | 1886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.2 | 314.8 | 96.9 | 423 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2013 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 501.2 | 801.2 | 95.4 | 82 | 840 | 457.1 | 731.3 | 87.1 | 44 | -8.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 69.9 | 8.3
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 111 | -14.8 | 2014 | 2019 | 5 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.1 | 14.8
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.9 | 189.9 | 95 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.2 | 156 | 94.6 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 435 | 745 | 93.5 | 87 | 796.7 | 390.3 | 670 | 84.1 | 44 | -9.4 | 2015 | 2016 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 75 | 9.4
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.5 | 364.5 | 93.5 | 554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.5 | 139.4 | 93.2 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 71 | 188.2 | 92.9 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 452.5 | 277.7 | 420.8 | 91.4 | 45 | -0.7 | 2016 | 2012 | -4 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -1.6 | 0.7
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 43.5 | 86.2 | 91.6 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.2 | 438.6 | 90.7 | 252 | 478 | 313 | 411.3 | 84.6 | 44 | -6.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.3 | 6.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 478 | 330.1 | 367.5 | 78.9 | 1124 | -11.5 | 2017 | 2015 | -2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 13.3 | 11.5
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 418 | 758.7 | 90.3 | 44 | 840 | 381.2 | 692.7 | 82.5 | 40 | -7.8 | 2017 | 2017 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 66 | 7.8
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.3 | 963.3 | 90.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.1 | 165.2 | 90.3 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 27 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 3 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 30 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening
[25 empty] | 34 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 65.9 | 112.6 | 910 | 58.5 | - | 52.1 | 89.1 | 706 | -23.5 | 2011 | 2013 | 2 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 13.8 | 23.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464 | 97.1 | 232 | 478 | - | 380.4 | 79.6 | 100 | -17.5 | 2013 | 2019 | 6 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 83.6 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1804.3 | 94.8 | 910 | 1904.3 | - | 1541.1 | 80.9 | 868 | -13.9 | 2014 | 2018 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.2 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976.7 | 91.5 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.3 | 91.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 11 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 6 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Base Case
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.3 | 94.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.1 | 91.6 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976.7
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.8 | 91.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.3 | #N/A | 973.3
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Anson
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.4 | 1657.6 | 201.7 | 5292 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 511 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 110.3 | 220.4 | 147 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 109.7 | 220.4 | 147 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.9 | 163.8 | 136.8 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 617 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 660 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 244 | 120.2 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 80 | 124.6 | 116.3 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -5.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 65.2 | 116.7 | 109.1 | 87 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.8 | 214.2 | 105.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 328.9 | 499.5 | 102.6 | 61 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 328.9 | 499.5 | 102.6 | 62 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.9 | 305.8 | 101.9 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 49.2 | 92.5 | 98.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -6.6 | 2012 | 2016 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 299.9 | 315.1 | 97 | 429 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 285.6 | 421.8 | 96.4 | 171 | 437 | 249.4 | 367.6 | 83.9 | 85 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 676 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 285.6 | 421.8 | 96.4 | 215 | 437 | 248.6 | 366.8 | 83.9 | 128 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 71.9 | 24.2
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.2 | 192.2 | 96.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.4 | 192 | 96 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 504.6 | 806.6 | 96 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.6 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 75.3 | 8.9
OCO3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1039.7 | 1319 | 95.1 | 8318 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1685.2 | 1859.4 | 95 | 7802 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.1 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 258.8 | 14.7
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76 | 155.8 | 94.4 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 146.4 | 187.9 | 94 | 54 | 200 | 140 | 176.3 | 88.1 | 12 | -5.9 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 351.8 | 393.5 | 93.9 | 1999 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -3.5 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 26 | 15
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 188.1 | 93 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 430.8 | 737.8 | 92.6 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.9 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 67.8 | 8.5
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.7 | 97.9 | 91.5 | 34 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.1 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420.8 | 763.8 | 90.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.6 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 71.1 | 8.4
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.4 | 438.8 | 90.8 | 258 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.5 | 6.2
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 279 | 412.9 | 90.8 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -7.9 | -0.6
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.7 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 53 | 90.6 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -12.1 | 2016 | 2024 | 8 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 73.3 | 125.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -12.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 21.2 | 36.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 459.8 | 96.2 | 232 | 478 | - | 464 | 97.1 | 232 | 0.9 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 79.4 | 16.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1800.2 | 94.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 259.1 | 13.6
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.4 | 91.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.2 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Anson
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CLI5GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
CLI5GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.1 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.4
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLI5GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 974.2
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.1 | 90.7 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.4 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.6 | 14.1 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 7 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 14 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
NANTGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1656.4 | 201.5 | 5676 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.3 | 161.4 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 765 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 808 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.8 | 163.2 | 136.2 | 94 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.5 | 243.2 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 82 | 126.3 | 117.9 | 68 | 108 | 74.6 | 118.5 | 110.8 | 49 | -7.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.8 | 117.5 | 109.9 | 89 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345 | 522.7 | 107.4 | 94 | 478 | 333.2 | 503.2 | 103.2 | 68 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345 | 522.7 | 107.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 69 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.5 | 213.6 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51.5 | 94.4 | 100.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -8.6 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76 | 134.1 | 100 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 461.7 | 790.2 | 99.2 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -5.7 | 2012 | 2015 | 3 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 120.2 | 15.1
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213 | 296.2 | 98.7 | 1830 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.3 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1751.8 | 1913.2 | 98.3 | 7908 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -3.2 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 312.6 | 18
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.9 | 195.4 | 97.7 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.2 | 195.1 | 97.6 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.8 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 304.2 | 314.8 | 96.9 | 614 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 148 | 193.3 | 96.7 | 62 | 200 | 140 | 176.3 | 88.1 | 12 | -8.6 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 343.3 | 373.9 | 95.9 | 726 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 502.8 | 803.6 | 95.7 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.3 | 8.6
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 446 | 783.4 | 93.3 | 52 | 840 | 420.2 | 738.3 | 87.9 | 44 | -5.4 | 2015 | 2018 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 119.4 | 14.2
DAN3GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 251.1 | 438.8 | 93.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -4.7 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.3 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.2 | 153.9 | 93.1 | 174 | 170 | 76.2 | 156 | 94.6 | 172 | 1.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1001.9 | 1289.2 | 93.1 | 5946 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 320.2 | 426.8 | 92.8 | 1162 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.4 | 187.5 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.3 | 98.7 | 92.3 | 39 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 132 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 88.1 | 109.8 | 92 | 644 | 119 | 72.3 | 93 | 77.8 | 192 | -14.2 | 2016 | 2024 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 280.2 | 414.5 | 91.1 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -6.3 | -0.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.3 | 761 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.3 | 8.1
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 494.3 | 822.9 | 90.5 | 49 | 889 | 486.6 | 810.2 | 89 | 44 | -1.5 | 2017 | 2017 | 0 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 67.8 | 8.9
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.3 | 437.4 | 90.5 | 235 | 478 | 334.2 | 438.6 | 90.7 | 252 | 0.2 | 2017 | 2016 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.1 | 5.9
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.5 | 379.2 | 90 | 2133 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 0.4 | 2017 | 2017 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 11.7 | 11.1
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 56.7 | 96.9 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -18.4 | 2013 | 2024 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.5 | 94.4 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77 | 131.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -19 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 24.9 | 42.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 99.9 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 476.2 | 99.6 | 244 | 478 | - | 464 | 97.1 | 232 | -2.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.8 | 20
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1873.1 | 98.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -3.6 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 332 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 68.4 | 96.1 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -15.7 | 2014 | 2023 | 9 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 24.6 | 34.5 | 87.5 | 56.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.2 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.9
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.7 | 92.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -4.1 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15.2 | 15.8 | #N/A | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.7 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960 | 983
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## Tillery-Blewett
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 10 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1657.7 | 201.7 | 5099 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 529 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.3 | 216.5 | 144.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.6 | 216.5 | 144.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48 | 164.1 | 137.1 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | -0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126.2 | 244.3 | 120.4 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 231 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 274 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 75.8 | 119.8 | 112 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.5 | 113.3 | 106 | 52 | 108 | 64.2 | 112.4 | 105.1 | 51 | -0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96.1 | 214.7 | 105.8 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.8 | 503.7 | 103.3 | 69 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.8 | 503.7 | 103.3 | 70 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.1 | 306 | 102 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 423 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 503 | 804 | 95.7 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.7 | 8.6
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1690 | 1862.8 | 95.1 | 7752 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.2 | 14.8
TURNGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.8 | 189.7 | 94.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1035.9 | 1319.7 | 94.8 | 8025 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.6 | 155.9 | 94.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.2 | 365.7 | 93.8 | 580 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.9 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.8 | 188.3 | 93.1 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 433 | 741.5 | 93.1 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.4 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 71.5 | 9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 44.7 | 87.6 | 93 | 8 | 95 | 43.5 | 86.2 | 91.6 | 5 | -1.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 282.3 | 417.7 | 91.8 | 46 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.1 | 0.4
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.9 | 382.9 | 90.9 | 2162 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.5 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.4 | 12
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335 | 439.6 | 90.9 | 261 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 28.3 | 6.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.5 | 761.3 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.6 | 8.1
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.1 | 963.1 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CLIFGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 67.4 | 115.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -2.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 15.3 | 26.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464.7 | 97.2 | 232 | 478 | - | 464 | 97.1 | 232 | -0.1 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 84.3 | 17.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1805 | 94.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.9 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976 | 91.5 | 910 | 1067 | - | 976.7 | 91.5 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972.8 | 91.2 | 910 | 1067 | - | 973.3 | 91.2 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Tillery-Blewett
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.6
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLIFGM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.3 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976
CAT1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.8 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.1 | #N/A | 972.8
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 660.6 | 1675.7 | 203.9 | 5399 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.7 | 161.1 | 476 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.8 | 158.6 | 132.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.9 | 238.9 | 117.8 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 77 | 122.7 | 115 | 116 | 108 | 74.6 | 118.5 | 110.8 | 49 | -4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 96 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67 | 116.7 | 109.4 | 95 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 554.2 | 885.3 | 105.4 | 140 | 840 | 501.2 | 801.2 | 95.4 | 82 | -10 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 154 | 18.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 309.6 | 103.2 | 1772 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.8 | 209.3 | 103.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 335.2 | 496 | 101.9 | 49 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 335.2 | 496 | 101.9 | 50 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 434.9 | 723.3 | 99.8 | 124 | 717 | 386.2 | 643 | 88 | 44 | -11.8 | 2012 | 2018 | 6 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 138.6 | 20.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 462.1 | 838.2 | 99.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -9.5 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 145.5 | 17.3
OXFDGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303.7 | 315.1 | 97 | 567 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.5 | 90.2 | 96.1 | 24 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.5 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1052.8 | 1325.7 | 95.5 | 8925 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.6 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83 | 105.6 | 95.2 | 455 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 347.1 | 371.4 | 95.2 | 928 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 71.8 | 155.6 | 94.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.3 | 189 | 94.5 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.6 | 188.7 | 94.4 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.7 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1650.3 | 1825.8 | 93.4 | 7950 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1.7 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 225.2 | 13.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.6 | 391.4 | 93.2 | 2219 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.8 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 23.9 | 14.3
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 340.5 | 446.8 | 92.7 | 283 | 478 | 334.2 | 438.6 | 90.7 | 252 | -2 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 35.5 | 8.1
MCG2GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.6 | 97.4 | 91.7 | 25 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.3 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318 | 419.2 | 91.2 | 1241 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 52.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 421.5 | 721.5 | 90.6 | 52 | 796.7 | 435 | 745 | 93.5 | 87 | 2.9 | 2016 | 2015 | -1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 51.5 | 6.5
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.5 | 182.9 | 90.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.4 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 106.8 | 180.8 | 90.4 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -4.8 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 107 | 180.9 | 90.4 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -4.7 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 237.1 | 422.8 | 90.4 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -1.9 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 469.9 | 98.3 | 248 | 478 | - | 464 | 97.1 | 232 | -1.2 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 89.5 | 18.7
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1761.8 | 92.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.3 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 220.7 | 11.6
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.9 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.1 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.3 | 92.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.1 | 982.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980.5 | 91.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_1200ImportDukeCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 16 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.8 | 1670.8 | 203.3 | 5380 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185 | 378.6 | 161.1 | 476 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.6 | 216.4 | 144.3 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.9 | 216.5 | 144.3 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.2 | 162.4 | 135.6 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.6 | 79.2 | 127.1 | 338 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -13.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.6 | 79.2 | 127.1 | 381 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -13.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.6 | 127.7 | 119.5 | 169 | 108 | 74.6 | 118.5 | 110.8 | 49 | -8.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.2 | 242.5 | 119.5 | 132 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.5 | 120.1 | 112.5 | 114 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 555.9 | 888.1 | 105.7 | 165 | 840 | 501.2 | 801.2 | 95.4 | 82 | -10.3 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 156.8 | 18.6
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.1 | 212.9 | 104.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 344.1 | 509.6 | 104.8 | 98 | 478 | 333.2 | 503.2 | 103.2 | 68 | -1.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 121.6 | 25.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 344.1 | 509.6 | 104.8 | 99 | 478 | 333.2 | 503.2 | 103.2 | 69 | -1.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 121.6 | 25.8
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.5 | 95.5 | 101.6 | 39 | 95 | 43.5 | 86.2 | 91.6 | 5 | -10 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 436.5 | 725.9 | 100.3 | 125 | 717 | 386.2 | 643 | 88 | 44 | -12.3 | 2011 | 2018 | 7 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 141.2 | 21.1
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60.8 | 108.6 | 100.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -6.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 19.1 | 17.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60.8 | 108.6 | 100.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -6.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 19.1 | 17.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 463.6 | 840.9 | 100.1 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -9.8 | 2011 | 2017 | 6 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 148.2 | 17.6
CLIFGM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 297.4 | 99.1 | 1655 | 300 | 213.3 | 306.1 | 102 | 1886 | 2.9 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303 | 314.8 | 96.9 | 672 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.9 | 375.6 | 96.3 | 934 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.8 | 191.6 | 95.8 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.8 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.1 | 191.4 | 95.7 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.9 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1695.7 | 1860.3 | 95.7 | 8114 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 259.7 | 15.4
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49 | 101.3 | 94.8 | 36 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 440.2 | 752.9 | 94.5 | 53 | 796.7 | 435 | 745 | 93.5 | 87 | -1 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 82.9 | 10.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 150.4 | 188.8 | 94.4 | 156 | 200 | 140 | 176.3 | 88.1 | 12 | -6.3 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1018.9 | 1299 | 93.7 | 8553 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 1.2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 31.9 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.2 | 389.7 | 92.9 | 2220 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.5 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 22.2 | 14
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 339.7 | 445.8 | 92.6 | 260 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.9 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 34.5 | 8
WYLIGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 69.9 | 186.6 | 92.3 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.6 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.7 | 151.8 | 92 | 87 | 170 | 76.2 | 156 | 94.6 | 172 | 2.6 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 95.4 | 91.6 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.7 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.7 | 15.7
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 95.4 | 91.6 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.7 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.7 | 15.7
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 58.2 | 165.2 | 90.5 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.2 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.2 | 94.2 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.6 | 119.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.5 | 30
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479.1 | 100.2 | 248 | 478 | - | 464 | 97.1 | 232 | -3.1 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.7 | 20.6
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1812 | 95.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.4 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 270.9 | 14.3
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.6 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.4 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.2 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.4 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 982.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.3 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.4
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.7 | 90.3 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.2 | 13.7 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEPVP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 3 | Not in original screening
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
THALGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 654.2 | 1666.6 | 202.8 | 5402 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.5 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.4 | 157.7 | 131.7 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 5.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.3 | 237.9 | 117.3 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 76.9 | 122.3 | 114.6 | 125 | 108 | 74.6 | 118.5 | 110.8 | 49 | -3.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.7 | 116.3 | 109 | 100 | 108 | 64.2 | 112.4 | 105.1 | 51 | -3.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 94 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 545.3 | 871.2 | 103.7 | 133 | 840 | 501.2 | 801.2 | 95.4 | 82 | -8.3 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 139.9 | 16.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 208.9 | 308.3 | 102.8 | 1720 | 300 | 213.3 | 306.1 | 102 | 1886 | -0.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.2 | 208.3 | 102.7 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 334 | 492.8 | 101.1 | 41 | 478 | 333.2 | 503.2 | 103.2 | 68 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 334 | 492.8 | 101.1 | 42 | 478 | 333.2 | 503.2 | 103.2 | 69 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 454.7 | 824.9 | 98.2 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -7.9 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 132.2 | 15.7
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 426.7 | 709.9 | 97.7 | 90 | 717 | 386.2 | 643 | 88 | 44 | -9.7 | 2013 | 2018 | 5 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 125.2 | 18.5
CLI5GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 558 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.4 | 89.9 | 95.7 | 25 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.1 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.1 | 372.2 | 95.4 | 743 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 82.4 | 105.6 | 95.2 | 348 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 103.7 | 187.8 | 93.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 1.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103 | 187.5 | 93.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.8 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 70.2 | 153.9 | 93.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1021.2 | 1293.1 | 92.9 | 8615 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.9 | 388.3 | 92.4 | 2188 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.8 | 13.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 339.5 | 445.6 | 92.4 | 255 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.7 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 34.3 | 7.8
OCO3GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 212 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1631 | 1802.2 | 92 | 7820 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 201.6 | 11.7
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.2 | 97 | 91.3 | 26 | 108 | 45.8 | 93.5 | 87.4 | 5 | -3.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 53.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 315.9 | 415.5 | 90.3 | 1016 | 478 | 315.6 | 414.1 | 89.8 | 696 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.1 | 182 | 90 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.9 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 62.9 | 107.5 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 5.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 10.8 | 18.4
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 468.2 | 97.9 | 248 | 478 | - | 464 | 97.1 | 232 | -0.8 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 87.8 | 18.3
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.2 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.9 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1740.1 | 91.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3.4 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 199 | 10.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.4 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.4 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 981.2
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 977.9
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_1200ImprtDukeCPLE_AEPVP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 16 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 656.3 | 1660.2 | 202 | 5338 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185 | 378.6 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.1 | 216.6 | 144.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.3 | 216.6 | 144.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 46.8 | 161.4 | 134.7 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.4 | 76.1 | 121.7 | 322 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -8.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.4 | 76.1 | 121.7 | 365 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -8.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.5 | 127.4 | 119.2 | 168 | 108 | 74.6 | 118.5 | 110.8 | 49 | -8.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 124.7 | 241.4 | 118.9 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.2 | 119.7 | 112.1 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 94.6 | 211.8 | 104.3 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 547.1 | 874.1 | 104.1 | 137 | 840 | 501.2 | 801.2 | 95.4 | 82 | -8.7 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 142.8 | 17
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 343 | 506.5 | 104.1 | 92 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118.5 | 25.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 343 | 506.5 | 104.1 | 93 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118.5 | 25.1
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.5 | 95.2 | 101.3 | 39 | 95 | 43.5 | 86.2 | 91.6 | 5 | -9.7 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 208.9 | 296.9 | 99 | 1621 | 300 | 213.3 | 306.1 | 102 | 1886 | 3 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60 | 107.1 | 98.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.1 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 17.6 | 16.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60 | 107.1 | 98.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.1 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 17.6 | 16.2
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 456.2 | 827.6 | 98.5 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -8.2 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 134.9 | 16
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 428.3 | 712.6 | 98.2 | 122 | 717 | 386.2 | 643 | 88 | 44 | -10.2 | 2012 | 2018 | 6 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 127.9 | 19
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.7 | 314.8 | 96.9 | 524 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.1 | 190.3 | 95.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.4 | 190.1 | 95.1 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.3 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 149.9 | 188.9 | 94.5 | 181 | 200 | 140 | 176.3 | 88.1 | 12 | -6.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.7 | 100.8 | 94.4 | 34 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 368.3 | 94.4 | 739 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1677.1 | 1837.5 | 94.2 | 8212 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.9 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 236.9 | 13.9
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 31.8 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 430.4 | 736.2 | 92.4 | 52 | 796.7 | 435 | 745 | 93.5 | 87 | 1.1 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 66.2 | 8.3
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 338.9 | 444.8 | 92.3 | 249 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.6 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 33.5 | 7.7
WYLIGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.7 | 92.2 | 172 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.5 | 386.6 | 92 | 2233 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.6 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 19.1 | 13.1
DAN3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 69.5 | 185.6 | 91.7 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.2 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 94.8 | 91.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.2 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.1 | 15.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 94.8 | 91.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.2 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.1 | 15.2
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 986.8 | 1266.8 | 91.1 | 6114 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.8 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75 | 150.2 | 90.9 | 90 | 170 | 76.2 | 156 | 94.6 | 172 | 3.7 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 59.1 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.8 | 119.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.7 | 30.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 477.1 | 99.8 | 248 | 478 | - | 464 | 97.1 | 232 | -2.7 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 96.7 | 20.2
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1789.1 | 94 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.8 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 248 | 13.1
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 980.5 | 91.9 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.2 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.5 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.5 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 980.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.3 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 977.2
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.8 | 90.5 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.2 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.3 | 13.9 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 10 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665 | 1664.5 | 202.5 | 5198 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.7 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.4 | 136.1 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 92.9 | 186.8 | 124.6 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.6 | 246.3 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.4 | 74.7 | 119.4 | 262 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -6.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.4 | 74.7 | 119.4 | 305 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -6.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 80.6 | 126.2 | 118.1 | 164 | 108 | 74.6 | 118.5 | 110.8 | 49 | -7.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.8 | 118.7 | 111.2 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -6.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.6 | 213.4 | 105 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.3 | 305 | 101.7 | 1847 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 337.3 | 494.7 | 101.5 | 53 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 106.7 | 22.5
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 337.3 | 494.7 | 101.5 | 54 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 106.7 | 22.5
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 530.9 | 848.3 | 101 | 129 | 840 | 501.2 | 801.2 | 95.4 | 82 | -5.6 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 117 | 13.9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 49.5 | 94 | 100 | 36 | 95 | 43.5 | 86.2 | 91.6 | 5 | -8.4 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 59.2 | 105.7 | 97.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.8 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 16.2 | 14.9
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 59.2 | 105.7 | 97.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.8 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 16.2 | 14.9
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.1 | 314.8 | 96.9 | 382 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 442.7 | 803.3 | 95.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -5.3 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 110.6 | 13.1
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.7 | 189.6 | 94.8 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104 | 189.4 | 94.7 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 413.4 | 688 | 94.6 | 52 | 717 | 386.2 | 643 | 88 | 44 | -6.6 | 2014 | 2018 | 4 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 103.3 | 15.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 148.6 | 187.2 | 93.6 | 175 | 200 | 140 | 176.3 | 88.1 | 12 | -5.5 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 74.5 | 154.5 | 93.6 | 169 | 170 | 76.2 | 156 | 94.6 | 172 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.3 | 99.8 | 93.5 | 32 | 108 | 45.8 | 93.5 | 87.4 | 5 | -6.1 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345 | 362.4 | 92.9 | 577 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.6 | 187.5 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 337.6 | 443 | 91.8 | 242 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 31.7 | 7.2
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343 | 384.5 | 91.4 | 2195 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17 | 12.5
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1628.2 | 1792.4 | 91.3 | 7657 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 191.8 | 11
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 94.3 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.6 | 14.6
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 94.3 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.6 | 14.6
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.1 | 963.1 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.5 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | 150 | - | 140.7 | 93.8 | 88 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 68.6 | 117.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -4.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 16.5 | 28.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 471.2 | 98.6 | 248 | 478 | - | 464 | 97.1 | 232 | -1.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 90.8 | 19
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976 | 91.5 | 910 | 1067 | - | 976.7 | 91.5 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972.6 | 91.2 | 910 | 1067 | - | 973.3 | 91.2 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1735.1 | 91.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3.7 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 194 | 10.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141 | 94 | 21 | 150 | - | 141.3 | 94.2 | 21 | 0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 975.4 | 91.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972 | 91.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.1 | #N/A | 972.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.5 | 90.1 | 21 | 96 | - | 84.8 | 88.3 | 21 | -1.8 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13 | 13.5 | #N/A | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 13 | Not in original screening
[25 empty] | 24 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 658.9 | 1654 | 201.2 | 5766 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.9 | 161.2 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 62.9 | 91.4 | 145.9 | 703 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -32.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 62.9 | 91.4 | 145.9 | 747 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -32.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.5 | 162.4 | 135.5 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 88 | 134.1 | 125.3 | 287 | 108 | 74.6 | 118.5 | 110.8 | 49 | -14.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 124.9 | 242.1 | 119.2 | 131 | 201 | 126 | 247.2 | 120 | 172 | 0.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.4 | 123.9 | 115.9 | 139 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 57.4 | 102.2 | 108.5 | 88 | 95 | 43.5 | 86.2 | 91.6 | 5 | -16.9 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 348.8 | 514.1 | 105.5 | 124 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.1 | 26.5
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 348.8 | 514.1 | 105.5 | 125 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.1 | 26.5
THALGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95 | 212.6 | 104.7 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 156.6 | 204.3 | 102.1 | 275 | 200 | 140 | 176.3 | 88.1 | 12 | -14 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 532.3 | 850.7 | 101.3 | 129 | 840 | 501.2 | 801.2 | 95.4 | 82 | -5.9 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 119.4 | 14.2
STUDYS | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.7 | 133.7 | 99.5 | 214 | 131 | 55.2 | 98.1 | 72.9 | 43 | -26.6 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.8 | 105.1 | 98.3 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.9 | 2012 | 2018 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211 | 295 | 98.3 | 1760 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.7 | 195 | 97.5 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.5 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107 | 194.8 | 97.4 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.6 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | GUARDSOUTH | 546 | 8MCGUIRE | 836 | 8WOODLF | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.9 | 314.8 | 96.9 | 592 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.7 | 104.8 | 96.7 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.9 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.3 | 14
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.7 | 104.8 | 96.7 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.9 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.3 | 14
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 46.5 | 90.2 | 96.3 | 48 | 95 | 32.8 | 74.4 | 79.4 | 42 | -16.9 | 2013 | 2023 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 443.9 | 805.4 | 95.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -5.6 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 112.7 | 13.4
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 414.7 | 690.2 | 95 | 84 | 717 | 386.2 | 643 | 88 | 44 | -7 | 2014 | 2018 | 4 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 105.5 | 15.8
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1691 | 1844.9 | 94.4 | 8109 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.7 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 244.3 | 14.1
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 367.9 | 94.3 | 732 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.8 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 435.3 | 745 | 93.5 | 53 | 796.7 | 435 | 745 | 93.5 | 87 | 0 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 75 | 9.4
THRPGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.3 | 139.4 | 93.1 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 248.7 | 430.6 | 92.3 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.8 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.1 | 424.7 | 92.2 | 1048 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.8 | 92.2 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.5 | 152.4 | 92.2 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2.4 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.1 | 186.6 | 92.1 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.8 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.7 | 441.8 | 91.7 | 241 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 30.5 | 7.1
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 41.7 | 97.5 | 91.6 | 31 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.9 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 88 | 109.2 | 91.4 | 607 | 119 | 72.3 | 93 | 77.8 | 192 | -13.6 | 2016 | 2024 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.8 | 382.9 | 91.1 | 2258 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.7 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.4 | 12.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.3 | 94.1 | 90.4 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.5 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.4 | 14.5
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.3 | 94.1 | 90.4 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.5 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.4 | 14.5
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 57.3 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 59.2 | 101.1 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -22.6 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.3 | 94.2 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 5 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 79.7 | 136.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -23.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 27.6 | 47.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 483.3 | 101.1 | 248 | 478 | - | 464 | 97.1 | 232 | -4 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 102.9 | 21.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 99.9 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1802.1 | 94.6 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 261 | 13.7
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.8 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.6 | 90.3 | 455 | 96 | - | 81.1 | 84.5 | 455 | -5.8 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 16.9 | 17.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 70.9 | 99.6 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -19.2 | 2012 | 2023 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 27.1 | 38 | 91.4 | 59.2 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.3 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 90.4 | 94.2 | 21 | 96 | - | 84.8 | 88.3 | 21 | -5.9 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 16.9 | 17.6 | #N/A | #N/A | 86.6
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.4 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 982.8
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.3
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.8 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SOCO
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 671.1 | 1670.8 | 203.3 | 5281 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.2 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.2 | 163.6 | 136.4 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 53.7 | 78.1 | 124.9 | 399 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -11.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 53.7 | 78.1 | 124.9 | 442 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -11.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 83.5 | 130.3 | 121.9 | 231 | 108 | 74.6 | 118.5 | 110.8 | 49 | -11.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.6 | 243.1 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 68.6 | 122.3 | 114.6 | 135 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.8 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 52.6 | 98.2 | 104.5 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -12.9 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 344.1 | 504 | 103.4 | 94 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116 | 24.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 344.1 | 504 | 103.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116 | 24.4
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 304.8 | 101.6 | 1890 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 517.9 | 827.6 | 98.5 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -3.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 96.3 | 11.4
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 50.1 | 103.5 | 96.9 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.5 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.1 | 314.8 | 96.9 | 428 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.3 | 104.2 | 96.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.4 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 14.7 | 13.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.3 | 104.2 | 96.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.4 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 14.7 | 13.5
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.9 | 191.8 | 95.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.9 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 153.3 | 191.6 | 95.8 | 222 | 200 | 140 | 176.3 | 88.1 | 12 | -7.7 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.2 | 191.5 | 95.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.6 | 155.1 | 94 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.6 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.8 | 364.9 | 93.6 | 653 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 431.9 | 783.6 | 93.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -3 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 90.9 | 10.8
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1647.2 | 1813.8 | 92.6 | 7801 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 2.5 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 213.2 | 12.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.8 | 388.2 | 92.4 | 2256 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.7 | 13.5
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 41.7 | 86.3 | 92.3 | 43 | 95 | 32.8 | 74.4 | 79.4 | 42 | -12.9 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 401.5 | 668.2 | 91.8 | 49 | 717 | 386.2 | 643 | 88 | 44 | -3.8 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 83.5 | 12.6
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.2 | 441.1 | 91.5 | 240 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.8 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.8 | 6.9
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 997.2 | 1272.4 | 91.3 | 7380 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.6 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.6 | 94.2 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.5 | 14.6
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.6 | 94.2 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.5 | 14.6
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 43 | 95.9 | 90.2 | 23 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 316.6 | 415.4 | 90.2 | 774 | 478 | 315.6 | 414.1 | 89.8 | 696 | -0.4 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70.9 | 121.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -8.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 18.8 | 32.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 478 | 100 | 248 | 478 | - | 464 | 97.1 | 232 | -2.9 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 97.6 | 20.4
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1755.6 | 92.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.6 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 214.5 | 11.3
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.9 | 91.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.5 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SOCO
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.2 | 93 | 21 | 96 | - | 84.8 | 88.3 | 21 | -4.7 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15.7 | 16.4 | #N/A | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.5 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.9
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 975.1 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 974.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SOCO
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 12 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 13 | Not in original screening
[25 empty] | 25 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665.7 | 1661.8 | 202.2 | 5850 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.4 | 161.4 | 478 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 67.3 | 97.9 | 156.9 | 791 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -43.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 67.3 | 97.9 | 156.9 | 835 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -43.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.6 | 162.8 | 135.8 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 90.9 | 138.2 | 129.1 | 380 | 108 | 74.6 | 118.5 | 110.8 | 49 | -18.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.3 | 242.8 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 69.1 | 127.5 | 119.3 | 147 | 108 | 64.2 | 112.4 | 105.1 | 51 | -14.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 60.4 | 106.4 | 113 | 89 | 95 | 43.5 | 86.2 | 91.6 | 5 | -21.4 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 358.2 | 529.7 | 109 | 150 | 478 | 333.2 | 503.2 | 103.2 | 68 | -5.8 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 141.7 | 30
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 358.2 | 529.7 | 109 | 151 | 478 | 333.2 | 503.2 | 103.2 | 69 | -5.8 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 141.7 | 30
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.3 | 213.2 | 105 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 161.3 | 208.7 | 104.4 | 382 | 200 | 140 | 176.3 | 88.1 | 12 | -16.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 50.6 | 108.7 | 101.7 | 48 | 108 | 45.8 | 93.5 | 87.4 | 5 | -14.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 49.5 | 94.4 | 100.8 | 67 | 95 | 32.8 | 74.4 | 79.4 | 42 | -21.4 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76 | 134 | 100 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 523.2 | 836.2 | 99.5 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 104.9 | 12.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108.9 | 197.2 | 98.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -3.6 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 108.2 | 197 | 98.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -3.7 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.8 | 294.9 | 98.3 | 1844 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.2 | 315.1 | 97 | 771 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.3 | 375.4 | 96.3 | 941 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1717.6 | 1869.7 | 95.6 | 8033 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.5 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 269.1 | 15.3
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57.8 | 103.2 | 95.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.5 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 13.7 | 12.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57.8 | 103.2 | 95.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.5 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 13.7 | 12.6
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 43.5 | 101.1 | 95 | 38 | 108 | 38.7 | 85.9 | 80.7 | 1 | -14.3 | 2014 | 2022 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 442.6 | 757.2 | 95 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | -1.5 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 87.2 | 10.9
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 436.4 | 791.7 | 94.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 99 | 11.8
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 90 | 111.7 | 93.7 | 662 | 119 | 72.3 | 93 | 77.8 | 192 | -15.9 | 2015 | 2024 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 252.7 | 441.1 | 93.7 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.2 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 321 | 428.3 | 93.2 | 1165 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3.4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.7 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 406.3 | 676.3 | 93 | 51 | 717 | 386.2 | 643 | 88 | 44 | -5 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 91.6 | 13.8
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 168 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 80.6 | 153 | 92.6 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187 | 92.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 166 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 77.1 | 88.4 | 92.1 | 494 | 96 | 69 | 80.4 | 83.8 | 350 | -8.3 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 19.2 | 20
OCO3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343.5 | 384.3 | 91.4 | 2267 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 16.8 | 12.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335.3 | 440 | 91.4 | 239 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.7 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 28.7 | 6.8
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 494.9 | 823.8 | 90.8 | 47 | 889 | 486.6 | 810.2 | 89 | 44 | -1.8 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 68.7 | 9.2
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.8 | 94 | 90.3 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.4 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.3 | 14.4
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.8 | 94 | 90.3 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.4 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.3 | 14.4
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 117.5 | 153.9 | 90.2 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -5.1 | 2017 | 2020 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 322.5 | 422.3 | 90.2 | 671 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.5 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 63.6 | 108.7 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -30.2 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.3 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 82 | 140.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -27.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 29.9 | 51
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 490.1 | 102.5 | 256 | 478 | - | 464 | 97.1 | 232 | -5.4 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 109.7 | 22.9
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100.1 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1800.6 | 94.6 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 259.5 | 13.7
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.3 | 93.1 | 455 | 96 | - | 81.1 | 84.5 | 455 | -8.6 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 19.6 | 20.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.5 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 986 | 92.4 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.9 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.6 | 92.1 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SOCO
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 73.2 | 102.8 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -22.4 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 29.4 | 41.2 | 97.9 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.1 | 97 | 21 | 96 | - | 84.8 | 88.3 | 21 | -8.7 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 19.6 | 20.4 | 88.4 | #N/A | 89.3
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.4 | 94.9 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88.1
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.4 | 92.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.3 | 986
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980 | 91.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 982.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 292.6 | 90 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.1 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_TVA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 669.1 | 1668.5 | 203 | 5278 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.3 | 378.9 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.2 | 163.5 | 136.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.4 | 76.2 | 121.8 | 325 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -8.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.4 | 76.2 | 121.8 | 368 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -8.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 82 | 128.2 | 120 | 213 | 108 | 74.6 | 118.5 | 110.8 | 49 | -9.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 246.6 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.7 | 120.5 | 112.9 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 342 | 501.5 | 102.9 | 90 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.5 | 23.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 342 | 501.5 | 102.9 | 91 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.5 | 23.9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51 | 96.1 | 102.2 | 41 | 95 | 43.5 | 86.2 | 91.6 | 5 | -10.6 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.9 | 304.9 | 101.6 | 1890 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 522.8 | 835.4 | 99.5 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 104.1 | 12.4
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 59.4 | 107.4 | 99.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.4 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 17.9 | 16.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 59.4 | 107.4 | 99.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.4 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 17.9 | 16.5
ALL4GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.4 | 315.3 | 97 | 387 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.4 | 190.9 | 95.4 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.7 | 190.7 | 95.3 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49.3 | 101.7 | 95.2 | 37 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7.8 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 150.9 | 189.2 | 94.6 | 173 | 200 | 140 | 176.3 | 88.1 | 12 | -6.5 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 435.9 | 791 | 94.2 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -3.9 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 98.3 | 11.7
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.2 | 155 | 93.9 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.7 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 364.5 | 93.4 | 632 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.8 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 406 | 675.6 | 92.8 | 49 | 717 | 386.2 | 643 | 88 | 44 | -4.8 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 90.9 | 13.6
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1642.6 | 1809.1 | 92.3 | 7829 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 2.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 208.5 | 12
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.1 | 387.4 | 92.2 | 2242 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 19.9 | 13.3
STUDYL | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.8 | 441.9 | 91.6 | 240 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.9 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 30.6 | 7
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 994.9 | 1270.2 | 91.1 | 7308 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.8 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.4 | 94.7 | 91 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.1 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7 | 15.1
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.4 | 94.7 | 91 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.1 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7 | 15.1
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.4 | 963.4 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.1 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | 150 | - | 140.7 | 93.8 | 88 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.7 | 119.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.6 | 30
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 475.9 | 99.6 | 248 | 478 | - | 464 | 97.1 | 232 | -2.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.5 | 20
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1750.6 | 91.9 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.9 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 209.5 | 11
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.2 | 91.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.8 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from TVA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
ALL5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.1 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.2
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.7 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.4 | #N/A | 973.8
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.3 | 90.9 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.6 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.8 | 14.3 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_TVA
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 12 | Not in original screening
[25 empty] | 22 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 663.1 | 1658.9 | 201.8 | 5843 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.4 | 379.1 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 66 | 96 | 153.8 | 739 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -40.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 66 | 96 | 153.8 | 783 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -40.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.6 | 162.7 | 135.8 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 89.4 | 136.1 | 127.2 | 346 | 108 | 74.6 | 118.5 | 110.8 | 49 | -16.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.3 | 242.7 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 68.3 | 125.7 | 117.6 | 144 | 108 | 64.2 | 112.4 | 105.1 | 51 | -12.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 58.8 | 104.2 | 110.7 | 85 | 95 | 43.5 | 86.2 | 91.6 | 5 | -19.1 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 353.8 | 519.8 | 106.9 | 141 | 478 | 333.2 | 503.2 | 103.2 | 68 | -3.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 131.8 | 27.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 353.8 | 519.8 | 106.9 | 142 | 478 | 333.2 | 503.2 | 103.2 | 69 | -3.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 131.8 | 27.9
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.2 | 212.9 | 104.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 159 | 206.3 | 103.2 | 338 | 200 | 140 | 176.3 | 88.1 | 12 | -15.1 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49.8 | 106.9 | 100 | 45 | 108 | 45.8 | 93.5 | 87.4 | 5 | -12.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.9 | 133.9 | 99.9 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 524.1 | 837.5 | 99.7 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.3 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 106.2 | 12.6
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 47.9 | 92.3 | 98.5 | 50 | 95 | 32.8 | 74.4 | 79.4 | 42 | -19.1 | 2012 | 2023 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.6 | 295 | 98.3 | 1810 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108.4 | 196.3 | 98.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -3.2 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.7 | 196.1 | 98 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -3.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.8 | 105.1 | 97 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.2 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.6 | 14.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.8 | 105.1 | 97 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.2 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.6 | 14.3
DAN3GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.1 | 315.2 | 97 | 731 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 373.1 | 95.7 | 871 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1704.2 | 1859.9 | 95.4 | 8115 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 259.3 | 15.1
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 440.9 | 754.5 | 94.7 | 54 | 796.7 | 435 | 745 | 93.5 | 87 | -1.2 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 84.5 | 10.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 437.1 | 793 | 94.4 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4.1 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 100.3 | 11.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 42.6 | 99.3 | 93.3 | 34 | 108 | 38.7 | 85.9 | 80.7 | 1 | -12.6 | 2015 | 2022 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 407.2 | 677.6 | 93.2 | 54 | 717 | 386.2 | 643 | 88 | 44 | -5.2 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 92.9 | 14
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 251.3 | 439 | 93.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -4.7 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.5 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 89.2 | 110.8 | 92.8 | 612 | 119 | 72.3 | 93 | 77.8 | 192 | -15 | 2015 | 2024 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 320.2 | 426.9 | 92.8 | 1160 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 169 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.9 | 152.8 | 92.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 186.9 | 92.3 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.6 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 160 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.8 | 385.7 | 91.8 | 2255 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.4 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 18.2 | 12.9
RIV7GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335.7 | 440.5 | 91.5 | 239 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.8 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.2 | 6.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.6 | 94.5 | 90.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.8 | 14.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.6 | 94.5 | 90.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.8 | 14.9
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 492.3 | 819.5 | 90.3 | 47 | 889 | 486.6 | 810.2 | 89 | 44 | -1.3 | 2017 | 2017 | 0 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 64.4 | 8.7
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.8 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 75.1 | 86.5 | 90.1 | 482 | 96 | 69 | 80.4 | 83.8 | 350 | -6.3 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 17.3 | 18
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 62.4 | 106.6 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -28.1 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 80.7 | 138 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -25.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 28.6 | 48.9
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 488.1 | 102.1 | 256 | 478 | - | 464 | 97.1 | 232 | -5 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 107.7 | 22.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100.1 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1817.5 | 95.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 276.4 | 14.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985 | 92.3 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 981.6 | 92 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.4 | 91 | 455 | 96 | - | 81.1 | 84.5 | 455 | -6.5 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 17.7 | 18.4
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_TVA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 71.9 | 101 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -20.6 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 28.1 | 39.4 | 96 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 91.2 | 95 | 21 | 96 | - | 84.8 | 88.3 | 21 | -6.7 | 2014 | 2018 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 17.7 | 18.4 | 86.5 | #N/A | 87.4
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.2 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.6 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.1 | 985
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 981.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 677.2 | 1678.1 | 204.2 | 5337 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.7 | 379.4 | 161.4 | 509 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 60.5 | 87.9 | 140.5 | 571 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -27.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 60.5 | 87.9 | 140.5 | 615 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -27.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.7 | 136.5 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 91.4 | 141.4 | 132.3 | 363 | 108 | 74.6 | 118.5 | 110.8 | 49 | -21.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 73.4 | 132 | 123.7 | 177 | 108 | 64.2 | 112.4 | 105.1 | 51 | -18.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 243.5 | 119.9 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 61 | 109.8 | 116.8 | 85 | 95 | 43.5 | 86.2 | 91.6 | 5 | -25.2 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 55 | 113.3 | 106.2 | 59 | 108 | 45.8 | 93.5 | 87.4 | 5 | -18.8 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.6 | 213.8 | 105.3 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 50.1 | 97.9 | 104.7 | 66 | 95 | 32.8 | 74.4 | 79.4 | 42 | -25.3 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345.4 | 505 | 103.6 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 117 | 24.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345.4 | 505 | 103.6 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 117 | 24.6
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 165.9 | 204.2 | 102.1 | 641 | 200 | 140 | 176.3 | 88.1 | 12 | -14 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.4 | 304.4 | 101.5 | 1858 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 47.9 | 105.7 | 99.5 | 44 | 108 | 38.7 | 85.9 | 80.7 | 1 | -18.8 | 2012 | 2022 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.4 | 194.5 | 97.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.7 | 194.2 | 97.1 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.3 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRBK1 | 233 | 6BUSH RV | 42004 | 6PARR | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 81.4 | 93.1 | 97 | 693 | 96 | 69 | 80.4 | 83.8 | 350 | -13.2 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 23.9 | 24.9
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 509.9 | 815 | 97 | 124 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.6 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 83.7 | 9.9
GTFLGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.7 | 314.8 | 96.9 | 433 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.2 | 155.3 | 94.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 101.8 | 94 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.2 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.3 | 11.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 101.8 | 94 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.2 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.3 | 11.3
TUXDGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 362.9 | 93.1 | 639 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.8 | 92.8 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.3 | 387.6 | 92.2 | 2279 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.1 | 13.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1643.7 | 1806.1 | 92.1 | 7618 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 205.5 | 11.8
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 425.3 | 771.7 | 91.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.6 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 79 | 9.4
OXFDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.5 | 438.9 | 91 | 216 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.3 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.6 | 6.4
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318.3 | 419.6 | 90.9 | 1081 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.2 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 394.2 | 656.1 | 90 | 47 | 717 | 386.2 | 643 | 88 | 44 | -2 | 2017 | 2018 | 1 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 71.4 | 10.8
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 237.8 | 423.8 | 90 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -1.5 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 57 | 97.4 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -18.9 | 2013 | 2024 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.2 | 94.1 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77.3 | 132.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -19.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 25.2 | 43
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479.3 | 100.3 | 248 | 478 | - | 464 | 97.1 | 232 | -3.2 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.9 | 20.7
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.7 | 97.6 | 455 | 96 | - | 81.1 | 84.5 | 455 | -13.1 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 24 | 25
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1751.1 | 92 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 210 | 11.1
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.9 | 91.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.5 | 91.5 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 97.5 | 101.6 | 21 | 96 | - | 84.8 | 88.3 | 21 | -13.3 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 24 | 25 | 93.1 | #N/A | 93.7
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 68.5 | 96.2 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -15.8 | 2013 | 2023 | 10 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 24.7 | 34.6 | 87.9 | 57 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.2 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 980.3 | 91.9 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 979.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.9 | 91.6 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 976.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 14 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 14 | Not in original screening
[25 empty] | 28 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 672.9 | 1669.6 | 203.1 | 5920 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 74 | 107.6 | 172.5 | 942 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -59.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 74 | 107.6 | 172.5 | 986 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -59.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.6 | 161.5 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 99 | 149.5 | 139.7 | 666 | 108 | 74.6 | 118.5 | 110.8 | 49 | -28.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.5 | 162.8 | 135.9 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 73.9 | 137.3 | 128.6 | 170 | 108 | 64.2 | 112.4 | 105.1 | 51 | -23.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 68.9 | 118 | 125.4 | 205 | 95 | 43.5 | 86.2 | 91.6 | 5 | -33.8 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.5 | 242.9 | 119.6 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 57.9 | 106 | 113.3 | 93 | 95 | 32.8 | 74.4 | 79.4 | 42 | -33.9 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 55.5 | 118.6 | 111.1 | 82 | 108 | 45.8 | 93.5 | 87.4 | 5 | -23.7 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 174.2 | 221.5 | 110.7 | 790 | 200 | 140 | 176.3 | 88.1 | 12 | -22.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 359.5 | 530.7 | 109.2 | 150 | 478 | 333.2 | 503.2 | 103.2 | 68 | -6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.7 | 30.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 359.5 | 530.7 | 109.2 | 151 | 478 | 333.2 | 503.2 | 103.2 | 69 | -6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.7 | 30.2
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.4 | 213.3 | 105.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 48.4 | 111 | 104.4 | 46 | 108 | 38.7 | 85.9 | 80.7 | 1 | -23.7 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 85.3 | 97.6 | 101.7 | 681 | 96 | 69 | 80.4 | 83.8 | 350 | -17.9 | 2011 | 2020 | 9 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 28.4 | 29.6
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76.9 | 134.6 | 101 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -28.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 110.4 | 199.9 | 99.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -4.9 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 109.6 | 199.6 | 99.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -5 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 294.5 | 98.2 | 1847 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.8 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 515.3 | 823.6 | 98 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.6 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 92.3 | 10.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20723 | CAMD JCT 115 | 20734 | WATRE 115 | 1 | 20723-20734-1 | 131 | 131 | 53.2 | 124.1 | 97.4 | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2013 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.3 | 315.6 | 97.1 | 851 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.2 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.3 | 375.6 | 96.3 | 977 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 92.5 | 114.4 | 96.2 | 947 | 119 | 72.3 | 93 | 77.8 | 192 | -18.4 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 444.1 | 759.9 | 95.4 | 57 | 796.7 | 435 | 745 | 93.5 | 87 | -1.9 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 89.9 | 11.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1706.4 | 1858.7 | 95.2 | 8183 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.1 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 258.1 | 14.9
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 256.2 | 445.1 | 94.9 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -6.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 322.7 | 431.4 | 94.1 | 1165 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 35.2 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.4 | 100.8 | 93.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.7 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.3 | 10.4
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.4 | 100.8 | 93.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.7 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.3 | 10.4
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 429.7 | 779.8 | 92.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.5 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 87.1 | 10.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 172 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.2 | 153.2 | 92.8 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187.1 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.7 | 92.2 | 202 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 498.2 | 829.3 | 91.4 | 51 | 889 | 486.6 | 810.2 | 89 | 44 | -2.4 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 74.2 | 9.8
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 399 | 664.3 | 91.3 | 48 | 717 | 386.2 | 643 | 88 | 44 | -3.3 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 79.6 | 12.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344 | 383.6 | 91.3 | 2394 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.9 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 16.1 | 12.4
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 325.1 | 425.3 | 91 | 995 | 478 | 306.7 | 403.9 | 85.7 | 343 | -5.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 118.1 | 154.8 | 90.9 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -5.8 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.8 | 437.9 | 90.9 | 230 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.6 | 6.3
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20524 | JACKSONV 230 | 20528 | RHEMS 230 | 1 | 20524-20528-1 | 478 | 478 | 230.9 | 417.2 | 90.2 | 86 | 478 | 208.3 | 390.9 | 83.8 | 43 | -6.4 | 2017 | 2020 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 2 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70 | 119.7 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -41.2 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.2 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | - | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 100.1 | 92.6 | 124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.6 | 91.2 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 963.2 | 90.3 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 959.9 | 90 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 88.4 | 151.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -38.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 36.3 | 62
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 491.4 | 102.8 | 260 | 478 | - | 464 | 97.1 | 232 | -5.7 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 111 | 23.2
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 97.6 | 101.6 | 455 | 96 | - | 81.1 | 84.5 | 455 | -17.1 | 2011 | 2020 | 9 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 27.9 | 29
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1796.4 | 94.3 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.5 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 255.3 | 13.4
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.4 | 93 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 988.9 | 92.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.5 | 92.4 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 352 | 90.3 | 455 | 390 | - | 345.2 | 88.5 | 455 | -1.8 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 79.8 | 112 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -31.6 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 36 | 50.4 | #N/A | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 101.4 | 105.6 | 21 | 96 | - | 84.8 | 88.3 | 21 | -17.3 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 27.9 | 29 | 97.6 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.6 | 95.1 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 142 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.5 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.6 | 88.4
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.5 | 92.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.2 | 988.9
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.7 | 92.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 959.9 | 985.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
STUDYL | BADX | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 98.3 | 91 | 42 | 108 | - | 69.1 | 64 | 42 | -27 | 2016 | 2034 | 18 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 149.5 | 100.1 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.5 | 90.3 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.6 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
RIV7GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 678.7 | 1679.1 | 204.3 | 5380 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.4 | 161.5 | 511 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 61.2 | 88.9 | 142.1 | 617 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -28.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 61.2 | 88.9 | 142.1 | 661 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -28.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48 | 163.6 | 136.5 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 90.9 | 140.2 | 131.2 | 354 | 108 | 74.6 | 118.5 | 110.8 | 49 | -20.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 72.2 | 130.6 | 122.4 | 186 | 108 | 64.2 | 112.4 | 105.1 | 51 | -17.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 243.5 | 119.9 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 60.6 | 108.6 | 115.6 | 87 | 95 | 43.5 | 86.2 | 91.6 | 5 | -24 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 214 | 105.4 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 53.9 | 111.9 | 104.9 | 56 | 108 | 45.8 | 93.5 | 87.4 | 5 | -17.5 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 49.7 | 96.7 | 103.4 | 65 | 95 | 32.8 | 74.4 | 79.4 | 42 | -24 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345.2 | 504.5 | 103.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.5 | 24.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345.2 | 504.5 | 103.4 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.5 | 24.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 164.3 | 204.4 | 102.2 | 555 | 200 | 140 | 176.3 | 88.1 | 12 | -14.1 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.4 | 304.2 | 101.4 | 1857 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 46.8 | 104.3 | 98.1 | 42 | 108 | 38.7 | 85.9 | 80.7 | 1 | -17.4 | 2012 | 2022 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108 | 195.5 | 97.7 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.2 | 195.3 | 97.6 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.8 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 509.4 | 814.2 | 96.9 | 124 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.5 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 82.9 | 9.8
LOOKGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303.1 | 314.8 | 96.9 | 434 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.3 | 155.3 | 94.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.7 | 93.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.2 | 11.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.7 | 93.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.2 | 11.2
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28.7 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.6 | 362.7 | 93 | 620 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 138 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.8 | 92.8 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 424.8 | 770.9 | 91.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.5 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 78.2 | 9.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1640.5 | 1800.3 | 91.8 | 7655 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 199.7 | 11.5
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 76.5 | 88 | 91.6 | 487 | 96 | 69 | 80.4 | 83.8 | 350 | -7.8 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 18.8 | 19.5
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.3 | 384.8 | 91.5 | 2243 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17.3 | 12.6
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.1 | 421.1 | 91.3 | 1154 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.7 | 439.2 | 91.1 | 219 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.4 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.9 | 6.5
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 239.6 | 426.1 | 90.5 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.1 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 57.6 | 98.5 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -20 | 2012 | 2024 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.6 | 91.2 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77.9 | 133.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -20.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 25.8 | 44
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479 | 100.2 | 248 | 478 | - | 464 | 97.1 | 232 | -3.1 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.6 | 20.6
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.8 | 92.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -8 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 19.1 | 19.9
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.2 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1747.3 | 91.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 206.2 | 10.9
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.8 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 69.1 | 97.1 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -16.7 | 2013 | 2023 | 10 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 25.3 | 35.5 | 88.9 | 57.6 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 92.5 | 96.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -8.1 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 19 | 19.8 | 88 | #N/A | 88.8
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.4 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.6 | 88
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.6 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960.2 | 981.2
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.1 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 977.8
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 16 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 14 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 676 | 1672.8 | 203.5 | 5918 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 74.7 | 108.6 | 174.1 | 992 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -60.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 74.7 | 108.6 | 174.1 | 1036 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -60.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.9 | 379.7 | 161.6 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 98.5 | 148.2 | 138.6 | 658 | 108 | 74.6 | 118.5 | 110.8 | 49 | -27.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.4 | 162.8 | 135.9 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 72.8 | 135.8 | 127.2 | 170 | 108 | 64.2 | 112.4 | 105.1 | 51 | -22.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 68.4 | 116.8 | 124.1 | 202 | 95 | 43.5 | 86.2 | 91.6 | 5 | -32.5 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.4 | 242.9 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 57.5 | 104.8 | 112 | 95 | 95 | 32.8 | 74.4 | 79.4 | 42 | -32.6 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 172.5 | 221.7 | 110.8 | 796 | 200 | 140 | 176.3 | 88.1 | 12 | -22.7 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 54.3 | 117.2 | 109.7 | 83 | 108 | 45.8 | 93.5 | 87.4 | 5 | -22.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 359.3 | 530.3 | 109.1 | 147 | 478 | 333.2 | 503.2 | 103.2 | 68 | -5.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.3 | 30.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 359.3 | 530.3 | 109.1 | 148 | 478 | 333.2 | 503.2 | 103.2 | 69 | -5.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.3 | 30.1
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.4 | 213.3 | 105.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 47.2 | 109.5 | 103 | 48 | 108 | 38.7 | 85.9 | 80.7 | 1 | -22.3 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 77.2 | 134.7 | 101.1 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -28.2 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 110.9 | 200.9 | 100.4 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -5.4 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 110.2 | 200.6 | 100.3 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -5.5 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20723 | CAMD JCT 115 | 20734 | WATRE 115 | 1 | 20723-20734-1 | 131 | 131 | 54.9 | 125.4 | 98.5 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 294.3 | 98.1 | 1848 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.9 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 514.7 | 822.7 | 97.9 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.5 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 91.4 | 10.8
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 94 | 115.8 | 97.5 | 991 | 119 | 72.3 | 93 | 77.8 | 192 | -19.7 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.3 | 315.2 | 97 | 1058 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 375.6 | 96.3 | 998 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 80.4 | 91.9 | 95.7 | 672 | 96 | 69 | 80.4 | 83.8 | 350 | -11.9 | 2014 | 2020 | 6 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 22.7 | 23.6
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 258 | 447.3 | 95.4 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -6.9 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1703.1 | 1853.1 | 94.8 | 8128 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 252.5 | 14.5
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.5 | 432.8 | 94.5 | 1233 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.7 | 2014 | 2017 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 439.7 | 752.5 | 94.5 | 54 | 796.7 | 435 | 745 | 93.5 | 87 | -1 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 82.5 | 10.4
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 35.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.4 | 100.7 | 93 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.8 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.2 | 10.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.4 | 100.7 | 93 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.8 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.2 | 10.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 135 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.4 | 153.2 | 92.8 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 429.2 | 779 | 92.7 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.4 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 86.3 | 10.2
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.9 | 92.3 | 205 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 326.4 | 426.8 | 91.4 | 1420 | 478 | 306.7 | 403.9 | 85.7 | 343 | -5.7 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 118.6 | 155.4 | 91.3 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -6.2 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 497.9 | 828.8 | 91.3 | 50 | 889 | 486.6 | 810.2 | 89 | 44 | -2.3 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 73.7 | 9.7
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 398.5 | 663.5 | 91.1 | 48 | 717 | 386.2 | 643 | 88 | 44 | -3.1 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 78.8 | 11.9
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.7 | 438 | 90.9 | 232 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.7 | 6.3
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20524 | JACKSONV 230 | 20528 | RHEMS 230 | 1 | 20524-20528-1 | 478 | 478 | 232.6 | 419.2 | 90.7 | 86 | 478 | 208.3 | 390.9 | 83.8 | 43 | -6.9 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342 | 380.9 | 90.6 | 2205 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.2 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 13.4 | 11.7
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 80.1 | 100.3 | 90.3 | 298 | 111 | 79.4 | 79.4 | 71.5 | 130 | -18.8 | 2017 | 2028 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.7 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 2 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70.7 | 120.8 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -42.3 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.2 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | - | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 99.6 | 92.2 | 124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.7 | 91.3 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 964.4 | 90.4 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 89.1 | 152.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -39.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 37 | 63.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 491.2 | 102.8 | 260 | 478 | - | 464 | 97.1 | 232 | -5.7 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 110.8 | 23.2
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 92.6 | 96.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -12 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 22.9 | 23.9
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1793.2 | 94.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.6 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 252.1 | 13.3
BUC5GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 92.9 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.7 | 92.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 986.1 | 92.4 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 351.5 | 90.1 | 455 | 390 | - | 345.2 | 88.5 | 455 | -1.6 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 80.4 | 112.9 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -32.5 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 36.6 | 51.3 | #N/A | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 96.4 | 100.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -12.1 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 22.9 | 23.8 | 91.9 | #N/A | 92.6
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.8 | 95.2 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.3 | #N/A
STUDYL | BADX | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 102.2 | 94.6 | 42 | 108 | - | 69.1 | 64 | 42 | -30.6 | 2014 | 2034 | 20 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 148.2 | 99.6 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.2 | 92.9 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.7 | 88.3
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 987.5 | 92.6 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.4 | 989.7
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 983.5 | 92.2 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 961.1 | 986.1
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.7 | 90.4 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.2 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_CPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 656.1 | 1643.8 | 200 | 5704 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 2.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.4 | 379.1 | 161.3 | 506 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.3 | 226.4 | 151 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 112.5 | 226.4 | 151 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 62.3 | 90.4 | 144.3 | 668 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -31 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 62.3 | 90.4 | 144.3 | 712 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -31 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.6 | 136.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 87 | 132.6 | 123.8 | 274 | 108 | 74.6 | 118.5 | 110.8 | 49 | -13 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 246.7 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.6 | 122.5 | 114.6 | 147 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 56.4 | 100.6 | 106.8 | 89 | 95 | 43.5 | 86.2 | 91.6 | 5 | -15.2 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20039 | SUT 3 F 230 | 20554 | 9THORG T 230 | 1 | 20039-20554-1 | 590 | 590 | 225.3 | 612.1 | 104.6 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 342.3 | 498.8 | 102.2 | 68 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 110.8 | 23.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 342.3 | 498.8 | 102.2 | 69 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 110.8 | 23.2
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 154.8 | 202.8 | 101.4 | 280 | 200 | 140 | 176.3 | 88.1 | 12 | -13.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.3 | 301.4 | 100.5 | 1850 | 300 | 213.3 | 306.1 | 102 | 1886 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 74.1 | 131 | 98.3 | 166 | 131 | 55.2 | 98.1 | 72.9 | 43 | -25.4 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48 | 103.7 | 97 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.6 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.1 | 315.1 | 97 | 377 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107 | 193.7 | 96.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.9 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.3 | 193.5 | 96.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 506.9 | 810.3 | 96.5 | 121 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.1 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 79 | 9.4
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20552 | E WILM 230 | 20554 | 9THORG T 230 | 1 | 20552-20554-1 | 590 | 590 | 173.1 | 560.9 | 95.9 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 45.5 | 88.7 | 94.6 | 46 | 95 | 32.8 | 74.4 | 79.4 | 42 | -15.2 | 2014 | 2023 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 101.9 | 94.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.3 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.4 | 11.4
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 101.9 | 94.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.3 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.4 | 11.4
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 77.2 | 155.1 | 93.9 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.7 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 29.9 | 139.4 | 93.1 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.3 | 92.1 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | OAKBOR100CAP | 5635 | OAKBRCAP | 635 | OAKBORO | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.1 | 358.7 | 92 | 523 | 390 | 344.5 | 364.5 | 93.5 | 554 | 1.5 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 422.7 | 767.2 | 91.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 74.5 | 8.8
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 316.7 | 419 | 91.1 | 806 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.3 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.4 | 438.8 | 90.9 | 207 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.5 | 6.3
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 243.5 | 424.1 | 90.7 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2.2 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964 | 964 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ROCKGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.9 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 40.9 | 96.1 | 90.2 | 25 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1620.3 | 1772.5 | 90 | 7512 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 5.1 | 2017 | 2014 | -3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 171.9 | 9.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 58.5 | 100.1 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -21.6 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 78.8 | 134.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -22 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 26.7 | 45.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 475.7 | 99.5 | 248 | 478 | - | 464 | 97.1 | 232 | -2.4 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.3 | 19.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978 | 91.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.7 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1727.9 | 90.7 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 4.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 186.8 | 9.8
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.5 | 90.1 | 455 | 96 | - | 81.1 | 84.5 | 455 | -5.6 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 16.8 | 17.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 70.2 | 98.6 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -18.2 | 2012 | 2023 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 26.4 | 37 | 90.4 | 58.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.3 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 90.3 | 94 | 21 | 96 | - | 84.8 | 88.3 | 21 | -5.7 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 16.8 | 17.4 | #N/A | #N/A | 86.5
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.8
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.9 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 978
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 975.6 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964 | #N/A | 973.7
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.5 | 90.1 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.3 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_CPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 10 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 1057.9 | 1884.8 | 229.3 | 5969 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -26.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.2 | 161.4 | 509 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 64 | 93 | 148.3 | 668 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -35 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 64 | 93 | 148.3 | 712 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -35 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 49.9 | 168.1 | 140.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | -3.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 88.1 | 133.7 | 124.9 | 300 | 108 | 74.6 | 118.5 | 110.8 | 49 | -14.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 127.7 | 248 | 122.1 | 301 | 201 | 126 | 247.2 | 120 | 172 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.7 | 123.2 | 115.3 | 149 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 57.5 | 101.8 | 108.1 | 92 | 95 | 43.5 | 86.2 | 91.6 | 5 | -16.5 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 97.6 | 218.4 | 107.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 346.4 | 506 | 103.7 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118 | 24.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 346.4 | 506 | 103.7 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118 | 24.7
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 156 | 205.4 | 102.7 | 279 | 200 | 140 | 176.3 | 88.1 | 12 | -14.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.2 | 28.2 | 100.9 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.6 | 133.7 | 99.3 | 212 | 131 | 55.2 | 98.1 | 72.9 | 43 | -26.4 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.1 | 295.1 | 98.4 | 1732 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.6 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.1 | 104.4 | 97.7 | 51 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.3 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 95.9 | 116.9 | 97.5 | 1199 | 119 | 72.3 | 93 | 77.8 | 192 | -19.7 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.8 | 314.8 | 96.9 | 492 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 507.3 | 810.8 | 96.5 | 122 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.1 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 79.5 | 9.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.3 | 192.5 | 96.3 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.3 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.6 | 192.3 | 96.2 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.4 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 46.7 | 89.9 | 95.9 | 50 | 95 | 32.8 | 74.4 | 79.4 | 42 | -16.5 | 2014 | 2023 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 72.5 | 192.2 | 95 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -2.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 363 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20001 | BLEWETT 115 | 20004 | TIL 1-4H 115 | 1 | 20001-20004-1 | 118 | 118 | 80.2 | 116.3 | 94.5 | 414 | 118 | 60 | 95 | 77.4 | 81 | -17.1 | 2014 | 2024 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 33.4 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.3 | 153.6 | 93.1 | 130 | 170 | 76.2 | 156 | 94.6 | 172 | 1.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.9 | 92.3 | 173 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 247.8 | 434.6 | 92.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 343.3 | 359.6 | 92.2 | 560 | 390 | 344.5 | 364.5 | 93.5 | 554 | 1.3 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318.5 | 422.2 | 92 | 1073 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.2 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 423 | 767.8 | 91.4 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.1 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 75.1 | 8.9
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1639 | 1783.1 | 91 | 7906 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 4.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 182.5 | 10.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 40.9 | 96.8 | 90.9 | 28 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.2 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.1 | 438.4 | 90.8 | 206 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.1 | 6.2
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.3 | 964.3 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 57.3 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 2 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1041.6 | 126.7 | 176 | 822 | - | 646.7 | 78.7 | 176 | -48 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60.2 | 102.9 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -24.4 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.6 | 98.4 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141 | 94 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86 | 90.5 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0.3 | 2017 | 2016 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 80.4 | 137.5 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -24.9 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 28.3 | 48.4
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1089.9 | 132.6 | 910 | 822 | - | 667.9 | 81.3 | 910 | -51.3 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 480.1 | 100.4 | 248 | 478 | - | 464 | 97.1 | 232 | -3.3 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 99.7 | 20.8
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.3 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.5 | 92.1 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981 | 91.9 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1748 | 91.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 206.9 | 10.9
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.5 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.2 | 90.8 | 455 | 96 | - | 81.1 | 84.5 | 455 | -6.3 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 17.5 | 18.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1067.3 | 129.8 | 42 | 822 | - | 662.5 | 80.6 | 42 | -49.2 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 71.9 | 100.9 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -20.5 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 28.1 | 39.3 | 93 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.2 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 91 | 94.8 | 21 | 96 | - | 84.8 | 88.3 | 21 | -6.5 | 2014 | 2018 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 17.5 | 18.2 | #N/A | #N/A | 87.2
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.9 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.5 | 92.1 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86 | 87.5
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 91.9 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.4 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 981
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.3 | #N/A | 977.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.5 | 90.1 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 5 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 5 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 662.7 | 1677 | 204 | 5213 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.7 | 161.2 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.1 | 159.3 | 133.2 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.3 | 239.7 | 118.2 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 71.1 | 114.9 | 107.6 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 331.2 | 504.8 | 103.7 | 62 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.8 | 24.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 331.2 | 504.8 | 103.7 | 63 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.8 | 24.7
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.8 | 310.7 | 103.6 | 1846 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.2 | 210.1 | 103.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.5 | 110.5 | 103.5 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 1.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1112.7 | 1393.7 | 100.7 | 9015 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -5.8 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 525.2 | 839.3 | 99.9 | 118 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.5 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 108 | 12.8
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 40.7 | 58.3 | 98.9 | 52 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 14.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 40.7 | 58.3 | 98.9 | 65 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 14.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1712.6 | 1896.2 | 97.2 | 7863 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -2.1 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 295.6 | 16.9
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.8 | 105 | 96.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.1 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.5 | 14.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.8 | 105 | 96.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.1 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.5 | 14.2
OXFDGM | CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 304.5 | 314.9 | 96.9 | 596 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 448 | 767.1 | 96.3 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -2.8 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 97.1 | 12.2
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.8 | 375.5 | 96.3 | 835 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 73 | 157 | 95.6 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 68 | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83.6 | 105.6 | 95.1 | 433 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.6 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 438 | 794.7 | 94.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4.3 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 102 | 12.1
TURNGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.4 | 189.1 | 94.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.7 | 188.9 | 94.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.3 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.9 | 139.4 | 93.7 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 408.2 | 679.4 | 93.3 | 82 | 717 | 386.2 | 643 | 88 | 44 | -5.3 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 94.7 | 14.1
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323.1 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.2 | 387.8 | 92.2 | 2170 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.3 | 13.3
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.4 | 421.7 | 91.9 | 1252 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 337.1 | 442.4 | 91.6 | 296 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.9 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 31.1 | 7
THTCGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 108 | 182.6 | 91.3 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -5.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 107.7 | 182.3 | 91.2 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -5.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 239.7 | 425.9 | 91.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.9 | 183.7 | 90.9 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 51 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 278.9 | 412.7 | 90.7 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1.4 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -8.1 | -0.7
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 432.7 | 760.2 | 90.5 | 44 | 840 | 420.2 | 738.3 | 87.9 | 44 | -2.6 | 2017 | 2018 | 1 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 96.2 | 11.4
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 93.9 | 90.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.2 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.2 | 14.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 93.9 | 90.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.2 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.2 | 14.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.6 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60 | 102.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 10 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 7.9 | 13.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 462.6 | 96.8 | 232 | 478 | - | 464 | 97.1 | 232 | 0.3 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 82.2 | 17.2
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1830.3 | 96.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -1.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 289.2 | 15.2
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.5 | 92.2 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980.3 | 91.9 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 87.9
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 984.4 | 92.3 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.6 | 983.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 981.2 | 92 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 980.3
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323.1 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_VP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
DAN3GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 657.6 | 1668.7 | 203 | 5294 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.3 | 378.8 | 161.2 | 487 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.7 | 158.4 | 132.4 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 4.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.8 | 238.7 | 117.7 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 70.9 | 114.6 | 107.3 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 3.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 309.5 | 103.2 | 1728 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.7 | 209.1 | 103.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.2 | 109.9 | 102.9 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 329.9 | 501.3 | 102.8 | 61 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.3 | 23.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 329.9 | 501.3 | 102.8 | 62 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.3 | 23.8
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 40.9 | 58.6 | 99.3 | 49 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 14 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 40.9 | 58.6 | 99.3 | 65 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 14 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 515.9 | 824.6 | 98.2 | 86 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.8 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 93.3 | 11.1
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1081 | 1361.6 | 98.1 | 8912 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -3.2 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.9 | 314.8 | 96.9 | 552 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1692.7 | 1872.3 | 95.7 | 7938 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 271.7 | 15.4
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58 | 103.5 | 95.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.8 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 14 | 12.9
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58 | 103.5 | 95.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.8 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 14 | 12.9
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83 | 105.6 | 95.2 | 370 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.5 | 370.3 | 94.9 | 710 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 71.8 | 155.4 | 94.5 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 438 | 750.2 | 94.2 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | -0.7 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 80.2 | 10.1
TUXDGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 103.7 | 187.9 | 94 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.1 | 187.7 | 93.9 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.9 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.7 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 430.3 | 780.8 | 93 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.7 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 88.1 | 10.5
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 212 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 281.9 | 417.1 | 91.7 | 46 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.4 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.7 | 0.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.6 | 384.7 | 91.4 | 2153 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17.2 | 12.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.1 | 441.1 | 91.3 | 273 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.6 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.8 | 6.7
BEL1GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 399.7 | 665.3 | 91.2 | 49 | 717 | 386.2 | 643 | 88 | 44 | -3.2 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 80.6 | 12
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 317.2 | 417.9 | 90.9 | 1190 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 51.9 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 107.2 | 181.1 | 90.6 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -4.9 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 107 | 181 | 90.5 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -4.9 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.5 | 182.7 | 90.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.5 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60.2 | 102.9 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 9.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 8.1 | 13.8
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 460.8 | 96.4 | 232 | 478 | - | 464 | 97.1 | 232 | 0.7 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 80.4 | 16.8
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1810 | 95 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 268.9 | 14.1
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.9 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.6 | 91.7 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_VP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.6 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.5 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960.2 | 981.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.2 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 978.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 13 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 22 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
MCG2GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 671.3 | 1685.3 | 205 | 5445 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.7 | 379.4 | 161.5 | 513 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.1 | 159.7 | 133.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.6 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.6 | 130 | 121.7 | 58 | 108 | 74.6 | 118.5 | 110.8 | 49 | -10.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.4 | 74.7 | 119.5 | 347 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -6.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.4 | 74.7 | 119.5 | 390 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -6.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.6 | 240.2 | 118.6 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 71.3 | 123.6 | 115.8 | 135 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 339.4 | 514.3 | 105.7 | 85 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.3 | 26.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 339.4 | 514.3 | 105.7 | 86 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.3 | 26.7
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51 | 98.3 | 104.6 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -13 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.4 | 210.6 | 103.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.8 | 310.1 | 103.4 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1106.4 | 1385.8 | 100.5 | 9054 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -5.6 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 52.8 | 104.9 | 98.3 | 44 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.9 | 2012 | 2018 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1728.3 | 1909.8 | 98.1 | 7734 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -3 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 309.2 | 17.8
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 454.2 | 777.5 | 97.6 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -4.1 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 107.5 | 13.5
TUXDGM | SINGLE 54 | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.2 | 315.8 | 97.2 | 1290 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.3 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.2 | 194.2 | 97.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.1 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.5 | 194 | 97 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.2 | 375.6 | 96.3 | 1071 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.1 | 157.8 | 96.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 504.2 | 805.9 | 95.9 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.5 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 74.6 | 8.8
RDHSGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84.2 | 105.6 | 95.2 | 799 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.1 | 428.3 | 93.8 | 1357 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 23.7 | 139.4 | 93.7 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 247.3 | 435.5 | 93.6 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.1 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.6 | 101.1 | 93.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.5 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.6 | 10.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.6 | 101.1 | 93.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.5 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.6 | 10.6
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.6 | 391 | 93 | 2162 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.6 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 23.5 | 14.1
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 131 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 40.3 | 86.4 | 92.5 | 52 | 95 | 32.8 | 74.4 | 79.4 | 42 | -13.1 | 2015 | 2023 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 77.5 | 88.6 | 92.3 | 505 | 96 | 69 | 80.4 | 83.8 | 350 | -8.5 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 19.4 | 20.2
TUXDGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.3 | 323 | 92.3 | 308 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 108.9 | 184.1 | 92.1 | 75 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.5 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 109 | 184.2 | 92.1 | 79 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.4 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 153.7 | 183.9 | 92 | 111 | 200 | 140 | 176.3 | 88.1 | 12 | -3.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 438.7 | 770.8 | 91.8 | 47 | 840 | 420.2 | 738.3 | 87.9 | 44 | -3.9 | 2016 | 2018 | 2 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 106.8 | 12.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 45.8 | 97.3 | 91.6 | 37 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.9 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68.1 | 184.1 | 91.2 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.7 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420.5 | 763.1 | 90.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.5 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 70.4 | 8.3
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 50.4 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334 | 438.2 | 90.8 | 263 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.9 | 6.2
ALL5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 320 | 419.9 | 90.1 | 614 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.4 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.7 | 91.3 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 965.2 | 90.5 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 962.1 | 90.2 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 68.6 | 117.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -4.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 16.5 | 28.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 470.9 | 98.5 | 232 | 478 | - | 464 | 97.1 | 232 | -1.4 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 90.5 | 18.9
BEL1GM | BEL2 | - | - | - | - | - | 431 | ENGR6TAP | 576 | CONLY TB | 1 | 431-576-1 | 126.4 | 126.4 | - | 124 | 98.1 | 455 | 126.4 | - | 122.5 | 96.9 | 455 | -1.2 | 2012 | 2013 | 1 |  | 126.4 | 139.4 | 126.4 | HOPEWELL B | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 103.4 | 81.8 | 20.6 | 16.3
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1848.7 | 97.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -2.3 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 307.6 | 16.2
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.7 | 93.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -9 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 20 | 20.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 92.9 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 988.3 | 92.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.2 | 92.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.5 | 97.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -9.1 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 20 | 20.8 | 88.6 | #N/A | 89.7
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.8 | 95.2 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.3 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.2 | 92.9 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.7 | 88.3
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 987.7 | 92.6 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 965.2 | 988.3
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 984.6 | 92.3 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 962.1 | 985.2
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.2 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.2 | 90.2 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.8 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 676.9 | 1684.7 | 205 | 5404 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.5 | 161.5 | 515 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45 | 159.6 | 133.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.6 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.1 | 75.6 | 121.1 | 398 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -7.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.1 | 75.6 | 121.1 | 441 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -7.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.2 | 128.8 | 120.6 | 55 | 108 | 74.6 | 118.5 | 110.8 | 49 | -9.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.6 | 240.2 | 118.6 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | MONROEWH | 380 | LANCASTR | 654 | ROUGHEDG | &1 | 10392 | RED R BL 100 | 10381 | LAN R BL 100 | 1 | 10381-10392-1 | 70.8 | 70.8 | 40.6 | 82.4 | 117.4 | 84 | 70.8 | 38.8 | 80.9 | 114.9 | 71 | -2.5 | 2011 | 2011 | 0 |  | 58.2 | 70.8 | 58.2 | MONROE BL | 100 kV Line | 71.1852 | 78.1132 | 71.1852 | 70.8 | 22.6 | 61.9 | 87.3 | 20.5 | 30.1
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 70.1 | 122.1 | 114.5 | 124 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 339.1 | 513.8 | 105.6 | 86 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 125.8 | 26.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 339.1 | 513.8 | 105.6 | 87 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 125.8 | 26.6
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.3 | 210.5 | 103.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.6 | 97.1 | 103.4 | 45 | 95 | 43.5 | 86.2 | 91.6 | 5 | -11.8 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.9 | 309.9 | 103.3 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1090.4 | 1370 | 99.3 | 8826 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -4.4 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1725 | 1904.2 | 97.7 | 7758 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -2.6 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 303.6 | 17.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.8 | 195.2 | 97.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.6 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107 | 194.9 | 97.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 452.4 | 774.6 | 97.2 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -3.7 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 104.6 | 13.1
THALGM | SINGLE 54 | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.4 | 315.4 | 97.1 | 1402 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.2 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 51.7 | 103.4 | 96.9 | 44 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.5 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 375.6 | 96.3 | 996 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.2 | 157.8 | 96.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 503.6 | 805 | 95.8 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.4 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 73.7 | 8.7
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84.4 | 105.6 | 95.2 | 868 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.9 | 429.8 | 94.2 | 1365 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 249 | 437.6 | 94.1 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.6 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 23.9 | 139.4 | 93.8 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.5 | 100.9 | 93.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.6 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.4 | 10.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.5 | 100.9 | 93.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.6 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.4 | 10.5
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343.5 | 388.2 | 92.3 | 2180 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.9 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.7 | 13.4
WYLIGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.3 | 323 | 92.3 | 270 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 152.1 | 184.2 | 92.1 | 100 | 200 | 140 | 176.3 | 88.1 | 12 | -4 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 108.9 | 183.9 | 92 | 80 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 108.6 | 183.7 | 91.9 | 79 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 437 | 767.7 | 91.4 | 47 | 840 | 420.2 | 738.3 | 87.9 | 44 | -3.5 | 2016 | 2018 | 2 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 103.7 | 12.3
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 39.9 | 85.3 | 91.2 | 48 | 95 | 32.8 | 74.4 | 79.4 | 42 | -11.8 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68 | 184 | 91.2 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.7 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 50.6 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.2 | 438.5 | 90.8 | 264 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.2 | 6.2
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420 | 762.2 | 90.7 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.4 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 69.5 | 8.2
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 321.3 | 421.5 | 90.5 | 791 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.8 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 44.6 | 95.9 | 90.2 | 13 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.5 | 95 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.8 | 91.4 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 966.4 | 90.6 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 963.3 | 90.3 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.2 | 118.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -5.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.1 | 29.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 470.3 | 98.4 | 232 | 478 | - | 464 | 97.1 | 232 | -1.3 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 89.9 | 18.8
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1844.8 | 96.9 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -2.1 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 303.7 | 16
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.4 | 93.1 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.8 | 92.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 986.6 | 92.5 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 143.1 | 95.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.5 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 93 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.8 | 88.4
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.1 | 92.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 966.4 | 989.8
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.8 | 92.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 963.3 | 986.6
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.5 | 92.2 | 21 | 96 | - | 84.8 | 88.3 | 21 | -3.9 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15 | 15.6 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.4 | 90.3 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.4 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.2 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_Duke
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 12 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 3 | Not in original screening
[25 empty] | 15 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
TUXDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665.7 | 1679.8 | 204.4 | 5364 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.2 | 161.4 | 548 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.4 | 160.1 | 133.9 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 2.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.7 | 240.5 | 118.7 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -10.5 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 68.8 | 112 | 104.9 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 5.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.6 | 210.9 | 104.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 214.6 | 311.1 | 103.7 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -6.8 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 371 | 21.6
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 474 | 811.3 | 101.8 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -8.3 | 2011 | 2015 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 141.3 | 17.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 63.5 | 107.9 | 101.1 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 174 | 20122 | REGNCYPK | 20211 | APEX | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.8 | 315.2 | 97 | 679 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75 | 158.4 | 96.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.9 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.9 | 375.5 | 96.3 | 873 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 457.8 | 804.1 | 95.7 | 80 | 840 | 420.2 | 738.3 | 87.9 | 44 | -7.8 | 2014 | 2018 | 4 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 140.1 | 16.6
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 68 | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84 | 105.6 | 95.1 | 707 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.6 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105 | 190.2 | 95.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.3 | 190 | 95 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 498.3 | 796.6 | 94.8 | 78 | 840 | 501.2 | 801.2 | 95.4 | 82 | 0.6 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 65.3 | 7.7
MCG2GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.1 | 139.4 | 93.8 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 287.6 | 425.5 | 93.6 | 52 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | -1.5 | 2015 | 2016 | 1 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | 4.7 | 2.2
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 38.5 | 55.1 | 93.6 | 42 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 19.7 | 2015 | 2011 | -4 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 38.5 | 55.1 | 93.6 | 48 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 19.7 | 2015 | 2011 | -4 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.6 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 22.6 | 14.1
OCO1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 841 | 6BOBWH B 230 | 1 | 714-841-1 | 478 | 478 | 359.8 | 449 | 92.9 | 376 | 478 | 328.3 | 416.2 | 85.7 | 126 | -7.2 | 2015 | 2019 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 64.1 | 14.5
OCO3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 842 | 6BOBWH W 230 | 2 | 714-842-2 | 478 | 478 | 360 | 449 | 92.9 | 419 | 478 | 328.3 | 416.2 | 85.7 | 162 | -7.2 | 2015 | 2019 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 64.1 | 14.5
BRDGGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 131 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 291.8 | 453 | 92.8 | 39 | 478 | 333.2 | 503.2 | 103.2 | 68 | 10.4 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 65 | 13.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 291.8 | 453 | 92.8 | 40 | 478 | 333.2 | 503.2 | 103.2 | 69 | 10.4 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 65 | 13.8
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 321.1 | 424.7 | 92.7 | 1264 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.9 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1.4 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 10.6 | 9.7
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1.4 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 10.6 | 9.7
BEL1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 109.3 | 184.6 | 92.3 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 257 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 109.1 | 184.5 | 92.2 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 242.9 | 430 | 92.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 270.3 | 398.8 | 91.5 | 167 | 437 | 249.4 | 367.6 | 83.9 | 85 | -7.6 | 2016 | 2020 | 4 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 676 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 270.3 | 398.8 | 91.5 | 211 | 437 | 248.6 | 366.8 | 83.9 | 128 | -7.6 | 2016 | 2020 | 4 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 48.9 | 19.3
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68.3 | 184.5 | 91.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.5 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 1 | 7-106-1 | 478 | 478 | 193.9 | 448.6 | 91.3 | 5 | 478 | 187.8 | 430.9 | 87.6 | 2 | -3.7 | 2016 | 2018 | 2 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 2 | 7-106-2 | 478 | 478 | 193.9 | 448.6 | 91.3 | 5 | 478 | 187.8 | 430.9 | 87.6 | 2 | -3.7 | 2016 | 2018 | 2 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230 | 540 | 6MCGUIRE 230 | 1 | 537-540-1 | 318.6 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | 318.6 | 162.7 | 283.2 | 86.9 | 44 | -4.3 | 2016 | 2019 | 3 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 57.1 | 18.4
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 49.4 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 332.2 | 435.9 | 90.3 | 233 | 478 | 334.2 | 438.6 | 90.7 | 252 | 0.4 | 2017 | 2016 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 24.6 | 5.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1726.3 | 90.7 | 176 | 1904.3 | - | 1623 | 85.2 | 176 | -5.5 | 2016 | 2020 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1369 | 71.9 | 357.3 | 18.8
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 963.2 | 90.3 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1909.2 | 100.3 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -5.5 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 368.1 | 19.4
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 58.1 | 99.4 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 13.2 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 6 | 10.3
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.6 | 92.4 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.9 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.5 | 92.1 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_Duke
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.5 | 95 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.8 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 142 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 88.1
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.7 | 92.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.2 | 985.6
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.6 | 92.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 960.2 | 982.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293 | 90.2 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.2 | #N/A | #N/A
Populate Summary Worksheet