## RelResults Summary
PEC Reliability Study Summary |  |  | PEC Import 3600 MW (>90% loading) |  | BaseCase | PEC Import 3200 MW (>94% loading) |  | Duke Generation Outage Sensitivity PEC Import 3200 MW (>94% loading) | [9 empty] | Duke Transmission Outage Sensitivity PEC Import 3200 MW (>94% loading)
2011 Summer |  |  | Loading% |  | Loading% | Loading% |  | Loading% | [9 empty] | Loading% of Richmond-Newport 500kV Line
[8 empty] | Ble1 |  | Cat |  | Marshall 3 |  | McG1 |  | McG2 |  | Contingency | HR Dn Shorterm | BR1 DN Shorterm
Monitored Facility | Contingency Facility | Rating MVA | Br1 | Har | GenUp | Br1 | Har | Br1 | Har | Br1 | Har | Br1 | Har | Br1 | Har | Br1 | Har
20377 RICHMOND 500 337 8NEWPORT 500 1 | PHSH1-ANSON230_&_PHSH2-ANSON230 | 1350 | 109.1 | 107.6 | 81 | 102.8 | 101.3 | 103.9 | 102.3 | 97.5 | 95.8 | 100 | 98.4 | 99 | 97.5 | 97.7 | 96 | GUARDNORTH | 111.9 | 113 | Reduced rating was a test as possible phase angle limit. Ignore loadings. Rating not applicable for contingencies other than Rich-Newport 500
20185 FALLS 115 20182 FALLS 230 1 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115 | 300 | 104.3 | 104.9 | 101.4 | 103.4 | 104.1 | 103.2 | 103.9 | 104 | 104.7 | 103.8 | 104.5 | 103.9 | 104.6 | 103.8 | 104.5 | PARKWOOD | 101.5 | 102.5 | Add project to plan for 2013. Seen in other studies.
20039 SUT 3 F 230 20554 9THORG T 230 1 | BR1-BARCK230_&_BR2-BARCRK230 | 590 | 100.4 | 106.4 | 107.7 | 100.6 | 104.2 | 101.1 | 107.1 | 101.1 | 103.4 | 100.5 | 111.3 | 100.7 | 106 | 100.7 | 111.2 | GUARDSOUTH | 100.2 | 101.3 | Operating procedure established reducing generation.
20421 LAURINBG 115 20424 LAURINBG 230 1 | 20421 LAURINBG 115 20424 LAURINBG 230 2 | 200 | 97.1 | 98.9 | 94.9 | 97.8 | 99.5 | 98 | 99.7 | 96.8 | 98.5 | 97.2 | 98.9 | 97.2 | 98.9 | 97.3 | 99 | STEPHENS | 99.2 | 100.6 | Project in 2012. May can delay.
20421 LAURINBG 115 20424 LAURINBG 230 2 | 20421 LAURINBG 115 20424 LAURINBG 230 1 | 200 | 97 | 98.8 | 94.8 | 97.6 | 99.3 | 97.8 | 99.6 | 96.7 | 98.4 | 97.1 | 98.8 | 97 | 98.7 | 97.2 | 98.9 | ROCK_SPRINGS | 95.1 | 96.4 | Same
20654 DILLON T 115 20632 MARION 115 1 | 20663 LATTA 230 20682 DILLMP T 230 1 | 97 | 95.3 |  |  | 97.1 |  | 97.8 |  |  |  | 94.4 |  | 94.8 |  | 96.1 |  | CPL1aor | 94.8 | 96.2 | Operating procedure established to open circuit.
20185 FALLS 115 20111 E18-WK F 115 1 | 20089 HENDERSN 115 20105 FRANKLIN 115 1 | 170 | 94.8 |  | 94.1 | 94 | 92.5 |  |  | 94.4 |  | 94.3 |  | 94.3 |  | 94.3 |  | CPL1b | 94 | 95.2 | Establish operating procedure to move load.
20304 E14-ULAH 115 20303 SEAGROVE 115 1 | 20309 BISCOE W 230 20332 ASHEB 230 1 | 148 |  | 102.6 |  |  | 100.9 |  | 101.3 |  | 99.3 |  | 99.6 |  | 99.2 |  | 100.5 |  |  |  | Operating procedure established to open bank.
B$0024 1.00 20183 WAKE 500 1 | 3Wnd: OPEN B$0045 2 | 1000 | 94.1 | 98.4 | 75 | 90.9 | 95.5 |  | 95.7 |  | 94.8 |  | 95 |  | 95 |  | 94.8 | GUARDNORTH | = (cplgen 500 - PL GRDN 500) |  | Follow. May need to increas bank size or add bank.
B$0045 1.00 20183 WAKE 500 2 | 3Wnd: OPEN B$0024 1 | 1000 | 94.1 | 98.3 | 75 | 90.9 | 95.5 |  | 95.7 |  | 94.8 |  | 95 |  | 95 |  | 94.7 | PARKWOOD | =(Parkwood - PL GRDN 500) |  | Follow. May need to increas bank size or add bank.
20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | 637 |  | 99.2 |  |  | 97.4 |  | 98 |  | 94.8 |  | 95.8 |  | 95.5 |  | 95.7 | STEPHENS | =(O'conee - S Hall 500) |  | Project in 2012
20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | 637 |  | 95.4 |  |  | 92.7 | [13 empty] | Project in 2013
20615 BARNARD 230 20616 BARNARD 115 1 | ** Base Case ** | 150 | 95.3 | 95.3 | 95.2 | 95.3 | 95.2 |  |  |  |  | 95.3 | [5 empty] | ROCK_SPRINGS | =(McGuire- Antioch 500) |  | Constant loading over contingencies. Follow.
20155 CHSTNT H 115 20163 MILBURNE 115 1 | 20145 NEUSE 115 20185 FALLS 115 1 | 158 | 94 | 94.3 | 93.2 | 93.7 | 94.1 |  | 94.2 |  | 94.1 |  | 94.1 |  | 94.1 |  | 94.1 | CPL1aor | =(Mayo-durha-mayo 500kV) |  | Constant loading over contingencies. Follow.
20387 P1-FAY 0 230 20392 FAY 115 2 | 20387 P1-FAY 0 230 20392 FAY 115 1 | 200 | 95.7 |  |  | 93.4 | 90.2 | [10 empty] | CPL1b | =(Wake-Carson 500kV) |  | Project in 2012. Follow.
20387 P1-FAY 0 230 20392 FAY 115 1 | 20387 P1-FAY 0 230 20392 FAY 115 2 | 200 | 95.7 |  |  | 93.4 | 90.1 | [13 empty] | Same
Note on A4: PTI: ** From bus ** ** To bus ** Circuit Type
Note on B4: PTI: Contingency Description

## 3600 MW BR1 DN BRANCH
Branch Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- MON, APR 17 2006 15:26
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 REL6/05, 400 IMP DUKE, BR1 DN
Case.File J:\NC Stakeholders\2011S Study\Study Cases\TRMcases\400MW_Intch_Mod\duk11s_PEC_FinalNP_400MW_IntchMod_Br1Dn.sav
Subsys.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.sub
Monit.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.mon
Contin.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-Eastern System.EXC
************** Report on violations ********************
Branches with MVA flow more than 90.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Ncon | Contingency
20039 SUT 3 F 230 20554 9THORG T 230 1 | LN | 592.2 | 301 | 590 | 100.4 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20155 CHSTNT H 115 20163 MILBURNE 115 1 | LN | 148.6 | 18.9 | 158 | 94 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20168 YONKERS 115 20163 MILBURNE 115 1 | LN | 173.2 | 50.1 | 190 | 91.2 | 223 | 20137 METHOD 115 20150 I-NCSU S 115 1
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 161.2 | 70.6 | 170 | 94.8 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 154.3 | 70.6 | 170 | 90.8 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 153.8 | 70.6 | 170 | 90.5 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | TR | 312.8 | 210.1 | 300 | 104.3 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | TR | 307.8 | 210.1 | 300 | 102.6 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20182 FALLS 230 1 | TR | 280 | 210.1 | 300 | 93.3 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20185 FALLS 115 20182 FALLS 230 1 | TR | 271.7 | 210.1 | 300 | 90.6 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20349 PH SH 2W 230 20985 ANSON 230 1 | LN | 367.9 | 213.9 | 398 | 92.4 | 869 | 337 8NEWPORT 500 20377 RICHMOND 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1472.6 | 1310.5 | 1350 | 109.1 | 33 | PHSH1-ANSON230_&_PHSH2-ANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1371.7 | 1310.5 | 1350 | 101.6 | 61 | 20015 MAYO 1F 500 20054 DURHAM 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1360.3 | 1310.5 | 1350 | 100.8 | 32 | OAKBORO-ANSON230_&_OAKBORO-IANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1361.4 | 1310.5 | 1350 | 100.8 | 864 | 44902 8CARSON 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1358.9 | 1310.5 | 1350 | 100.7 | 31 | BOWMANT-IANSON230_&_ANSON-OAKBORO230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1358.9 | 1310.5 | 1350 | 100.7 | 34 | ANSON-OAKBORO230_&_ANSON-BOWMANT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1343.8 | 1310.5 | 1350 | 99.5 | 465 | 20348 RKH 230 20349 PH SH 2W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1343.9 | 1310.5 | 1350 | 99.5 | 466 | 20348 RKH 230 20350 PH SH 1B 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1343.8 | 1310.5 | 1350 | 99.5 | 472 | 20349 PH SH 2W 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1343.9 | 1310.5 | 1350 | 99.5 | 473 | 20350 PH SH 1B 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1340 | 1310.5 | 1350 | 99.3 | 35 | ROB-NUCOR230_&_ROB-REIDPK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1340.7 | 1310.5 | 1350 | 99.3 | 126 | 20054 DURHAM 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1339.9 | 1310.5 | 1350 | 99.3 | 863 | 845 6E.DURHM 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1339.4 | 1310.5 | 1350 | 99.2 | 5 | ROX-FALLS230_&_FALLS23-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1339.2 | 1310.5 | 1350 | 99.2 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1337.2 | 1310.5 | 1350 | 99.1 | 69 | 20018 ROB 2 N 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1336.3 | 1310.5 | 1350 | 99 | 6 | ROX-FALLS230_&_PER-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1336.2 | 1310.5 | 1350 | 99 | 129 | 20057 DARL CO 230 20668 I-TALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1334.8 | 1310.5 | 1350 | 98.9 | 795 | 20668 I-TALLY 230 20705 SOCTY HL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1333.5 | 1310.5 | 1350 | 98.8 | 827 | 20705 SOCTY HL 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1334.4 | 1310.5 | 1350 | 98.8 | 860 | 845 6E.DURHM 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1333.8 | 1310.5 | 1350 | 98.8 | 879 | 42002 6WATEREE 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1332.4 | 1310.5 | 1350 | 98.7 | 17 | FALLS-MILB230_&_FALLS23-HOMESTED230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1331.4 | 1310.5 | 1350 | 98.6 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1331.1 | 1310.5 | 1350 | 98.6 | 153 | 20073 BLUE RDG 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1329.7 | 1310.5 | 1350 | 98.5 | 2 | ROX-EDANVLN230_&_YANCYVLT-EDANVL230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1330 | 1310.5 | 1350 | 98.5 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1330.3 | 1310.5 | 1350 | 98.5 | 802 | 20676 KINGST N 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1329.9 | 1310.5 | 1350 | 98.5 | 876 | 43008 6KNGSTRE 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1328.3 | 1310.5 | 1350 | 98.4 | 15 | FALLS-MILB230_&_HOMESTED-PINELK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1328.2 | 1310.5 | 1350 | 98.4 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1328.3 | 1310.5 | 1350 | 98.4 | 50 | 20004 TIL 1-4H 115 20302 E14-TROY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1328 | 1310.5 | 1350 | 98.4 | 154 | 20073 BLUE RDG 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1328.4 | 1310.5 | 1350 | 98.4 | 801 | 20675 LAKE CTY 230 20676 KINGST N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1327.6 | 1310.5 | 1350 | 98.3 | 1 | ROX-EDANVL230_&_CONCORD-YANCYVLT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1326.8 | 1310.5 | 1350 | 98.3 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1327.6 | 1310.5 | 1350 | 98.3 | 39 | MARION-MARION(SCPSA)230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1327.3 | 1310.5 | 1350 | 98.3 | 415 | 20302 E14-TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1326.7 | 1310.5 | 1350 | 98.3 | 471 | 20348 RKH 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1327.7 | 1310.5 | 1350 | 98.3 | 733 | 20587 E1-CHADP 230 20631 MARION 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1326.7 | 1310.5 | 1350 | 98.3 | 800 | 20674 OLANTA 230 20675 LAKE CTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1326.7 | 1310.5 | 1350 | 98.3 | 828 | 20706 BENETSVL 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.2 | 1310.5 | 1350 | 98.2 | 16 | FALLS-MILB230_&_PINELK-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1326.2 | 1310.5 | 1350 | 98.2 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.2 | 1310.5 | 1350 | 98.2 | 145 | 20066 FALLS23 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.9 | 1310.5 | 1350 | 98.2 | 150 | 20070 PERSON 230 20079 OXF S T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.7 | 1310.5 | 1350 | 98.2 | 414 | 20301 TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.8 | 1310.5 | 1350 | 98.2 | 799 | 20671 SARDIS 230 20674 OLANTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1323.9 | 1310.5 | 1350 | 98.1 | 146 | 20066 FALLS23 230 20157 HOMESTED 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324.1 | 1310.5 | 1350 | 98.1 | 159 | 20079 OXF S T 230 20085 OXFORD N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1323.9 | 1310.5 | 1350 | 98.1 | 413 | 20301 TROY 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324.7 | 1310.5 | 1350 | 98.1 | 557 | 20424 LAURINBG 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324.9 | 1310.5 | 1350 | 98.1 | 732 | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324.8 | 1310.5 | 1350 | 98.1 | 798 | 20671 SARDIS 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1323.6 | 1310.5 | 1350 | 98 | 20 | MILB-FALLS230_&_MILB-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1323.4 | 1310.5 | 1350 | 98 | 778 | 20653 CASHUA 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322.7 | 1310.5 | 1350 | 98 | 868 | 542 6OAKBORO 230 20248 I-ANSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322.3 | 1310.5 | 1350 | 98 | 882 | 542 6OAKBORO 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.3 | 1310.5 | 1350 | 97.9 | 21 | TILLERY-BADIN1&2_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.8 | 1310.5 | 1350 | 97.9 | 36 | SUMT-WDGFLD230_&_GOLDT-KNGHWY115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.8 | 1310.5 | 1350 | 97.9 | 37 | SUMT-WDGFLD230_&_SUMT-GOLDT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.7 | 1310.5 | 1350 | 97.9 | 85 | 20024 ROX 1-4F 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322.3 | 1310.5 | 1350 | 97.9 | 151 | 20070 PERSON 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.9 | 1310.5 | 1350 | 97.9 | 165 | 20085 OXFORD N 230 20087 HEND E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322 | 1310.5 | 1350 | 97.9 | 357 | 20248 I-ANSONV 230 20358 BOWMAN T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322 | 1310.5 | 1350 | 97.9 | 482 | 20358 BOWMAN T 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.6 | 1310.5 | 1350 | 97.9 | 777 | 20653 CASHUA 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322.1 | 1310.5 | 1350 | 97.9 | 788 | 20662 FLORENCE 230 20663 LATTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.8 | 1310.5 | 1350 | 97.9 | 824 | 20700 SUMTER 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.3 | 1310.5 | 1350 | 97.9 | 856 | 43014 6S BETH 230 20057 DARL CO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1320.4 | 1310.5 | 1350 | 97.8 | 47 | GRNVL-CHOCWNTY230_&_GRNVL-EVERETT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1320.5 | 1310.5 | 1350 | 97.8 | 62 | 20015 MAYO 1F 500 20071 PERSON 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1320.1 | 1310.5 | 1350 | 97.8 | 107 | 20044 ROB 1 F 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1320.5 | 1310.5 | 1350 | 97.8 | 152 | 3Wnd: OPEN B$0011 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1319.6 | 1310.5 | 1350 | 97.8 | 168 | 20087 HEND E 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1320.4 | 1310.5 | 1350 | 97.8 | 247 | 20157 HOMESTED 230 20160 PINE LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1319.7 | 1310.5 | 1350 | 97.8 | 866 | 44591 6NASH 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318.8 | 1310.5 | 1350 | 97.7 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318.4 | 1310.5 | 1350 | 97.7 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1319.3 | 1310.5 | 1350 | 97.7 | 19 | MILB-WHITEOAK230_&_MILB-AUBURN230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1319.4 | 1310.5 | 1350 | 97.7 | 46 | RKYMT-NASH230_&_RKYMT-EDGCMB230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1319.2 | 1310.5 | 1350 | 97.7 | 808 | 20684 ALICE DR 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317.2 | 1310.5 | 1350 | 97.6 | 70 | 20018 ROB 2 N 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318 | 1310.5 | 1350 | 97.6 | 175 | 20091 BRIERCK 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317.3 | 1310.5 | 1350 | 97.6 | 176 | 20091 BRIERCK 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317.7 | 1310.5 | 1350 | 97.6 | 249 | 20160 PINE LK 230 20161 FOXCROFT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317.3 | 1310.5 | 1350 | 97.6 | 809 | 20684 ALICE DR 230 20703 SUMTER N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318 | 1310.5 | 1350 | 97.6 | 825 | 20700 SUMTER 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317.2 | 1310.5 | 1350 | 97.6 | 832 | 20710 HARTS T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318.2 | 1310.5 | 1350 | 97.6 | 870 | 44574 6EVERETS 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.6 | 1310.5 | 1350 | 97.5 | 211 | 20126 MORRISVI 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.3 | 1310.5 | 1350 | 97.5 | 250 | 20161 FOXCROFT 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.1 | 1310.5 | 1350 | 97.5 | 254 | 20162 MILBURNE 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.8 | 1310.5 | 1350 | 97.5 | 602 | 20471 CCWDCG T 230 20472 CG-CC WD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.7 | 1310.5 | 1350 | 97.5 | 719 | 20578 CG-ELIZ 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.6 | 1310.5 | 1350 | 97.5 | 742 | 20601 CG-SOPRT 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.4 | 1310.5 | 1350 | 97.4 | 147 | 20067 MAYOSUSW 230 20068 RXBOWMAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.5 | 1310.5 | 1350 | 97.4 | 148 | 20067 MAYOSUSW 230 20088 HENDERSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.9 | 1310.5 | 1350 | 97.4 | 149 | 20068 RXBOWMAN 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.3 | 1310.5 | 1350 | 97.4 | 196 | 20117 DURHAM 230 20118 RDU AIRP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.6 | 1310.5 | 1350 | 97.4 | 197 | 20118 RDU AIRP 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.3 | 1310.5 | 1350 | 97.4 | 198 | 20119 PRISON F 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315 | 1310.5 | 1350 | 97.4 | 210 | 20126 MORRISVI 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.7 | 1310.5 | 1350 | 97.4 | 253 | 20162 MILBURNE 230 20178 AUBURN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.7 | 1310.5 | 1350 | 97.4 | 278 | 20188 PA-SELMA 230 20192 SELMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315 | 1310.5 | 1350 | 97.4 | 279 | 20188 PA-SELMA 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.3 | 1310.5 | 1350 | 97.4 | 281 | 20190 WAKE 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.8 | 1310.5 | 1350 | 97.4 | 422 | 20310 E17-SARE 115 20605 CG-KORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.7 | 1310.5 | 1350 | 97.4 | 756 | 20630 MULLINS 115 20632 MARION 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.9 | 1310.5 | 1350 | 97.4 | 822 | 20699 SUMMER T 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.2 | 1310.5 | 1350 | 97.4 | 855 | 52577 05EDANV1 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.5 | 1310.5 | 1350 | 97.4 | 861 | 52578 05EDANV2 230 20094 YANCY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.5 | 1310.5 | 1350 | 97.4 | 878 | 42001 6SANTEE 230 20699 SUMMER T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314 | 1310.5 | 1350 | 97.3 | 9 | METH-NCCENT230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.8 | 1310.5 | 1350 | 97.3 | 10 | NCCENT-CARALI230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.9 | 1310.5 | 1350 | 97.3 | 45 | WILSON-PA_WILSON#1_115KV_PODS
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313 | 1310.5 | 1350 | 97.3 | 52 | 20004 TIL 1-4H 115 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.4 | 1310.5 | 1350 | 97.3 | 57 | 20009 HARRIS1N 230 20204 DUNCAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.2 | 1310.5 | 1350 | 97.3 | 60 | 20009 HARRIS1N 230 20338 E15-BRDW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.5 | 1310.5 | 1350 | 97.3 | 111 | 20046 WSPN BUS 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.3 | 1310.5 | 1350 | 97.3 | 120 | 20050 PA-GRN W 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.2 | 1310.5 | 1350 | 97.3 | 155 | 20077 SIX FORK 230 20078 WD VALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314 | 1310.5 | 1350 | 97.3 | 157 | 20078 WD VALLY 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.1 | 1310.5 | 1350 | 97.3 | 160 | 20082 I-NCCENT 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.1 | 1310.5 | 1350 | 97.3 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.7 | 1310.5 | 1350 | 97.3 | 179 | 20094 YANCY T 230 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.5 | 1310.5 | 1350 | 97.3 | 199 | 20119 PRISON F 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.2 | 1310.5 | 1350 | 97.3 | 201 | 20120 CARY TAP 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.7 | 1310.5 | 1350 | 97.3 | 239 | 20151 WHITEOAK 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.1 | 1310.5 | 1350 | 97.3 | 271 | 20178 AUBURN 230 20179 WILS MIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.5 | 1310.5 | 1350 | 97.3 | 272 | 20179 WILS MIL 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.1 | 1310.5 | 1350 | 97.3 | 302 | 20204 DUNCAN 230 20213 FUQUAY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.9 | 1310.5 | 1350 | 97.3 | 325 | 20222 ROCKY MT 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314 | 1310.5 | 1350 | 97.3 | 330 | 20228 WILSON 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.9 | 1310.5 | 1350 | 97.3 | 386 | 20274 EKRN+CGK 115 20310 E17-SARE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.4 | 1310.5 | 1350 | 97.3 | 454 | 20338 E15-BRDW 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.2 | 1310.5 | 1350 | 97.3 | 577 | 20451 PA-GRNVL 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.3 | 1310.5 | 1350 | 97.3 | 579 | 20453 PA-WASH 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.4 | 1310.5 | 1350 | 97.3 | 755 | 20629 NICHOLS 115 20630 MULLINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.1 | 1310.5 | 1350 | 97.3 | 762 | 20632 MARION 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313 | 1310.5 | 1350 | 97.3 | 764 | 20633 INDST T 115 20635 I-DUP FL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313 | 1310.5 | 1350 | 97.3 | 765 | 20633 INDST T 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.4 | 1310.5 | 1350 | 97.3 | 767 | 20635 I-DUP FL 115 20641 I-STONE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.1 | 1310.5 | 1350 | 97.3 | 773 | 20644 PAMPLICO 115 20645 HEMINGWA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314 | 1310.5 | 1350 | 97.3 | 774 | 20645 HEMINGWA 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.1 | 1310.5 | 1350 | 97.3 | 826 | 20703 SUMTER N 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.8 | 1310.5 | 1350 | 97.3 | 858 | 44697 6HALIFAX 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.1 | 1310.5 | 1350 | 97.3 | 873 | 43007 3HEMING1 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313 | 1310.5 | 1350 | 97.3 | 883 | 2511 BADIN 100 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.7 | 1310.5 | 1350 | 97.3 | 885 | 416 WATEREE 100 20734 WATRE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.1 | 1310.5 | 1350 | 97.2 | 13 | FALLS-HONEYCUT230_&_FALLS-LAKESTON115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 14 | FALLS-LAKESTON115_&_CHSTNTHL-NEUSE115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 18 | MILB-CLAYTON115_&_MILB-PERSTP115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 23 | BISCOEW-BISCOESUB115_&_SPRINGT-I_FNDRY_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.2 | 1310.5 | 1350 | 97.2 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.8 | 1310.5 | 1350 | 97.2 | 53 | 20004 TIL 1-4H 115 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.8 | 1310.5 | 1350 | 97.2 | 68 | 20018 ROB 2 N 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.7 | 1310.5 | 1350 | 97.2 | 73 | 20020 BRUN 2 N 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312 | 1310.5 | 1350 | 97.2 | 74 | 20020 BRUN 2 N 230 20615 BARNARD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.2 | 1310.5 | 1350 | 97.2 | 115 | 20047 WSP BUS 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.8 | 1310.5 | 1350 | 97.2 | 121 | 20050 PA-GRN W 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.2 | 1310.5 | 1350 | 97.2 | 130 | 20057 DARL CO 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.6 | 1310.5 | 1350 | 97.2 | 132 | 20059 E18-KITT 115 20089 HENDERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 133 | 20059 E18-KITT 115 20096 YOUNGSVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 156 | 20077 SIX FORK 230 20083 HONEYCUT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.8 | 1310.5 | 1350 | 97.2 | 161 | 20082 I-NCCENT 230 20125 CARALEIG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.1 | 1310.5 | 1350 | 97.2 | 162 | 20083 HONEYCUT 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 163 | 20084 I-NOVO 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312 | 1310.5 | 1350 | 97.2 | 164 | 20084 I-NOVO 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 166 | 20086 E12-HYCO 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 167 | 20086 E12-HYCO 115 20093 CONCORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 177 | 20093 CONCORD 115 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 180 | 20096 YOUNGSVL 115 20141 WF T NC2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 184 | 20100 HEND N T 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 189 | 20108 LOUISBRG 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.8 | 1310.5 | 1350 | 97.2 | 202 | 20120 CARY TAP 230 20173 TRI FRST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 206 | 20124 METHOD 230 20129 OAKDAL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 209 | 20125 CARALEIG 230 20130 EAST ST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.6 | 1310.5 | 1350 | 97.2 | 240 | 20151 WHITEOAK 230 20186 EDMONDSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312 | 1310.5 | 1350 | 97.2 | 257 | 20163 MILBURNE 115 20170 CLAYTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 291 | 20196 ERWIN 230 20215 BUIES CK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 307 | 20205 CLINTON 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 315 | 20213 FUQUAY 230 20214 ANGIER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.2 | 1310.5 | 1350 | 97.2 | 316 | 20214 ANGIER 230 20215 BUIES CK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 335 | 20230 WILSON 115 20242 PA-W1-1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 351 | 20242 PA-W1-1 115 20243 PA-W-6 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 404 | 20292 E14-ETHR 115 20294 BISCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.2 | 405 | 20292 E14-ETHR 115 20303 SEAGROVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 406 | 20294 BISCOSUB 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 475 | 20352 BURLCR T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 507 | 20379 M-FBMAIN 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.8 | 1310.5 | 1350 | 97.2 | 575 | 20448 FAIRMONT 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 594 | 20465 NEW BERN 230 20484 HAVELOCK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 595 | 20465 NEW BERN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 596 | 20465 NEW BERN 230 20506 DOVER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 634 | 20500 WOMMACK 230 20506 DOVER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 640 | 20505 ROSE HIL 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.8 | 1310.5 | 1350 | 97.2 | 715 | 20571 ELIZAB T 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 725 | 20582 DELCO 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.9 | 1310.5 | 1350 | 97.2 | 735 | 20588 CHADBN T 115 20590 TABOR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 737 | 20590 TABOR T 115 20597 E1-CHRYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 738 | 20597 E1-CHRYG 115 20598 FAIR B T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.7 | 1310.5 | 1350 | 97.2 | 740 | 20598 FAIR B T 115 20629 NICHOLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 761 | 20632 MARION 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 770 | 20641 I-STONE 115 20642 DELTA T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 772 | 20642 DELTA T 115 20644 PAMPLICO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.3 | 1310.5 | 1350 | 97.2 | 779 | 20655 FLOR SO 115 20656 I-ESAB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.4 | 1310.5 | 1350 | 97.2 | 780 | 20656 I-ESAB 115 20657 GE TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 782 | 20657 GE TAP 115 20659 FLORENCE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 842 | 20721 BETHNE T 115 20723 CAMD JCT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 844 | 20723 CAMD JCT 115 20734 WATRE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1310.5 | 1350 | 97.2 | 862 | 44702 3KERR 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1310.5 | 1350 | 97.2 | 875 | 43005 6DARLING 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1310.5 | 1350 | 97.2 | 877 | 42003 3EASTOVE 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.8 | 1310.5 | 1350 | 97.2 | 884 | 2511 BADIN 100 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 |  | ** Base Case **
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 12 | METH-TRYONHL115_&_METH-RALSO115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 43 | LEE-BELFAST115_&_LEE-NEWHOPE115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 44 | LEE-CLINTON230_&_LEE-FRIENDSHIP_T_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 54 | 20009 HARRIS1N 230 20041 CF 5-6 F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 55 | 20009 HARRIS1N 230 20041 CF 5-6 F 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 59 | 20009 HARRIS1N 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 63 | 20018 ROB 2 N 230 20044 ROB 1 F 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 64 | 20018 ROB 2 N 230 20044 ROB 1 F 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 65 | 20018 ROB 2 N 230 20057 DARL CO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 66 | 20018 ROB 2 N 230 20057 DARL CO 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 67 | 20018 ROB 2 N 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 72 | 20020 BRUN 2 N 230 20603 E1-PROSP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 79 | 20024 ROX 1-4F 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 80 | 20024 ROX 1-4F 230 20070 PERSON 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 81 | 20024 ROX 1-4F 230 20070 PERSON 230 3
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 88 | 20030 LEE 1-3F 115 20253 E17-RSWD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 89 | 20030 LEE 1-3F 115 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 90 | 20030 LEE 1-3F 115 20261 LEE 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 91 | 20030 LEE 1-3F 115 20266 E17-GENO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 92 | 20030 LEE 1-3F 115 20281 BELFAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 93 | 20030 LEE 1-3F 115 20283 NEW HOPE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 94 | 20035 SUT 1-2F 115 20545 CASTLE H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 95 | 20035 SUT 1-2F 115 20545 CASTLE H 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 97 | 20035 SUT 1-2F 115 20558 I-DAKMON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 98 | 20035 SUT 1-2F 115 20560 IND OOB5 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 105 | 20041 CF 5-6 F 230 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 109 | 20044 ROB 1 F 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 110 | 20046 WSPN BUS 230 20047 WSP BUS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 114 | 20047 WSP BUS 115 20406 ST PAULS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 119 | 20047 WSP BUS 115 20606 CG-LUMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 123 | 20052 CAPE F F 115 20220 LILINGTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 124 | 20052 CAPE F F 115 20286 E14-PKWD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 128 | 20057 DARL CO 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 134 | 20060 MOREHEAD 115 20494 BEAUFORT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 135 | 20060 MOREHEAD 115 20498 MR WILDW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 169 | 20088 HENDERSN 230 20089 HENDERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 170 | 20088 HENDERSN 230 20089 HENDERSN 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.2 | 1310.5 | 1350 | 97.1 | 171 | 20089 HENDERSN 115 20090 E12-ROX 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 172 | 20089 HENDERSN 115 20100 HEND N T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 174 | 20090 E12-ROX 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 181 | 20099 E18-POCO 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 182 | 20099 E18-POCO 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 185 | 20102 WARREN T 115 20104 E6-KING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.2 | 1310.5 | 1350 | 97.1 | 188 | 20108 LOUISBRG 115 20109 STALLING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 190 | 20109 STALLING 115 20110 SPRING H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 191 | 20110 SPRING H 115 20127 SPGHP SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 194 | 20116 NASHVIL 115 20127 SPGHP SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 195 | 20116 NASHVIL 115 20223 ROCKY MT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 207 | 20124 METHOD 230 20137 METHOD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 208 | 20124 METHOD 230 20137 METHOD 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 214 | 20129 OAKDAL T 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 215 | 20130 EAST ST 230 20131 WORTHDAL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 216 | 20131 WORTHDAL 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 217 | 20132 RAL SO 115 20137 METHOD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 221 | 20137 METHOD 115 20138 LAKESTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 222 | 20137 METHOD 115 20146 NORTHSID 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.2 | 1310.5 | 1350 | 97.1 | 223 | 20137 METHOD 115 20150 I-NCSU S 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 224 | 20137 METHOD 115 20153 TRYON HL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 225 | 20138 LAKESTON 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 226 | 20140 PANTH BR 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 227 | 20141 WF T NC2 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 229 | 20142 ATLANTIC 115 20143 I-AVX 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 231 | 20144 AVX TAP 115 20146 NORTHSID 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 232 | 20144 AVX TAP 115 20147 TIMBERLK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 233 | 20145 NEUSE 115 20155 CHSTNT H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 235 | 20147 TIMBERLK 115 20163 MILBURNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 236 | 20148 RALEIGH 115 20149 MORDECAI 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 237 | 20148 RALEIGH 115 20150 I-NCSU S 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 238 | 20149 MORDECAI 115 20168 YONKERS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 241 | 20152 GARNER 115 20153 TRYON HL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 242 | 20152 GARNER 115 20174 I-PERSTP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 244 | 20155 CHSTNT H 115 20163 MILBURNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 255 | 20163 MILBURNE 115 20164 KNIGHTDL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 256 | 20163 MILBURNE 115 20168 YONKERS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 258 | 20163 MILBURNE 115 20174 I-PERSTP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 259 | 20164 KNIGHTDL 115 20165 ZEB SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 260 | 20165 ZEB SUB 115 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 263 | 20170 CLAYTON 115 20172 CLAY IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 265 | 20172 CLAY IND 115 20175 SMITHF T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 266 | 20173 TRI FRST 230 20210 APEXPOD4 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 270 | 20177 SELMA 115 20252 PRINCETN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 273 | 20182 FALLS 230 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 277 | 20186 EDMONDSN 230 20196 ERWIN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 284 | 20192 SELMA 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 289 | 20196 ERWIN 230 20208 ERWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 290 | 20196 ERWIN 230 20208 ERWIN 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.5 | 1310.5 | 1350 | 97.1 | 299 | 20202 ERWINSUB 115 20208 ERWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 304 | 20205 CLINTON 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 305 | 20205 CLINTON 230 20255 CLINTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 306 | 20205 CLINTON 230 20279 MT OLIVE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 308 | 20206 MTO IN T 115 20268 E17-DUDL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 309 | 20206 MTO IN T 115 20270 MT OLV W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 312 | 20208 ERWIN 115 20220 LILINGTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 314 | 20209 ERWIN T 115 20555 IND OOB4 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 317 | 20216 E3-RDHAR 230 20333 PITTSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 318 | 20216 E3-RDHAR 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 319 | 20219 W-SHARPB 115 20223 ROCKY MT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 320 | 20219 W-SHARPB 115 20224 PA-WRE-T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 321 | 20221 PA-RMT 69.0 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 322 | 20221 PA-RMT 69.0 20222 ROCKY MT 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 323 | 20222 ROCKY MT 230 20223 ROCKY MT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 324 | 20222 ROCKY MT 230 20223 ROCKY MT 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 327 | 20224 PA-WRE-T 115 20227 ELM CITY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 329 | 20227 ELM CITY 115 20230 WILSON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 331 | 20228 WILSON 230 20230 WILSON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 332 | 20228 WILSON 230 20230 WILSON 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.2 | 1310.5 | 1350 | 97.1 | 333 | 20230 WILSON 115 20232 PA-W-1-T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.2 | 1310.5 | 1350 | 97.1 | 338 | 20232 PA-W-1-T 115 20236 PA-W-23 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 339 | 20234 PA-W-4&7 115 20243 PA-W-6 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 340 | 20234 PA-W-4&7 115 20244 PA-W-5 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 341 | 20236 PA-W-23 115 20238 BLACK CK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 348 | 20239 GOLD C T 115 20284 WEIL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 349 | 20239 GOLD C T 115 20285 SEY JOHN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 350 | 20241 I-NC GAS 115 20263 E15-BNTV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 355 | 20247 GA PAC T 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 356 | 20247 GA PAC T 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 358 | 20251 LEE 230 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 359 | 20251 LEE 230 20261 LEE 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 360 | 20251 LEE 230 20267 GRANTHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 361 | 20251 LEE 230 20279 MT OLIVE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 362 | 20252 PRINCETN 115 20253 E17-RSWD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 363 | 20254 E15-HARG 115 20255 CLINTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 364 | 20254 E15-HARG 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 366 | 20255 CLINTON 115 20257 E15-CLNT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 367 | 20257 E15-CLNT 115 20258 CLINTN N 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 372 | 20261 LEE 115 20271 FRNDSP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 373 | 20261 LEE 115 20284 WEIL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 378 | 20266 E17-GENO 115 20268 E17-DUDL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 379 | 20267 GRANTHAM 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 381 | 20270 MT OLV W 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 383 | 20271 FRNDSP T 115 20273 KORNEGAY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 384 | 20273 KORNEGAY 115 20274 EKRN+CGK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 385 | 20274 EKRN+CGK 115 20307 E17-PINK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 387 | 20275 E17-BEUL 115 20280 BEULAVIL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 388 | 20275 E17-BEUL 115 20307 E17-PINK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 389 | 20278 MT OLIVE 115 20279 MT OLIVE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 390 | 20280 BEULAVIL 115 20517 WALLACE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 391 | 20281 BELFAST 115 20282 LANGSTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 392 | 20282 LANGSTON 115 20287 GOLDS SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 393 | 20283 NEW HOPE 115 20287 GOLDS SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 394 | 20285 SEY JOHN 115 20287 GOLDS SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 395 | 20286 E14-PKWD 115 20298 ROBBINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 396 | 20287 GOLDS SW 115 20288 LAGRANGE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 398 | 20288 LAGRANGE 115 20289 E17-LAGR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 399 | 20289 E17-LAGR 115 20291 E17-FALL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 400 | 20290 I-OLVRRB 115 20304 E14-ULAH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 402 | 20290 I-OLVRRB 115 20312 ASHEB E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 403 | 20291 E17-FALL 115 20507 WOMMACK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 407 | 20296 CANDOR T 115 20298 ROBBINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 409 | 20296 CANDOR T 115 20308 I-FNDRY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 412 | 20300 I-SPRING 115 20305 SPRING T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 416 | 20303 SEAGROVE 115 20304 E14-ULAH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 417 | 20305 SPRING T 115 20308 I-FNDRY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 418 | 20305 SPRING T 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 423 | 20312 ASHEB E 115 20313 ASHEBW T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 425 | 20312 ASHEB E 115 20331 ASHEB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 427 | 20313 ASHEBW T 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 435 | 20319 ASHEB N 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 436 | 20319 ASHEB N 115 20331 ASHEB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 438 | 20321 GTP 115 20482 E13-HUGO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 439 | 20321 GTP 115 20483 SNOW HIL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 444 | 20323 RAMS TAP 115 20331 ASHEB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 445 | 20323 RAMS TAP 115 20335 SILER SB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 450 | 20333 PITTSBOR 230 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 452 | 20335 SILER SB 115 20336 E3-SILR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 453 | 20336 E3-SILR 115 20339 SILER C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 455 | 20339 SILER C 115 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 462 | 20346 RKH 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 484 | 20361 WEST END 230 20362 WEST END 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 485 | 20361 WEST END 230 20366 WEST END 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 488 | 20362 WEST END 115 20366 WEST END 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 523 | 20392 FAY 115 20403 HM CHURC 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 531 | 20403 HM CHURC 115 20404 E15-GRCK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 532 | 20404 E15-GRCK 115 20412 F DUP SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 533 | 20405 I-DUP FA 115 20412 F DUP SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 534 | 20405 I-DUP FA 115 20412 F DUP SW 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 535 | 20406 ST PAULS 115 20412 F DUP SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 543 | 20411 RAEFORD 115 20416 MAXAPT T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 546 | 20416 MAXAPT T 115 20419 WAGRAMSW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 548 | 20419 WAGRAMSW 115 20421 LAURINBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 552 | 20421 LAURINBG 115 20433 I-PLKLOF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 553 | 20421 LAURINBG 115 20452 E10-LBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 560 | 20429 E10-RENN 115 20431 SHANNON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 561 | 20429 E10-RENN 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 564 | 20433 I-PLKLOF 115 20452 E10-LBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 568 | 20437 CONVRS T 115 20438 I-CONVRS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 569 | 20437 CONVRS T 115 20440 E10-WLUM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 574 | 20447 E10-HOGS 115 20448 FAIRMONT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 580 | 20453 PA-WASH 230 20467 E16-EDWD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 582 | 20454 AURORA 230 20458 I-PCS G 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 584 | 20454 AURORA 230 20467 E16-EDWD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 585 | 20459 GRIFTON 115 20481 PA-AYDEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 586 | 20459 GRIFTON 115 20482 E13-HUGO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 591 | 20465 NEW BERN 230 20466 NEW BERN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 592 | 20465 NEW BERN 230 20466 NEW BERN 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 597 | 20466 NEW BERN 115 20468 I-AMITAL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 599 | 20466 NEW BERN 115 20475 WEYER T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 600 | 20468 I-AMITAL 115 20492 CHYPT T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 604 | 20473 E2-LAURL 115 20495 N RIVER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 605 | 20473 E2-LAURL 115 20496 E2-HARLW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 606 | 20474 DUP KIN 230 20480 DUKIN SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 609 | 20475 WEYER T 115 20477 IBRDB T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 611 | 20477 IBRDB T 115 20480 DUKIN SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 612 | 20479 I-DUPONT 115 20480 DUKIN SW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 613 | 20479 I-DUPONT 115 20480 DUKIN SW 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 614 | 20480 DUKIN SW 115 20481 PA-AYDEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 618 | 20484 HAVELOCK 230 20497 MR WILDW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 621 | 20485 HAVELOCK 115 20488 E2-CH PT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 622 | 20485 HAVELOCK 115 20490 E2-HAVLK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 623 | 20485 HAVELOCK 115 20492 CHYPT T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 624 | 20487 M-CH PT2 115 20488 E2-CH PT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 625 | 20487 M-CH PT2 115 20496 E2-HARLW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 626 | 20490 E2-HAVLK 115 20491 NEWPORT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 627 | 20491 NEWPORT 115 20503 E2-NEWPT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 629 | 20494 BEAUFORT 115 20495 N RIVER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 630 | 20497 MR WILDW 230 20498 MR WILDW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 631 | 20498 MR WILDW 115 20503 E2-NEWPT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 635 | 20500 WOMMACK 230 20507 WOMMACK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 636 | 20500 WOMMACK 230 20507 WOMMACK 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 638 | 20504 E9-N JAX 115 20530 JACKSNVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 639 | 20504 E9-N JAX 115 20536 JAX CITY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 641 | 20505 ROSE HIL 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 643 | 20507 WOMMACK 115 20509 E9-PL HI 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 645 | 20509 E9-PL HI 115 20510 E9-EAGLE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 646 | 20510 E9-EAGLE 115 20511 E9-GUM B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 647 | 20511 E9-GUM B 115 20530 JACKSNVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 650 | 20513 BURGAW C 115 20523 WALL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 653 | 20514 I-OXYCHM 115 20561 I-CEMENT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 655 | 20515 WALLACE 230 20517 WALLACE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 656 | 20515 WALLACE 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 658 | 20517 WALLACE 115 20523 WALL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 666 | 20524 JACKSONV 230 20530 JACKSNVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 667 | 20524 JACKSONV 230 20530 JACKSNVL 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 670 | 20530 JACKSNVL 115 20535 NORTHWDS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 674 | 20535 NORTHWDS 115 20536 JAX CITY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 676 | 20536 JAX CITY 115 20547 E9-DAWCB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 686 | 20545 CASTLE H 115 20550 CSTL HYN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 687 | 20545 CASTLE H 115 20550 CSTL HYN 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 689 | 20550 CSTL HYN 230 20562 I-CORNGW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 692 | 20550 CSTL HYN 230 20622 OGDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 699 | 20560 IND OOB5 115 20565 EAGLE IS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 700 | 20562 I-CORNGW 230 20625 CEDAR AV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 701 | 20563 LELANIND 115 20567 LELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 702 | 20563 LELANIND 115 20568 DELCO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 703 | 20565 EAGLE IS 115 20566 E1-WILM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 704 | 20566 E1-WILM 115 20567 LELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 706 | 20568 DELCO 115 20575 LK WACCA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 708 | 20568 DELCO 115 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 709 | 20568 DELCO 115 20582 DELCO 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 711 | 20569 ICG-IPPR 115 20579 IND OOB6 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 718 | 20575 LK WACCA 115 20583 E1-HALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 720 | 20580 WHTV TAP 115 20581 WHITEVIL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 721 | 20580 WHTV TAP 115 20583 E1-HALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 724 | 20581 WHITEVIL 115 20624 WHTVL12T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1310.5 | 1350 | 97.1 | 729 | 20585 WH IND T 115 20588 CHADBN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 730 | 20585 WH IND T 115 20624 WHTVL12T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 747 | 20615 BARNARD 230 20620 WINTER P 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 753 | 20620 WINTER P 230 20625 CEDAR AV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 754 | 20622 OGDEN 230 20626 WRIGHTVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 757 | 20631 MARION 230 20632 MARION 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 758 | 20631 MARION 230 20632 MARION 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 759 | 20631 MARION 230 20663 LATTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 760 | 20632 MARION 115 20648 BURCHES 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 763 | 20633 INDST T 115 20634 IND OOB7 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 766 | 20635 I-DUP FL 115 20639 I-ROCHE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 768 | 20639 I-ROCHE 115 20640 MARS BLF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 769 | 20640 MARS BLF 115 20659 FLORENCE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 771 | 20642 DELTA T 115 20643 I-DLTAML 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1310.5 | 1350 | 97.1 | 776 | 20648 BURCHES 115 20655 FLOR SO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 784 | 20659 FLORENCE 115 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.8 | 1310.5 | 1350 | 97.1 | 785 | 20659 FLORENCE 115 20662 FLORENCE 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 786 | 20659 FLORENCE 115 20681 PINEVILL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 789 | 20662 FLORENCE 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311 | 1310.5 | 1350 | 97.1 | 790 | 20662 FLORENCE 230 20670 FLOR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 796 | 20669 DARLN T 115 20681 PINEVILL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.9 | 1310.5 | 1350 | 97.1 | 797 | 20669 DARLN T 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 805 | 20678 KINGSTRE 115 20680 MANNIG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 807 | 20680 MANNIG T 115 20686 SUMTER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 811 | 20686 SUMTER 115 20688 GOLD TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 812 | 20686 SUMTER 115 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 813 | 20686 SUMTER 115 20700 SUMTER 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 815 | 20688 GOLD TAP 115 20694 KING HWY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97.1 | 817 | 20690 CRESTL T 115 20691 I-CRESNT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.6 | 1310.5 | 1350 | 97.1 | 819 | 20694 KING HWY 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.3 | 1310.5 | 1350 | 97.1 | 838 | 20716 CAMCTY02 115 20725 CAMDEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 839 | 20716 CAMCTY02 115 20729 STEEPLE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 843 | 20723 CAMD JCT 115 20726 CAMCTYDB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 845 | 20724 CAMCTY01 115 20729 STEEPLE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 846 | 20724 CAMCTY01 115 20738 I-KENDAL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 849 | 20726 CAMCTYDB 115 20738 I-KENDAL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.5 | 1310.5 | 1350 | 97.1 | 852 | 20732 ELGIN T 115 20734 WATRE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.4 | 1310.5 | 1350 | 97.1 | 865 | 44564 6EDGECOM 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 871 | 43068 6MARION 230 20631 MARION 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.7 | 1310.5 | 1350 | 97.1 | 872 | 43068 6MARION 230 20631 MARION 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.3 | 1310.5 | 1350 | 97.1 | 874 | 43005 6DARLING 230 20670 FLOR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 77 | 20022 BRUN 1 N 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 78 | 20022 BRUN 1 N 230 20621 BARNRD W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 82 | 20024 ROX 1-4F 230 20074 ROXB SO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 83 | 20024 ROX 1-4F 230 20075 BAHAMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 84 | 20024 ROX 1-4F 230 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 86 | 20030 LEE 1-3F 115 20240 FREMONT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 87 | 20030 LEE 1-3F 115 20250 E17-FREM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 100 | 20039 SUT 3 F 230 20554 9THORG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 101 | 20039 SUT 3 F 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 102 | 20041 CF 5-6 F 230 20052 CAPE F F 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 108 | 20044 ROB 1 F 115 20721 BETHNE T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 117 | 20047 WSP BUS 115 20447 E10-HOGS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 118 | 20047 WSP BUS 115 20574 BLADENBO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.3 | 1310.5 | 1350 | 97 | 131 | 20058 HOLLYSPG 230 20133 BELLS LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 141 | 20063 E12-RDMT 230 20074 ROXB SO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 178 | 20094 YANCY T 230 20095 YANCYVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 192 | 20111 E18-WK F 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 193 | 20111 E18-WK F 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 203 | 20122 REGNCYPK 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 204 | 20122 REGNCYPK 230 20210 APEXPOD4 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 212 | 20127 SPGHP SW 115 20609 SAMARIA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.4 | 1310.5 | 1350 | 97 | 218 | 20132 RAL SO 115 20158 GUILML T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 219 | 20133 BELLS LK 230 20140 PANTH BR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.3 | 1310.5 | 1350 | 97 | 220 | 20134 MONCURE 115 20158 GUILML T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 248 | 20158 GUILML T 115 20169 I-GLFDML 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 251 | 20162 MILBURNE 230 20163 MILBURNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 252 | 20162 MILBURNE 230 20163 MILBURNE 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 268 | 20175 SMITHF T 115 20177 SELMA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 269 | 20177 SELMA 115 20192 SELMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 283 | 20192 SELMA 230 20193 FOUR OAK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.2 | 1310.5 | 1350 | 97 | 285 | 20193 FOUR OAK 230 20194 BENSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 287 | 20195 I-BENPGI 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 288 | 20196 ERWIN 230 20197 DUNN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 294 | 20197 DUNN 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 296 | 20200 ZEBULON 230 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 298 | 20201 ZEBULON 115 20609 SAMARIA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 300 | 20202 ERWINSUB 115 20209 ERWIN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 303 | 20205 CLINTON 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 310 | 20206 MTO IN T 115 20277 MTOLVIND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 313 | 20209 ERWIN T 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 328 | 20225 PA-W-RE 115 20226 E13-DAVN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.4 | 1310.5 | 1350 | 97 | 342 | 20237 E9-W ONS 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 343 | 20237 E9-W ONS 230 20521 CATHRNLK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 344 | 20238 BLACK CK 115 20240 FREMONT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 345 | 20238 BLACK CK 115 20245 PA-W-RW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 346 | 20238 BLACK CK 115 20250 E17-FREM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 352 | 20244 PA-W-5 115 20245 PA-W-RW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 354 | 20247 GA PAC T 230 20249 I-GA PAC 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.4 | 1310.5 | 1350 | 97 | 371 | 20261 LEE 115 20264 E+GAS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 375 | 20263 E15-BNTV 115 20264 E+GAS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 376 | 20264 E+GAS T 115 20276 E17-GRAN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 382 | 20271 FRNDSP T 115 20272 E17-FRDS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 397 | 20287 GOLDS SW 115 20489 E13-ARBA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 410 | 20299 SC HWY64 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97 | 411 | 20299 SC HWY64 230 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 430 | 20315 I-SAPONA 69.0 20329 RAMSEUR 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 434 | 20318 E14-SPER 115 20353 I-UN&TIE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97 | 448 | 20331 ASHEB 115 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97 | 449 | 20331 ASHEB 115 20332 ASHEB 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.4 | 1310.5 | 1350 | 97 | 461 | 20346 RKH 115 20348 RKH 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 506 | 20379 M-FBMAIN 230 20380 M-FBKNOX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.2 | 1310.5 | 1350 | 97 | 508 | 20380 M-FBKNOX 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 518 | 20389 P2-FAY E 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 521 | 20392 FAY 115 20401 VANDER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 522 | 20392 FAY 115 20402 E15-VAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309 | 1310.5 | 1350 | 97 | 525 | 20393 SLOCUMB 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 529 | 20401 VANDER 115 20402 E15-VAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 539 | 20409 E15-WADE 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 541 | 20411 RAEFORD 115 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 542 | 20411 RAEFORD 115 20415 RAEFORD 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 558 | 20425 RED SP T 115 20431 SHANNON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 571 | 20443 ROWLAND 230 20444 ROWLND T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 583 | 20454 AURORA 230 20461 E16-SLVR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.3 | 1310.5 | 1350 | 97 | 603 | 20471 CCWDCG T 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 610 | 20477 IBRDB T 115 20478 I-I BRDB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 615 | 20483 SNOW HIL 115 20489 E13-ARBA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 616 | 20484 HAVELOCK 230 20485 HAVELOCK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 617 | 20484 HAVELOCK 230 20485 HAVELOCK 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 619 | 20484 HAVELOCK 230 20499 E2-MAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.2 | 1310.5 | 1350 | 97 | 651 | 20513 BURGAW C 115 20533 ID/OCC T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 664 | 20521 CATHRNLK 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.9 | 1310.5 | 1350 | 97 | 665 | 20524 JACKSONV 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 673 | 20533 ID/OCC T 115 20545 CASTLE H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 682 | 20543 E9-FOLKS 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 683 | 20543 E9-FOLKS 115 20547 E9-DAWCB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 684 | 20544 HOLLY RG 115 20545 CASTLE H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 685 | 20544 HOLLY RG 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 691 | 20550 CSTL HYN 230 20577 MURRAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 693 | 20552 E WILM 230 20554 9THORG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 694 | 20552 E WILM 230 20577 MURRAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 697 | 20558 I-DAKMON 115 20559 I-DAKFIB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 698 | 20559 I-DAKFIB 115 20627 DELCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 707 | 20568 DELCO 115 20576 KINGSBLF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 710 | 20568 DELCO 115 20627 DELCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 712 | 20570 CLARKTON 115 20571 ELIZAB T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 713 | 20570 CLARKTON 115 20576 KINGSBLF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 714 | 20571 ELIZAB T 115 20574 BLADENBO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.2 | 1310.5 | 1350 | 97 | 723 | 20581 WHITEVIL 115 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 726 | 20582 DELCO 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 731 | 20586 I-GAPCWH 115 20593 WHTV IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.6 | 1310.5 | 1350 | 97 | 739 | 20598 FAIR B T 115 20599 FAIR BLF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 741 | 20600 WHITEVIL 230 20603 E1-PROSP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1310.5 | 1350 | 97 | 751 | 20619 MASONBOR 230 20621 BARNRD W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 752 | 20619 MASONBOR 230 20626 WRIGHTVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 781 | 20657 GE TAP 115 20658 I-GE FL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 803 | 20677 KINGSTRE 230 20678 KINGSTRE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 804 | 20678 KINGSTRE 115 20679 ANDREWS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.1 | 1310.5 | 1350 | 97 | 806 | 20680 MANNIG T 115 20685 MANNING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 816 | 20689 I-SUMIND 115 20690 CRESTL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.7 | 1310.5 | 1350 | 97 | 818 | 20690 CRESTL T 115 20692 I-GOLD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.1 | 1310.5 | 1350 | 97 | 820 | 20695 SHAW AFB 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1310.5 | 1350 | 97 | 823 | 20699 SUMMER T 230 20701 SUMMERTN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.5 | 1310.5 | 1350 | 97 | 833 | 20711 ELLIOTT 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 834 | 20713 JEFFSN T 115 20714 JEFFERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.1 | 1310.5 | 1350 | 97 | 848 | 20725 CAMDEN 115 20731 I-DUP CA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 850 | 20731 I-DUP CA 115 20732 ELGIN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 851 | 20732 ELGIN T 115 20733 ELGIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 857 | 845 6E.DURHM 230 20063 E12-RDMT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1310.5 | 1350 | 97 | 859 | 845 6E.DURHM 230 20075 BAHAMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310.1 | 1310.5 | 1350 | 97 | 867 | 44554 3BTLEBRO 115 20223 ROCKY MT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 26 | FAYE-FBWOOD230_&_SLOC_TAP-SLOCUMB115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.6 | 1310.5 | 1350 | 96.9 | 51 | 20004 TIL 1-4H 115 20341 MT GILED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 56 | 20009 HARRIS1N 230 20058 HOLLYSPG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 71 | 20020 BRUN 2 N 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 75 | 20022 BRUN 1 N 230 20046 WSPN BUS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 76 | 20022 BRUN 1 N 230 20354 I-ROCKY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.7 | 1310.5 | 1350 | 96.9 | 96 | 20035 SUT 1-2F 115 20557 I-GE WLM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 99 | 20039 SUT 3 F 230 20520 I-KOSA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.6 | 1310.5 | 1350 | 96.9 | 106 | 20041 CF 5-6 F 230 20368 DEEPRV T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 122 | 20052 CAPE F F 115 20134 MONCURE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.7 | 1310.5 | 1350 | 96.9 | 125 | 20052 CAPE F F 115 20295 I-HONEYW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 143 | 20064 E6-WARTN 115 20103 WARRENTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.6 | 1310.5 | 1350 | 96.9 | 230 | 20142 ATLANTIC 115 20144 AVX TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 261 | 20166 ZEBULON 69.0 20167 E18-EMIT 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 262 | 20166 ZEBULON 69.0 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 286 | 20194 BENSON 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 292 | 20196 ERWIN 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.7 | 1310.5 | 1350 | 96.9 | 311 | 20207 NEWTON G 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 326 | 20224 PA-WRE-T 115 20225 PA-W-RE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 347 | 20238 BLACK CK 115 20293 W-3TOWNS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 353 | 20246 HEMLOCK 115 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 368 | 20258 CLINTN N 115 20259 E15-HALL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.1 | 1310.5 | 1350 | 96.9 | 380 | 20269 MTOLVSUB 115 20270 MT OLV W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 408 | 20296 CANDOR T 115 20306 CANDOR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.6 | 1310.5 | 1350 | 96.9 | 437 | 20320 E14-GRCH 115 20326 LIBERTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 440 | 20322 WDRMAN T 115 20394 E15-EUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.8 | 1310.5 | 1350 | 96.9 | 446 | 20327 E14-LIBR 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 447 | 20329 RAMSEUR 69.0 20330 I-RAMTEX 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.7 | 1310.5 | 1350 | 96.9 | 456 | 20341 MT GILED 115 20442 I-MG IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 460 | 20346 RKH 115 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 474 | 20351 I-CORDVA 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 476 | 20354 I-ROCKY 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.7 | 1310.5 | 1350 | 96.9 | 491 | 20367 LONGST T 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.8 | 1310.5 | 1350 | 96.9 | 493 | 20367 LONGST T 230 20386 CLIFFDAL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.1 | 1310.5 | 1350 | 96.9 | 524 | 20392 FAY 115 20407 E15-BEAR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.1 | 1310.5 | 1350 | 96.9 | 530 | 20401 VANDER 115 20502 I-VANDAK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 536 | 20407 E15-BEAR 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 537 | 20408 BEARD 115 20409 E15-WADE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.6 | 1310.5 | 1350 | 96.9 | 538 | 20408 BEARD 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 544 | 20411 RAEFORD 115 20425 RED SP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 549 | 20419 WAGRAMSW 115 20426 I-STV&GU 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 562 | 20430 RED SPRG 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.6 | 1310.5 | 1350 | 96.9 | 578 | 20451 PA-GRNVL 230 20474 DUP KIN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 588 | 20461 E16-SLVR 230 20463 NB WEST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.5 | 1310.5 | 1350 | 96.9 | 589 | 20463 NB WEST 230 20465 NEW BERN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 590 | 20464 BRIDGETN 115 20466 NEW BERN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.6 | 1310.5 | 1350 | 96.9 | 593 | 20465 NEW BERN 230 20471 CCWDCG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.3 | 1310.5 | 1350 | 96.9 | 607 | 20474 DUP KIN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 608 | 20475 WEYER T 115 20476 ICG-WYHS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 633 | 20499 E2-MAYVL 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 652 | 20514 I-OXYCHM 115 20533 ID/OCC T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 654 | 20515 WALLACE 230 20516 I-BASF 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1310.5 | 1350 | 96.9 | 657 | 20516 I-BASF 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 660 | 20519 M-TARAWA 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 662 | 20519 M-TARAWA 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.7 | 1310.5 | 1350 | 96.9 | 663 | 20520 I-KOSA 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 668 | 20524 JACKSONV 230 20540 GEI&SW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.1 | 1310.5 | 1350 | 96.9 | 680 | 20540 GEI&SW T 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308 | 1310.5 | 1350 | 96.9 | 681 | 20541 M-GEIGER 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.7 | 1310.5 | 1350 | 96.9 | 690 | 20550 CSTL HYN 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 696 | 20556 TOPSL T 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 717 | 20573 E4-POWEL 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 728 | 20585 WH IND T 115 20586 I-GAPCWH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.1 | 1310.5 | 1350 | 96.9 | 734 | 20588 CHADBN T 115 20589 CHADBORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.4 | 1310.5 | 1350 | 96.9 | 736 | 20590 TABOR T 115 20596 TABOR C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.6 | 1310.5 | 1350 | 96.9 | 745 | 20613 E1-SO WH 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 810 | 20686 SUMTER 115 20687 EASTOV T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 814 | 20687 EASTOV T 115 20689 I-SUMIND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.5 | 1310.5 | 1350 | 96.9 | 830 | 20709 HARTSN T 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.5 | 1310.5 | 1350 | 96.9 | 831 | 20709 HARTSN T 115 20717 I-SONOCO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1310.5 | 1350 | 96.9 | 835 | 20713 JEFFSN T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1310.5 | 1350 | 96.9 | 836 | 20713 JEFFSN T 115 20720 PAGELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.5 | 1310.5 | 1350 | 96.9 | 841 | 20721 BETHNE T 115 20722 BETHUNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.8 | 1310.5 | 1350 | 96.8 | 49 | 20001 BLEWETT 115 20345 RKH W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.7 | 1310.5 | 1350 | 96.8 | 140 | 20062 E4-TARHE 230 20573 E4-POWEL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.4 | 1310.5 | 1350 | 96.8 | 142 | 20064 E6-WARTN 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.2 | 1310.5 | 1350 | 96.8 | 158 | 20079 OXF S T 230 20080 OXFORD S 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.7 | 1310.5 | 1350 | 96.8 | 183 | 20100 HEND N T 115 20101 HEND NO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.6 | 1310.5 | 1350 | 96.8 | 186 | 20106 WAKEFORE 115 20107 E18-WEMC 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.6 | 1310.5 | 1350 | 96.8 | 187 | 20106 WAKEFORE 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.4 | 1310.5 | 1350 | 96.8 | 264 | 20171 AMBERLY 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.3 | 1310.5 | 1350 | 96.8 | 295 | 20198 BAILEY 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.7 | 1310.5 | 1350 | 96.8 | 336 | 20231 GC/LEE T 115 20233 GOLDSB C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.7 | 1310.5 | 1350 | 96.8 | 337 | 20231 GC/LEE T 115 20239 GOLD C T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.5 | 1310.5 | 1350 | 96.8 | 369 | 20259 E15-HALL 115 20260 ROSEBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.3 | 1310.5 | 1350 | 96.8 | 370 | 20260 ROSEBORO 115 20265 E15-STED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.8 | 1310.5 | 1350 | 96.8 | 426 | 20313 ASHEBW T 115 20317 ASHEB W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307 | 1310.5 | 1350 | 96.8 | 433 | 20318 E14-SPER 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.6 | 1310.5 | 1350 | 96.8 | 511 | 20386 CLIFFDAL 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.2 | 1310.5 | 1350 | 96.8 | 514 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.2 | 1310.5 | 1350 | 96.8 | 515 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.2 | 1310.5 | 1350 | 96.8 | 570 | 20439 LUMBERTN 115 20606 CG-LUMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.4 | 1310.5 | 1350 | 96.8 | 587 | 20461 E16-SLVR 230 20462 BAYBORO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.9 | 1310.5 | 1350 | 96.8 | 620 | 20485 HAVELOCK 115 20486 M-CH PT1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.3 | 1310.5 | 1350 | 96.8 | 628 | 20493 ATL BCH 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.1 | 1310.5 | 1350 | 96.8 | 637 | 20501 SCOTT HL 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.5 | 1310.5 | 1350 | 96.8 | 688 | 20549 TOPSAIL 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.6 | 1310.5 | 1350 | 96.8 | 716 | 20572 ELIZABTN 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.5 | 1310.5 | 1350 | 96.8 | 744 | 20611 SOUTH+PA 230 20612 I-ADM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.6 | 1310.5 | 1350 | 96.8 | 792 | 20664 DILLN MP 230 20667 DILN NTH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.2 | 1310.5 | 1350 | 96.8 | 840 | 20718 CHESTRFD 115 20719 CHERAW E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305 | 1310.5 | 1350 | 96.7 | 25 | FAY-FAYE230_&_FAY-WSP230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.9 | 1310.5 | 1350 | 96.7 | 112 | 20046 WSPN BUS 230 20446 WSPN SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.6 | 1310.5 | 1350 | 96.7 | 228 | 20141 WF T NC2 115 20607 PA-WF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.5 | 1310.5 | 1350 | 96.7 | 243 | 20154 ROLESVIL 230 20156 ROL/SQ T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.7 | 1310.5 | 1350 | 96.7 | 377 | 20265 E15-STED 115 20401 VANDER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305 | 1310.5 | 1350 | 96.7 | 421 | 20309 BISCOE W 230 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.1 | 1310.5 | 1350 | 96.7 | 424 | 20312 ASHEB E 115 20320 E14-GRCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.3 | 1310.5 | 1350 | 96.7 | 451 | 20334 BYNUM 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.5 | 1310.5 | 1350 | 96.7 | 458 | 20344 WADESBOR 230 20359 BOWMNSCH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.7 | 1310.5 | 1350 | 96.7 | 486 | 20362 WEST END 115 20363 PINEHRST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.9 | 1310.5 | 1350 | 96.7 | 494 | 20368 DEEPRV T 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.4 | 1310.5 | 1350 | 96.7 | 495 | 20368 DEEPRV T 230 20376 DEEP RIV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.1 | 1310.5 | 1350 | 96.7 | 509 | 20381 RAEF SO 115 20413 RAEF SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.7 | 1310.5 | 1350 | 96.7 | 547 | 20416 MAXAPT T 115 20420 MAXT APT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.7 | 1310.5 | 1350 | 96.7 | 567 | 20436 PEMBROKE 115 20441 E10-PEMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.4 | 1310.5 | 1350 | 96.7 | 649 | 20512 WALL SUB 115 20548 E4-WALL 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.8 | 1310.5 | 1350 | 96.7 | 678 | 20538 E9-PINYG 115 20539 E9-HARMN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.2 | 1310.5 | 1350 | 96.7 | 679 | 20540 GEI&SW T 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.4 | 1310.5 | 1350 | 96.7 | 775 | 20647 MAR BYPS 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.6 | 1310.5 | 1350 | 96.7 | 783 | 20659 FLORENCE 115 20661 MT HOPE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.8 | 1310.5 | 1350 | 96.7 | 787 | 20660 DARLINGT 115 20669 DARLN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.2 | 1310.5 | 1350 | 96.7 | 837 | 20715 HARTSVIL 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.4 | 1310.5 | 1350 | 96.7 | 847 | 20725 CAMDEN 115 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.6 | 1310.5 | 1350 | 96.6 | 48 | 20001 BLEWETT 115 20004 TIL 1-4H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1310.5 | 1350 | 96.6 | 116 | 20047 WSP BUS 115 20440 E10-WLUM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.5 | 1310.5 | 1350 | 96.6 | 136 | 20061 APEX US1 230 20065 APEX US1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.2 | 1310.5 | 1350 | 96.6 | 139 | 20062 E4-TARHE 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.5 | 1310.5 | 1350 | 96.6 | 144 | 20065 APEX US1 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.1 | 1310.5 | 1350 | 96.6 | 200 | 20120 CARY TAP 230 20121 CARY SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1310.5 | 1350 | 96.6 | 213 | 20129 OAKDAL T 230 20135 OAKDALE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.5 | 1310.5 | 1350 | 96.6 | 267 | 20175 SMITHF T 115 20176 PA-SMFLD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304 | 1310.5 | 1350 | 96.6 | 297 | 20200 ZEBULON 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.4 | 1310.5 | 1350 | 96.6 | 301 | 20203 BAILEY T 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.7 | 1310.5 | 1350 | 96.6 | 374 | 20262 E17-MT O 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.6 | 1310.5 | 1350 | 96.6 | 492 | 20367 LONGST T 230 20384 M-FBLONG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.3 | 1310.5 | 1350 | 96.6 | 528 | 20400 E15-MAN 115 20460 E3-MANCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.2 | 1310.5 | 1350 | 96.6 | 559 | 20425 RED SP T 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.6 | 1310.5 | 1350 | 96.6 | 573 | 20446 WSPN SUB 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.3 | 1310.5 | 1350 | 96.6 | 576 | 20449 DILLON 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.4 | 1310.5 | 1350 | 96.6 | 581 | 20454 AURORA 230 20455 I-PCS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.2 | 1310.5 | 1350 | 96.6 | 644 | 20508 PA-KINST 115 20529 KINSTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.5 | 1310.5 | 1350 | 96.6 | 659 | 20518 WARSAW T 230 20522 WARSAW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1310.5 | 1350 | 96.6 | 669 | 20525 M-LEJN#1 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1310.5 | 1350 | 96.6 | 727 | 20584 GARLAND 230 20591 E4-YORK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.8 | 1310.5 | 1350 | 96.6 | 793 | 20664 DILLN MP 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.9 | 1310.5 | 1350 | 96.6 | 853 | 844 6ENO 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.9 | 1310.5 | 1350 | 96.6 | 854 | 844 6ENO 230 20024 ROX 1-4F 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.9 | 1310.5 | 1350 | 96.6 | 880 | 43059 6BENNETT 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.3 | 1310.5 | 1350 | 96.6 | 881 | 43010 6LUGOFF 230 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303 | 1310.5 | 1350 | 96.5 | 245 | 20156 ROL/SQ T 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.1 | 1310.5 | 1350 | 96.5 | 246 | 20156 ROL/SQ T 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1310.5 | 1350 | 96.5 | 275 | 3Wnd: OPEN B$0024 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1310.5 | 1350 | 96.5 | 276 | 3Wnd: OPEN B$0045 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.5 | 1310.5 | 1350 | 96.5 | 365 | 20255 CLINTON 115 20256 CL FEREL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.6 | 1310.5 | 1350 | 96.5 | 401 | 20290 I-OLVRRB 115 20311 ASHEB S 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1310.5 | 1350 | 96.5 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.6 | 1310.5 | 1350 | 96.5 | 443 | 20323 RAMS TAP 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.2 | 1310.5 | 1350 | 96.5 | 467 | 20348 RKH 230 20355 HAMLET 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.8 | 1310.5 | 1350 | 96.5 | 477 | 20355 HAMLET 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303 | 1310.5 | 1350 | 96.5 | 498 | 20370 SO PINES 115 20371 CARTHAGE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1310.5 | 1350 | 96.5 | 510 | 20381 RAEF SO 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.2 | 1310.5 | 1350 | 96.5 | 572 | 20444 ROWLND T 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.3 | 1310.5 | 1350 | 96.5 | 661 | 20519 M-TARAWA 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.7 | 1310.5 | 1350 | 96.5 | 671 | 20532 E4-KELLY 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.4 | 1310.5 | 1350 | 96.5 | 794 | 20665 I-NUCOR 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1310.5 | 1350 | 96.5 | 829 | 20708 C REIDPK 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.1 | 1310.5 | 1350 | 96.4 | 205 | 20122 REGNCYPK 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1310.5 | 1350 | 96.4 | 280 | 20190 WAKE 230 20191 WENDELL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.6 | 1310.5 | 1350 | 96.4 | 282 | 20191 WENDELL 230 20200 ZEBULON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1310.5 | 1350 | 96.4 | 293 | 20196 ERWIN 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1310.5 | 1350 | 96.4 | 334 | 20230 WILSON 115 20235 PA-W-11 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301 | 1310.5 | 1350 | 96.4 | 463 | 20346 RKH 115 20456 E11-RHAM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.5 | 1310.5 | 1350 | 96.4 | 481 | 20357 SH US#1 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.4 | 1310.5 | 1350 | 96.4 | 500 | 20373 S GARD T 230 20374 SANF GAR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.9 | 1310.5 | 1350 | 96.4 | 513 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302 | 1310.5 | 1350 | 96.4 | 556 | 20424 LAURINBG 230 20444 ROWLND T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301 | 1310.5 | 1350 | 96.4 | 632 | 20498 MR WILDW 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.8 | 1310.5 | 1350 | 96.4 | 672 | 20532 E4-KELLY 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1310.5 | 1350 | 96.4 | 677 | 20537 E9-JAX E 115 20538 E9-PINYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.7 | 1310.5 | 1350 | 96.4 | 695 | 20553 9TH&ORNG 230 20554 9THORG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.1 | 1310.5 | 1350 | 96.4 | 705 | 20568 DELCO 115 20569 ICG-IPPR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1310.5 | 1350 | 96.4 | 722 | 20580 WHTV TAP 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.7 | 1310.5 | 1350 | 96.4 | 748 | 20616 BARNARD 115 20618 SUNSET P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.7 | 1310.5 | 1350 | 96.4 | 750 | 20617 CARL BCH 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.5 | 1310.5 | 1350 | 96.3 | 459 | 20345 RKH W 115 20346 RKH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.5 | 1310.5 | 1350 | 96.3 | 489 | 20364 ABERDEEN 115 20365 CENTER P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.5 | 1310.5 | 1350 | 96.3 | 499 | 20371 CARTHAGE 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.8 | 1310.5 | 1350 | 96.3 | 512 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.5 | 1310.5 | 1350 | 96.3 | 526 | 20395 SPRING L 115 20400 E15-MAN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.5 | 1310.5 | 1350 | 96.3 | 566 | 20435 MAXTON 115 20436 PEMBROKE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300 | 1310.5 | 1350 | 96.3 | 601 | 20469 PA-GLENB 115 20470 PA-NBCTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.5 | 1310.5 | 1350 | 96.3 | 648 | 20512 WALL SUB 115 20517 WALLACE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.3 | 1310.5 | 1350 | 96.3 | 743 | 20601 CG-SOPRT 230 20611 SOUTH+PA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.7 | 1310.5 | 1350 | 96.2 | 104 | 20041 CF 5-6 F 230 20297 JONESBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.2 | 1310.5 | 1350 | 96.2 | 480 | 20357 SH US#1 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.3 | 1310.5 | 1350 | 96.2 | 519 | 20390 CUMBERLD 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.6 | 1310.5 | 1350 | 96.2 | 821 | 20698 REIDPK T 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.2 | 1310.5 | 1350 | 96.1 | 29 | RKH-WADESBORO230_&_BLEW-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.7 | 1310.5 | 1350 | 96.1 | 478 | 20356 ROCKFISH 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.8 | 1310.5 | 1350 | 96.1 | 479 | 20356 ROCKFISH 230 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.7 | 1310.5 | 1350 | 96.1 | 490 | 20366 WEST END 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297 | 1310.5 | 1350 | 96.1 | 565 | 20434 BUTLER 115 20435 MAXTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.9 | 1310.5 | 1350 | 96 | 441 | 20322 WDRMAN T 115 20395 SPRING L 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1310.5 | 1350 | 96 | 540 | 20411 RAEFORD 115 20414 RAEF TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1310.5 | 1350 | 96 | 545 | 20414 RAEF TAP 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1310.5 | 1350 | 96 | 563 | 20433 I-PLKLOF 115 20434 BUTLER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.9 | 1310.5 | 1350 | 96 | 675 | 20536 JAX CITY 115 20537 E9-JAX E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.8 | 1310.5 | 1350 | 96 | 749 | 20616 BARNARD 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.2 | 1310.5 | 1350 | 95.9 | 24 | CUMB-FAY230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.7 | 1310.5 | 1350 | 95.9 | 127 | 3Wnd: OPEN B$0014 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.2 | 1310.5 | 1350 | 95.9 | 137 | 20061 APEX US1 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1310.5 | 1350 | 95.9 | 457 | 20344 WADESBOR 230 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1310.5 | 1350 | 95.8 | 429 | 20314 E3-CTRCH 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.1 | 1310.5 | 1350 | 95.8 | 432 | 20316 E10-ARAB 115 20418 E10-ROCK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1310.5 | 1350 | 95.8 | 442 | 20322 WDRMAN T 115 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292.9 | 1310.5 | 1350 | 95.8 | 502 | 3Wnd: OPEN B$0022 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1310.5 | 1350 | 95.8 | 527 | 20398 M-FBWOOD 230 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1310.5 | 1350 | 95.8 | 598 | 20466 NEW BERN 115 20469 PA-GLENB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292 | 1310.5 | 1350 | 95.7 | 138 | 20061 APEX US1 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292.6 | 1310.5 | 1350 | 95.7 | 428 | 20314 E3-CTRCH 230 20361 WEST END 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292 | 1310.5 | 1350 | 95.7 | 431 | 20316 E10-ARAB 115 20411 RAEFORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.5 | 1310.5 | 1350 | 95.7 | 487 | 20362 WEST END 115 20364 ABERDEEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292.6 | 1310.5 | 1350 | 95.7 | 503 | 3Wnd: OPEN B$0046 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1310.5 | 1350 | 95.6 | 58 | 20009 HARRIS1N 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1310.5 | 1350 | 95.6 | 470 | 20348 RKH 230 20378 RICHMOND 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.9 | 1310.5 | 1350 | 95.5 | 30 | RKH-WADESBORO230_&_RKH-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1310.5 | 1350 | 95.5 | 469 | 20348 RKH 230 20378 RICHMOND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.5 | 1310.5 | 1350 | 95.5 | 642 | 20507 WOMMACK 115 20508 PA-KINST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.7 | 1310.5 | 1350 | 95.3 | 746 | 20615 BARNARD 230 20616 BARNARD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.9 | 1310.5 | 1350 | 95.2 | 27 | FAY-ROCKFISH230_&_FAY-HAMLET230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.9 | 1310.5 | 1350 | 95.1 | 28 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280.6 | 1310.5 | 1350 | 94.9 | 504 | 20378 RICHMOND 230 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280.4 | 1310.5 | 1350 | 94.8 | 420 | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278 | 1310.5 | 1350 | 94.7 | 464 | 20347 ABRDN RD 230 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1273.9 | 1310.5 | 1350 | 94.4 | 483 | 20360 ELLERBE 230 20361 WEST END 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1272 | 1310.5 | 1350 | 94.2 | 468 | 20348 RKH 230 20360 ELLERBE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.6 | 1310.5 | 1350 | 94.1 | 555 | 20422 LBG CITY 230 20424 LAURINBG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1264.7 | 1310.5 | 1350 | 93.7 | 554 | 20422 LBG CITY 230 20423 LAUREL H 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1261.1 | 1310.5 | 1350 | 93.4 | 505 | 20378 RICHMOND 230 20423 LAUREL H 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.9 | 1310.5 | 1350 | 92.2 | 520 | 3Wnd: OPEN B$0005 1
20387 P1-FAY 0 230 20392 FAY 115 1 | TR | 191.5 | 113.4 | 200 | 95.7 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20387 P1-FAY 0 230 20392 FAY 115 2 | TR | 191.4 | 113.1 | 200 | 95.7 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20421 LAURINBG 115 20424 LAURINBG 230 1 | TR | 194.3 | 107.3 | 200 | 97.1 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20421 LAURINBG 115 20424 LAURINBG 230 2 | TR | 194 | 106.6 | 200 | 97 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20552 E WILM 230 20554 9THORG T 230 1 | LN | 543.5 | 249.4 | 590 | 92.1 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143.1 | 143 | 150 | 95.4 | 97 | 20035 SUT 1-2F 115 20558 I-DAKMON 115 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143.1 | 143 | 150 | 95.4 | 98 | 20035 SUT 1-2F 115 20560 IND OOB5 115 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.4 | 274 | 20183 WAKE 500 20391 CUMBERLD 500 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.4 | 520 | 3Wnd: OPEN B$0005 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.4 | 724 | 20581 WHITEVIL 115 20624 WHTVL12T 115 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.4 | 725 | 20582 DELCO 230 20604 E1-STHPT 230 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.4 | 730 | 20585 WH IND T 115 20624 WHTVL12T 115 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 143 | 143 | 150 | 95.3 |  | ** Base Case **
20654 DILLON T 115 20632 MARION 115 1 | LN | 92.5 | 68.4 | 97 | 95.3 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20654 DILLON T 115 20632 MARION 115 1 | LN | 87.9 | 68.4 | 97 | 90.6 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20985 ANSON 230 20350 PH SH 1B 230 1 | LN | 368.6 | 214.3 | 398 | 92.6 | 869 | 337 8NEWPORT 500 20377 RICHMOND 500 1
B$0024 1.00 20183 WAKE 500 1 | TR | 941.3 | 607.5 | 1000 | 94.1 | 276 | 3Wnd: OPEN B$0045 2
B$0024 1.00 20190 WAKE 230 1 | TR | 919.1 | 598.6 | 1000 | 91.9 | 276 | 3Wnd: OPEN B$0045 2
B$0045 1.00 20183 WAKE 500 2 | TR | 941 | 607.1 | 1000 | 94.1 | 275 | 3Wnd: OPEN B$0024 1
B$0045 1.00 20190 WAKE 230 2 | TR | 918.8 | 598.2 | 1000 | 91.9 | 275 | 3Wnd: OPEN B$0024 1
Note on A15: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C15: PTI: Contingency MVA for Tran and Amp for Lines
Note on D15: PTI: Base Case Flow
Note on E15: PTI: Branch Rating
Note on F15: PTI: Loading in %
Note on G15: PTI: Contingency index
Note on H15: PTI: Contingency Description

## 3600 MW HR DN BRANCH
Branch Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- MON, APR 17 2006 14:04
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 SER REL6/05, 400MW INTCH MOD
Case.File J:\NC Stakeholders\2011S Study\Study Cases\TRMcases\400MW_Intch_Mod\duk11s_PEC_FinalNP_400MW_IntchMod_HarDn.sav
Subsys.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.sub
Monit.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.mon
Contin.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-Eastern System.EXC
************** Report on violations ********************
Branches with MVA flow more than 93.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Ncon | Contingency
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | LN | 265.2 | 162.8 | 269 | 98.6 | 464 | 20347 ABRDN RD 230 20348 RKH 230 1
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | LN | 257.8 | 162.8 | 269 | 95.8 | 420 | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20039 SUT 3 F 230 20554 9THORG T 230 1 | LN | 627.8 | 231.7 | 590 | 106.4 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20155 CHSTNT H 115 20163 MILBURNE 115 1 | LN | 149 | 20.1 | 158 | 94.3 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20185 FALLS 115 20182 FALLS 230 1 | TR | 314.6 | 209.9 | 300 | 104.9 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | TR | 309.6 | 209.9 | 300 | 103.2 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20182 FALLS 230 1 | TR | 279.1 | 209.9 | 300 | 93 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20290 I-OLVRRB 115 20304 E14-ULAH 115 1 | LN | 130.1 | 58.9 | 138 | 94.3 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20304 E14-ULAH 115 20303 SEAGROVE 115 1 | LN | 151.9 | 79.8 | 148 | 102.6 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1452.2 | 1292.3 | 1350 | 107.6 | 33 | PHSH1-ANSON230_&_PHSH2-ANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1354.2 | 1292.3 | 1350 | 100.3 | 61 | 20015 MAYO 1F 500 20054 DURHAM 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1348.1 | 1292.3 | 1350 | 99.9 | 864 | 44902 8CARSON 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1340.3 | 1292.3 | 1350 | 99.3 | 32 | OAKBORO-ANSON230_&_OAKBORO-IANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1338.9 | 1292.3 | 1350 | 99.2 | 34 | ANSON-OAKBORO230_&_ANSON-BOWMANT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1338.9 | 1292.3 | 1350 | 99.2 | 31 | BOWMANT-IANSON230_&_ANSON-OAKBORO230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.2 | 1292.3 | 1350 | 98.2 | 465 | 20348 RKH 230 20349 PH SH 2W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.3 | 1292.3 | 1350 | 98.2 | 466 | 20348 RKH 230 20350 PH SH 1B 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.2 | 1292.3 | 1350 | 98.2 | 472 | 20349 PH SH 2W 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.3 | 1292.3 | 1350 | 98.2 | 473 | 20350 PH SH 1B 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1325.3 | 1292.3 | 1350 | 98.2 | 35 | ROB-NUCOR230_&_ROB-REIDPK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324 | 1292.3 | 1350 | 98.1 | 863 | 845 6E.DURHM 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1324.9 | 1292.3 | 1350 | 98.1 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1322.6 | 1292.3 | 1350 | 98 | 69 | 20018 ROB 2 N 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1321.7 | 1292.3 | 1350 | 97.9 | 5 | ROX-FALLS230_&_FALLS23-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318.4 | 1292.3 | 1350 | 97.7 | 860 | 845 6E.DURHM 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1318.5 | 1292.3 | 1350 | 97.7 | 6 | ROX-FALLS230_&_PER-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1317 | 1292.3 | 1350 | 97.6 | 126 | 20054 DURHAM 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1316.9 | 1292.3 | 1350 | 97.6 | 129 | 20057 DARL CO 230 20668 I-TALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.1 | 1292.3 | 1350 | 97.4 | 153 | 20073 BLUE RDG 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1315.4 | 1292.3 | 1350 | 97.4 | 795 | 20668 I-TALLY 230 20705 SOCTY HL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.9 | 1292.3 | 1350 | 97.4 | 879 | 42002 6WATEREE 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1314.2 | 1292.3 | 1350 | 97.3 | 827 | 20705 SOCTY HL 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.8 | 1292.3 | 1350 | 97.3 | 17 | FALLS-MILB230_&_FALLS23-HOMESTED230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1313.2 | 1292.3 | 1350 | 97.3 | 2 | ROX-EDANVLN230_&_YANCYVLT-EDANVL230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.6 | 1292.3 | 1350 | 97.2 | 50 | 20004 TIL 1-4H 115 20302 E14-TROY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.1 | 1292.3 | 1350 | 97.2 | 154 | 20073 BLUE RDG 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.6 | 1292.3 | 1350 | 97.2 | 415 | 20302 E14-TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.1 | 1292.3 | 1350 | 97.2 | 471 | 20348 RKH 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.7 | 1292.3 | 1350 | 97.2 | 802 | 20676 KINGST N 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1312.5 | 1292.3 | 1350 | 97.2 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.4 | 1292.3 | 1350 | 97.1 | 876 | 43008 6KNGSTRE 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1311.1 | 1292.3 | 1350 | 97.1 | 1 | ROX-EDANVL230_&_CONCORD-YANCYVLT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1310 | 1292.3 | 1350 | 97 | 414 | 20301 TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1292.3 | 1350 | 97 | 801 | 20675 LAKE CTY 230 20676 KINGST N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.9 | 1292.3 | 1350 | 97 | 828 | 20706 BENETSVL 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1309.8 | 1292.3 | 1350 | 97 | 15 | FALLS-MILB230_&_HOMESTED-PINELK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1292.3 | 1350 | 96.9 | 413 | 20301 TROY 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1292.3 | 1350 | 96.9 | 557 | 20424 LAURINBG 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.8 | 1292.3 | 1350 | 96.9 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1308.2 | 1292.3 | 1350 | 96.9 | 800 | 20674 OLANTA 230 20675 LAKE CTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.9 | 1292.3 | 1350 | 96.9 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.1 | 1292.3 | 1350 | 96.8 | 145 | 20066 FALLS23 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.9 | 1292.3 | 1350 | 96.8 | 150 | 20070 PERSON 230 20079 OXF S T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.3 | 1292.3 | 1350 | 96.8 | 733 | 20587 E1-CHADP 230 20631 MARION 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.3 | 1292.3 | 1350 | 96.8 | 798 | 20671 SARDIS 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307.3 | 1292.3 | 1350 | 96.8 | 799 | 20671 SARDIS 230 20674 OLANTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.7 | 1292.3 | 1350 | 96.8 | 16 | FALLS-MILB230_&_PINELK-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1307 | 1292.3 | 1350 | 96.8 | 39 | MARION-MARION(SCPSA)230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1306.2 | 1292.3 | 1350 | 96.8 | 21 | TILLERY-BADIN1&2_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.1 | 1292.3 | 1350 | 96.7 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.9 | 1292.3 | 1350 | 96.7 | 146 | 20066 FALLS23 230 20157 HOMESTED 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.3 | 1292.3 | 1350 | 96.7 | 159 | 20079 OXF S T 230 20085 OXFORD N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.9 | 1292.3 | 1350 | 96.7 | 778 | 20653 CASHUA 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.1 | 1292.3 | 1350 | 96.7 | 20 | MILB-FALLS230_&_MILB-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1305.2 | 1292.3 | 1350 | 96.7 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1292.3 | 1350 | 96.6 | 85 | 20024 ROX 1-4F 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.3 | 1292.3 | 1350 | 96.6 | 151 | 20070 PERSON 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.4 | 1292.3 | 1350 | 96.6 | 357 | 20248 I-ANSONV 230 20358 BOWMAN T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.5 | 1292.3 | 1350 | 96.6 | 732 | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1304.1 | 1292.3 | 1350 | 96.6 | 868 | 542 6OAKBORO 230 20248 I-ANSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.7 | 1292.3 | 1350 | 96.6 | 882 | 542 6OAKBORO 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.1 | 1292.3 | 1350 | 96.5 | 62 | 20015 MAYO 1F 500 20071 PERSON 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.6 | 1292.3 | 1350 | 96.5 | 107 | 20044 ROB 1 F 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1292.3 | 1350 | 96.5 | 165 | 20085 OXFORD N 230 20087 HEND E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.3 | 1292.3 | 1350 | 96.5 | 247 | 20157 HOMESTED 230 20160 PINE LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.4 | 1292.3 | 1350 | 96.5 | 482 | 20358 BOWMAN T 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.1 | 1292.3 | 1350 | 96.5 | 777 | 20653 CASHUA 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.3 | 1292.3 | 1350 | 96.5 | 788 | 20662 FLORENCE 230 20663 LATTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.4 | 1292.3 | 1350 | 96.5 | 824 | 20700 SUMTER 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.1 | 1292.3 | 1350 | 96.5 | 152 | 3Wnd: OPEN B$0011 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1302.4 | 1292.3 | 1350 | 96.5 | 856 | 43014 6S BETH 230 20057 DARL CO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.3 | 1292.3 | 1350 | 96.5 | 36 | SUMT-WDGFLD230_&_GOLDT-KNGHWY115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1303.3 | 1292.3 | 1350 | 96.5 | 37 | SUMT-WDGFLD230_&_SUMT-GOLDT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.8 | 1292.3 | 1350 | 96.4 | 168 | 20087 HEND E 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.9 | 1292.3 | 1350 | 96.4 | 175 | 20091 BRIERCK 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.2 | 1292.3 | 1350 | 96.4 | 176 | 20091 BRIERCK 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.3 | 1292.3 | 1350 | 96.4 | 866 | 44591 6NASH 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.8 | 1292.3 | 1350 | 96.4 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1301.1 | 1292.3 | 1350 | 96.4 | 46 | RKYMT-NASH230_&_RKYMT-EDGCMB230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.6 | 1292.3 | 1350 | 96.3 | 205 | 20122 REGNCYPK 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.8 | 1292.3 | 1350 | 96.3 | 206 | 20124 METHOD 230 20129 OAKDAL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.5 | 1292.3 | 1350 | 96.3 | 211 | 20126 MORRISVI 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.6 | 1292.3 | 1350 | 96.3 | 249 | 20160 PINE LK 230 20161 FOXCROFT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.7 | 1292.3 | 1350 | 96.3 | 808 | 20684 ALICE DR 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.5 | 1292.3 | 1350 | 96.3 | 825 | 20700 SUMTER 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.7 | 1292.3 | 1350 | 96.3 | 832 | 20710 HARTS T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.7 | 1292.3 | 1350 | 96.3 | 47 | GRNVL-CHOCWNTY230_&_GRNVL-EVERETT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1300.4 | 1292.3 | 1350 | 96.3 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.6 | 1292.3 | 1350 | 96.2 | 70 | 20018 ROB 2 N 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.1 | 1292.3 | 1350 | 96.2 | 111 | 20046 WSPN BUS 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.9 | 1292.3 | 1350 | 96.2 | 210 | 20126 MORRISVI 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.2 | 1292.3 | 1350 | 96.2 | 250 | 20161 FOXCROFT 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.6 | 1292.3 | 1350 | 96.2 | 602 | 20471 CCWDCG T 230 20472 CG-CC WD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.1 | 1292.3 | 1350 | 96.2 | 742 | 20601 CG-SOPRT 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.9 | 1292.3 | 1350 | 96.2 | 809 | 20684 ALICE DR 230 20703 SUMTER N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298.3 | 1292.3 | 1350 | 96.2 | 870 | 44574 6EVERETS 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.3 | 1292.3 | 1350 | 96.2 | 19 | MILB-WHITEOAK230_&_MILB-AUBURN230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.8 | 1292.3 | 1350 | 96.1 | 149 | 20068 RXBOWMAN 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.7 | 1292.3 | 1350 | 96.1 | 196 | 20117 DURHAM 230 20118 RDU AIRP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297 | 1292.3 | 1350 | 96.1 | 197 | 20118 RDU AIRP 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297 | 1292.3 | 1350 | 96.1 | 201 | 20120 CARY TAP 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1298 | 1292.3 | 1350 | 96.1 | 214 | 20129 OAKDAL T 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.5 | 1292.3 | 1350 | 96.1 | 254 | 20162 MILBURNE 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.4 | 1292.3 | 1350 | 96.1 | 719 | 20578 CG-ELIZ 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1297.2 | 1292.3 | 1350 | 96.1 | 878 | 42001 6SANTEE 230 20699 SUMMER T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.7 | 1292.3 | 1350 | 96.1 | 861 | 52578 05EDANV2 230 20094 YANCY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.5 | 1292.3 | 1350 | 96 | 52 | 20004 TIL 1-4H 115 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.3 | 1292.3 | 1350 | 96 | 147 | 20067 MAYOSUSW 230 20068 RXBOWMAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.3 | 1292.3 | 1350 | 96 | 148 | 20067 MAYOSUSW 230 20088 HENDERSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.5 | 1292.3 | 1350 | 96 | 157 | 20078 WD VALLY 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296 | 1292.3 | 1350 | 96 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.8 | 1292.3 | 1350 | 96 | 179 | 20094 YANCY T 230 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1292.3 | 1350 | 96 | 198 | 20119 PRISON F 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.9 | 1292.3 | 1350 | 96 | 199 | 20119 PRISON F 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.6 | 1292.3 | 1350 | 96 | 202 | 20120 CARY TAP 230 20173 TRI FRST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.2 | 1292.3 | 1350 | 96 | 203 | 20122 REGNCYPK 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.5 | 1292.3 | 1350 | 96 | 239 | 20151 WHITEOAK 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.5 | 1292.3 | 1350 | 96 | 278 | 20188 PA-SELMA 230 20192 SELMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 279 | 20188 PA-SELMA 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296 | 1292.3 | 1350 | 96 | 281 | 20190 WAKE 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.6 | 1292.3 | 1350 | 96 | 325 | 20222 ROCKY MT 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 386 | 20274 EKRN+CGK 115 20310 E17-SARE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1292.3 | 1350 | 96 | 422 | 20310 E17-SARE 115 20605 CG-KORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296 | 1292.3 | 1350 | 96 | 756 | 20630 MULLINS 115 20632 MARION 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 762 | 20632 MARION 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 774 | 20645 HEMINGWA 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.6 | 1292.3 | 1350 | 96 | 822 | 20699 SUMMER T 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 826 | 20703 SUMTER N 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.5 | 1292.3 | 1350 | 96 | 883 | 2511 BADIN 100 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.7 | 1292.3 | 1350 | 96 | 873 | 43007 3HEMING1 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.9 | 1292.3 | 1350 | 96 | 858 | 44697 6HALIFAX 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1296.4 | 1292.3 | 1350 | 96 | 855 | 52577 05EDANV1 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.3 | 1292.3 | 1350 | 95.9 | 53 | 20004 TIL 1-4H 115 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.9 | 1292.3 | 1350 | 95.9 | 115 | 20047 WSP BUS 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 120 | 20050 PA-GRN W 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.6 | 1292.3 | 1350 | 95.9 | 132 | 20059 E18-KITT 115 20089 HENDERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 133 | 20059 E18-KITT 115 20096 YOUNGSVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.7 | 1292.3 | 1350 | 95.9 | 155 | 20077 SIX FORK 230 20078 WD VALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 163 | 20084 I-NOVO 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 166 | 20086 E12-HYCO 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 167 | 20086 E12-HYCO 115 20093 CONCORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 177 | 20093 CONCORD 115 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.6 | 1292.3 | 1350 | 95.9 | 226 | 20140 PANTH BR 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.2 | 1292.3 | 1350 | 95.9 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 240 | 20151 WHITEOAK 230 20186 EDMONDSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.1 | 1292.3 | 1350 | 95.9 | 253 | 20162 MILBURNE 230 20178 AUBURN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 266 | 20173 TRI FRST 230 20210 APEXPOD4 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 271 | 20178 AUBURN 230 20179 WILS MIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295 | 1292.3 | 1350 | 95.9 | 330 | 20228 WILSON 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.2 | 1292.3 | 1350 | 95.9 | 406 | 20294 BISCOSUB 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 475 | 20352 BURLCR T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.7 | 1292.3 | 1350 | 95.9 | 577 | 20451 PA-GRNVL 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.1 | 1292.3 | 1350 | 95.9 | 717 | 20573 E4-POWEL 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 726 | 20582 DELCO 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 740 | 20598 FAIR B T 115 20629 NICHOLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.7 | 1292.3 | 1350 | 95.9 | 755 | 20629 NICHOLS 115 20630 MULLINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.5 | 1292.3 | 1350 | 95.9 | 764 | 20633 INDST T 115 20635 I-DUP FL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.5 | 1292.3 | 1350 | 95.9 | 765 | 20633 INDST T 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.2 | 1292.3 | 1350 | 95.9 | 767 | 20635 I-DUP FL 115 20641 I-STONE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.8 | 1292.3 | 1350 | 95.9 | 773 | 20644 PAMPLICO 115 20645 HEMINGWA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 779 | 20655 FLOR SO 115 20656 I-ESAB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.1 | 1292.3 | 1350 | 95.9 | 780 | 20656 I-ESAB 115 20657 GE TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 782 | 20657 GE TAP 115 20659 FLORENCE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.3 | 1292.3 | 1350 | 95.9 | 884 | 2511 BADIN 100 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.3 | 1292.3 | 1350 | 95.9 | 885 | 416 WATEREE 100 20734 WATRE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 862 | 44702 3KERR 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.4 | 1292.3 | 1350 | 95.9 | 23 | BISCOEW-BISCOESUB115_&_SPRINGT-I_FNDRY_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.5 | 1292.3 | 1350 | 95.9 | 9 | METH-NCCENT230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294.2 | 1292.3 | 1350 | 95.9 | 10 | NCCENT-CARALI230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1295.2 | 1292.3 | 1350 | 95.9 | 45 | WILSON-PA_WILSON#1_115KV_PODS
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 68 | 20018 ROB 2 N 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.7 | 1292.3 | 1350 | 95.8 | 72 | 20020 BRUN 2 N 230 20603 E1-PROSP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 73 | 20020 BRUN 2 N 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 77 | 20022 BRUN 1 N 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.3 | 1292.3 | 1350 | 95.8 | 109 | 20044 ROB 1 F 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294 | 1292.3 | 1350 | 95.8 | 121 | 20050 PA-GRN W 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 130 | 20057 DARL CO 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.3 | 1292.3 | 1350 | 95.8 | 140 | 20062 E4-TARHE 230 20573 E4-POWEL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294 | 1292.3 | 1350 | 95.8 | 156 | 20077 SIX FORK 230 20083 HONEYCUT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.7 | 1292.3 | 1350 | 95.8 | 160 | 20082 I-NCCENT 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 161 | 20082 I-NCCENT 230 20125 CARALEIG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.6 | 1292.3 | 1350 | 95.8 | 162 | 20083 HONEYCUT 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.7 | 1292.3 | 1350 | 95.8 | 164 | 20084 I-NOVO 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.3 | 1292.3 | 1350 | 95.8 | 174 | 20090 E12-ROX 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.6 | 1292.3 | 1350 | 95.8 | 180 | 20096 YOUNGSVL 115 20141 WF T NC2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 184 | 20100 HEND N T 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 189 | 20108 LOUISBRG 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 204 | 20122 REGNCYPK 230 20210 APEXPOD4 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1292.3 | 1350 | 95.8 | 217 | 20132 RAL SO 115 20137 METHOD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 219 | 20133 BELLS LK 230 20140 PANTH BR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.6 | 1292.3 | 1350 | 95.8 | 257 | 20163 MILBURNE 115 20170 CLAYTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 272 | 20179 WILS MIL 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 404 | 20292 E14-ETHR 115 20294 BISCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 405 | 20292 E14-ETHR 115 20303 SEAGROVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1292.3 | 1350 | 95.8 | 416 | 20303 SEAGROVE 115 20304 E14-ULAH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1292.3 | 1350 | 95.8 | 561 | 20429 E10-RENN 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.3 | 1292.3 | 1350 | 95.8 | 575 | 20448 FAIRMONT 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1294 | 1292.3 | 1350 | 95.8 | 579 | 20453 PA-WASH 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 594 | 20465 NEW BERN 230 20484 HAVELOCK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 671 | 20532 E4-KELLY 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 715 | 20571 ELIZAB T 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.7 | 1292.3 | 1350 | 95.8 | 737 | 20590 TABOR T 115 20597 E1-CHRYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 738 | 20597 E1-CHRYG 115 20598 FAIR B T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 770 | 20641 I-STONE 115 20642 DELTA T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 772 | 20642 DELTA T 115 20644 PAMPLICO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 877 | 42003 3EASTOVE 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.3 | 1292.3 | 1350 | 95.8 | 875 | 43005 6DARLING 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.4 | 1292.3 | 1350 | 95.8 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 13 | FALLS-HONEYCUT230_&_FALLS-LAKESTON115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.9 | 1292.3 | 1350 | 95.8 | 14 | FALLS-LAKESTON115_&_CHSTNTHL-NEUSE115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.8 | 1292.3 | 1350 | 95.8 | 12 | METH-TRYONHL115_&_METH-RALSO115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1293.5 | 1292.3 | 1350 | 95.8 | 18 | MILB-CLAYTON115_&_MILB-PERSTP115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1292.3 | 1292.3 | 1350 | 95.7 |  | ** Base Case **
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.1 | 1292.3 | 1350 | 95.6 | 71 | 20020 BRUN 2 N 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.5 | 1292.3 | 1350 | 95.6 | 101 | 20039 SUT 3 F 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.5 | 1292.3 | 1350 | 95.6 | 108 | 20044 ROB 1 F 115 20721 BETHNE T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.7 | 1292.3 | 1350 | 95.6 | 122 | 20052 CAPE F F 115 20134 MONCURE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.5 | 1292.3 | 1350 | 95.6 | 125 | 20052 CAPE F F 115 20295 I-HONEYW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290 | 1292.3 | 1350 | 95.6 | 138 | 20061 APEX US1 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.7 | 1292.3 | 1350 | 95.6 | 139 | 20062 E4-TARHE 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 178 | 20094 YANCY T 230 20095 YANCYVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 216 | 20131 WORTHDAL 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.6 | 1292.3 | 1350 | 95.6 | 261 | 20166 ZEBULON 69.0 20167 E18-EMIT 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.6 | 1292.3 | 1350 | 95.6 | 262 | 20166 ZEBULON 69.0 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.1 | 1292.3 | 1350 | 95.6 | 286 | 20194 BENSON 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.7 | 1292.3 | 1350 | 95.6 | 287 | 20195 I-BENPGI 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.9 | 1292.3 | 1350 | 95.6 | 292 | 20196 ERWIN 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.1 | 1292.3 | 1350 | 95.6 | 300 | 20202 ERWINSUB 115 20209 ERWIN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 307 | 20205 CLINTON 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.1 | 1292.3 | 1350 | 95.6 | 313 | 20209 ERWIN T 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.2 | 1292.3 | 1350 | 95.6 | 326 | 20224 PA-WRE-T 115 20225 PA-W-RE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.1 | 1292.3 | 1350 | 95.6 | 342 | 20237 E9-W ONS 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.1 | 1292.3 | 1350 | 95.6 | 343 | 20237 E9-W ONS 230 20521 CATHRNLK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290 | 1292.3 | 1350 | 95.6 | 347 | 20238 BLACK CK 115 20293 W-3TOWNS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 354 | 20247 GA PAC T 230 20249 I-GA PAC 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.4 | 1292.3 | 1350 | 95.6 | 368 | 20258 CLINTN N 115 20259 E15-HALL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 371 | 20261 LEE 115 20264 E+GAS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290 | 1292.3 | 1350 | 95.6 | 380 | 20269 MTOLVSUB 115 20270 MT OLV W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.5 | 1292.3 | 1350 | 95.6 | 410 | 20299 SC HWY64 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291 | 1292.3 | 1350 | 95.6 | 411 | 20299 SC HWY64 230 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 434 | 20318 E14-SPER 115 20353 I-UN&TIE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.4 | 1292.3 | 1350 | 95.6 | 447 | 20329 RAMSEUR 69.0 20330 I-RAMTEX 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.5 | 1292.3 | 1350 | 95.6 | 456 | 20341 MT GILED 115 20442 I-MG IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1292.3 | 1350 | 95.6 | 460 | 20346 RKH 115 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 461 | 20346 RKH 115 20348 RKH 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.1 | 1292.3 | 1350 | 95.6 | 474 | 20351 I-CORDVA 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.6 | 1292.3 | 1350 | 95.6 | 507 | 20379 M-FBMAIN 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 525 | 20393 SLOCUMB 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.9 | 1292.3 | 1350 | 95.6 | 530 | 20401 VANDER 115 20502 I-VANDAK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.7 | 1292.3 | 1350 | 95.6 | 539 | 20409 E15-WADE 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.1 | 1292.3 | 1350 | 95.6 | 549 | 20419 WAGRAMSW 115 20426 I-STV&GU 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.4 | 1292.3 | 1350 | 95.6 | 583 | 20454 AURORA 230 20461 E16-SLVR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.2 | 1292.3 | 1350 | 95.6 | 608 | 20475 WEYER T 115 20476 ICG-WYHS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.1 | 1292.3 | 1350 | 95.6 | 619 | 20484 HAVELOCK 230 20499 E2-MAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.6 | 1292.3 | 1350 | 95.6 | 640 | 20505 ROSE HIL 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1292.3 | 1350 | 95.6 | 641 | 20505 ROSE HIL 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.7 | 1292.3 | 1350 | 95.6 | 652 | 20514 I-OXYCHM 115 20533 ID/OCC T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 682 | 20543 E9-FOLKS 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 684 | 20544 HOLLY RG 115 20545 CASTLE H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 685 | 20544 HOLLY RG 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291.2 | 1292.3 | 1350 | 95.6 | 723 | 20581 WHITEVIL 115 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.2 | 1292.3 | 1350 | 95.6 | 728 | 20585 WH IND T 115 20586 I-GAPCWH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290 | 1292.3 | 1350 | 95.6 | 734 | 20588 CHADBN T 115 20589 CHADBORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1292.3 | 1350 | 95.6 | 736 | 20590 TABOR T 115 20596 TABOR C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.4 | 1292.3 | 1350 | 95.6 | 745 | 20613 E1-SO WH 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.9 | 1292.3 | 1350 | 95.6 | 806 | 20680 MANNIG T 115 20685 MANNING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1292.3 | 1350 | 95.6 | 810 | 20686 SUMTER 115 20687 EASTOV T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.3 | 1292.3 | 1350 | 95.6 | 814 | 20687 EASTOV T 115 20689 I-SUMIND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1291 | 1292.3 | 1350 | 95.6 | 820 | 20695 SHAW AFB 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.1 | 1292.3 | 1350 | 95.6 | 836 | 20713 JEFFSN T 115 20720 PAGELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.4 | 1292.3 | 1350 | 95.6 | 841 | 20721 BETHNE T 115 20722 BETHUNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290.8 | 1292.3 | 1350 | 95.6 | 848 | 20725 CAMDEN 115 20731 I-DUP CA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.9 | 1292.3 | 1350 | 95.6 | 26 | FAYE-FBWOOD230_&_SLOC_TAP-SLOCUMB115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1290 | 1292.3 | 1350 | 95.6 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 51 | 20004 TIL 1-4H 115 20341 MT GILED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 96 | 20035 SUT 1-2F 115 20557 I-GE WLM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.2 | 1292.3 | 1350 | 95.5 | 99 | 20039 SUT 3 F 230 20520 I-KOSA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.4 | 1292.3 | 1350 | 95.5 | 112 | 20046 WSPN BUS 230 20446 WSPN SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.2 | 1292.3 | 1350 | 95.5 | 142 | 20064 E6-WARTN 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 143 | 20064 E6-WARTN 115 20103 WARRENTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.1 | 1292.3 | 1350 | 95.5 | 158 | 20079 OXF S T 230 20080 OXFORD S 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.4 | 1292.3 | 1350 | 95.5 | 230 | 20142 ATLANTIC 115 20144 AVX TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.2 | 1292.3 | 1350 | 95.5 | 264 | 20171 AMBERLY 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.1 | 1292.3 | 1350 | 95.5 | 295 | 20198 BAILEY 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.5 | 1292.3 | 1350 | 95.5 | 311 | 20207 NEWTON G 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 353 | 20246 HEMLOCK 115 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 369 | 20259 E15-HALL 115 20260 ROSEBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 408 | 20296 CANDOR T 115 20306 CANDOR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.6 | 1292.3 | 1350 | 95.5 | 426 | 20313 ASHEBW T 115 20317 ASHEB W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.8 | 1292.3 | 1350 | 95.5 | 433 | 20318 E14-SPER 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.4 | 1292.3 | 1350 | 95.5 | 437 | 20320 E14-GRCH 115 20326 LIBERTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.8 | 1292.3 | 1350 | 95.5 | 440 | 20322 WDRMAN T 115 20394 E15-EUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 446 | 20327 E14-LIBR 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.8 | 1292.3 | 1350 | 95.5 | 506 | 20379 M-FBMAIN 230 20380 M-FBKNOX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.1 | 1292.3 | 1350 | 95.5 | 524 | 20392 FAY 115 20407 E15-BEAR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 536 | 20407 E15-BEAR 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.8 | 1292.3 | 1350 | 95.5 | 537 | 20408 BEARD 115 20409 E15-WADE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 538 | 20408 BEARD 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 562 | 20430 RED SPRG 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 578 | 20451 PA-GRNVL 230 20474 DUP KIN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 587 | 20461 E16-SLVR 230 20462 BAYBORO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.4 | 1292.3 | 1350 | 95.5 | 588 | 20461 E16-SLVR 230 20463 NB WEST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.8 | 1292.3 | 1350 | 95.5 | 590 | 20464 BRIDGETN 115 20466 NEW BERN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.9 | 1292.3 | 1350 | 95.5 | 593 | 20465 NEW BERN 230 20471 CCWDCG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.5 | 1292.3 | 1350 | 95.5 | 603 | 20471 CCWDCG T 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 607 | 20474 DUP KIN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.8 | 1292.3 | 1350 | 95.5 | 620 | 20485 HAVELOCK 115 20486 M-CH PT1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.8 | 1292.3 | 1350 | 95.5 | 633 | 20499 E2-MAYVL 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289 | 1292.3 | 1350 | 95.5 | 637 | 20501 SCOTT HL 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 654 | 20515 WALLACE 230 20516 I-BASF 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 656 | 20515 WALLACE 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 657 | 20516 I-BASF 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 660 | 20519 M-TARAWA 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 662 | 20519 M-TARAWA 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 663 | 20520 I-KOSA 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.1 | 1292.3 | 1350 | 95.5 | 665 | 20524 JACKSONV 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.6 | 1292.3 | 1350 | 95.5 | 668 | 20524 JACKSONV 230 20540 GEI&SW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.4 | 1292.3 | 1350 | 95.5 | 680 | 20540 GEI&SW T 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.9 | 1292.3 | 1350 | 95.5 | 681 | 20541 M-GEIGER 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 688 | 20549 TOPSAIL 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.2 | 1292.3 | 1350 | 95.5 | 690 | 20550 CSTL HYN 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.2 | 1292.3 | 1350 | 95.5 | 696 | 20556 TOPSL T 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 830 | 20709 HARTSN T 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.3 | 1292.3 | 1350 | 95.5 | 831 | 20709 HARTSN T 115 20717 I-SONOCO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289.7 | 1292.3 | 1350 | 95.5 | 835 | 20713 JEFFSN T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1289 | 1292.3 | 1350 | 95.5 | 840 | 20718 CHESTRFD 115 20719 CHERAW E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.4 | 1292.3 | 1350 | 95.4 | 49 | 20001 BLEWETT 115 20345 RKH W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.6 | 1292.3 | 1350 | 95.4 | 58 | 20009 HARRIS1N 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.6 | 1292.3 | 1350 | 95.4 | 60 | 20009 HARRIS1N 230 20338 E15-BRDW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.3 | 1292.3 | 1350 | 95.4 | 76 | 20022 BRUN 1 N 230 20354 I-ROCKY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 183 | 20100 HEND N T 115 20101 HEND NO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.4 | 1292.3 | 1350 | 95.4 | 186 | 20106 WAKEFORE 115 20107 E18-WEMC 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.4 | 1292.3 | 1350 | 95.4 | 187 | 20106 WAKEFORE 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.4 | 1292.3 | 1350 | 95.4 | 228 | 20141 WF T NC2 115 20607 PA-WF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.3 | 1292.3 | 1350 | 95.4 | 243 | 20154 ROLESVIL 230 20156 ROL/SQ T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 336 | 20231 GC/LEE T 115 20233 GOLDSB C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 337 | 20231 GC/LEE T 115 20239 GOLD C T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.4 | 1292.3 | 1350 | 95.4 | 370 | 20260 ROSEBORO 115 20265 E15-STED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.8 | 1292.3 | 1350 | 95.4 | 377 | 20265 E15-STED 115 20401 VANDER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.8 | 1292.3 | 1350 | 95.4 | 424 | 20312 ASHEB E 115 20320 E14-GRCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.3 | 1292.3 | 1350 | 95.4 | 458 | 20344 WADESBOR 230 20359 BOWMNSCH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.4 | 1292.3 | 1350 | 95.4 | 476 | 20354 I-ROCKY 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.5 | 1292.3 | 1350 | 95.4 | 486 | 20362 WEST END 115 20363 PINEHRST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.8 | 1292.3 | 1350 | 95.4 | 491 | 20367 LONGST T 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.1 | 1292.3 | 1350 | 95.4 | 508 | 20380 M-FBKNOX 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.8 | 1292.3 | 1350 | 95.4 | 514 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.8 | 1292.3 | 1350 | 95.4 | 515 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 519 | 20390 CUMBERLD 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.5 | 1292.3 | 1350 | 95.4 | 547 | 20416 MAXAPT T 115 20420 MAXT APT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.5 | 1292.3 | 1350 | 95.4 | 567 | 20436 PEMBROKE 115 20441 E10-PEMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288 | 1292.3 | 1350 | 95.4 | 570 | 20439 LUMBERTN 115 20606 CG-LUMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288 | 1292.3 | 1350 | 95.4 | 573 | 20446 WSPN SUB 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 589 | 20463 NB WEST 230 20465 NEW BERN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.2 | 1292.3 | 1350 | 95.4 | 628 | 20493 ATL BCH 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.3 | 1292.3 | 1350 | 95.4 | 649 | 20512 WALL SUB 115 20548 E4-WALL 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 716 | 20572 ELIZABTN 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.4 | 1292.3 | 1350 | 95.4 | 744 | 20611 SOUTH+PA 230 20612 I-ADM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.3 | 1292.3 | 1350 | 95.4 | 775 | 20647 MAR BYPS 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.4 | 1292.3 | 1350 | 95.4 | 783 | 20659 FLORENCE 115 20661 MT HOPE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.7 | 1292.3 | 1350 | 95.4 | 787 | 20660 DARLINGT 115 20669 DARLN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1288.5 | 1292.3 | 1350 | 95.4 | 792 | 20664 DILLN MP 230 20667 DILN NTH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.3 | 1292.3 | 1350 | 95.3 | 136 | 20061 APEX US1 230 20065 APEX US1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.3 | 1292.3 | 1350 | 95.3 | 144 | 20065 APEX US1 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 267 | 20175 SMITHF T 115 20176 PA-SMFLD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 297 | 20200 ZEBULON 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.8 | 1292.3 | 1350 | 95.3 | 301 | 20203 BAILEY T 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.6 | 1292.3 | 1350 | 95.3 | 374 | 20262 E17-MT O 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.5 | 1292.3 | 1350 | 95.3 | 421 | 20309 BISCOE W 230 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.1 | 1292.3 | 1350 | 95.3 | 451 | 20334 BYNUM 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.8 | 1292.3 | 1350 | 95.3 | 454 | 20338 E15-BRDW 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 492 | 20367 LONGST T 230 20384 M-FBLONG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.9 | 1292.3 | 1350 | 95.3 | 493 | 20367 LONGST T 230 20386 CLIFFDAL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287 | 1292.3 | 1350 | 95.3 | 495 | 20368 DEEPRV T 230 20376 DEEP RIV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.9 | 1292.3 | 1350 | 95.3 | 509 | 20381 RAEF SO 115 20413 RAEF SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.1 | 1292.3 | 1350 | 95.3 | 528 | 20400 E15-MAN 115 20460 E3-MANCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 556 | 20424 LAURINBG 230 20444 ROWLND T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286 | 1292.3 | 1350 | 95.3 | 559 | 20425 RED SP T 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.6 | 1292.3 | 1350 | 95.3 | 572 | 20444 ROWLND T 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.1 | 1292.3 | 1350 | 95.3 | 576 | 20449 DILLON 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 581 | 20454 AURORA 230 20455 I-PCS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.1 | 1292.3 | 1350 | 95.3 | 644 | 20508 PA-KINST 115 20529 KINSTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 659 | 20518 WARSAW T 230 20522 WARSAW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.7 | 1292.3 | 1350 | 95.3 | 678 | 20538 E9-PINYG 115 20539 E9-HARMN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287.2 | 1292.3 | 1350 | 95.3 | 679 | 20540 GEI&SW T 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287 | 1292.3 | 1350 | 95.3 | 837 | 20715 HARTSVIL 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1287 | 1292.3 | 1350 | 95.3 | 847 | 20725 CAMDEN 115 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.9 | 1292.3 | 1350 | 95.3 | 881 | 43010 6LUGOFF 230 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.7 | 1292.3 | 1350 | 95.3 | 880 | 43059 6BENNETT 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.9 | 1292.3 | 1350 | 95.3 | 853 | 844 6ENO 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.9 | 1292.3 | 1350 | 95.3 | 854 | 844 6ENO 230 20024 ROX 1-4F 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1292.3 | 1350 | 95.3 | 25 | FAY-FAYE230_&_FAY-WSP230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.6 | 1292.3 | 1350 | 95.2 | 116 | 20047 WSP BUS 115 20440 E10-WLUM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.9 | 1292.3 | 1350 | 95.2 | 200 | 20120 CARY TAP 230 20121 CARY SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.5 | 1292.3 | 1350 | 95.2 | 213 | 20129 OAKDAL T 230 20135 OAKDALE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.5 | 1292.3 | 1350 | 95.2 | 467 | 20348 RKH 230 20355 HAMLET 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.1 | 1292.3 | 1350 | 95.2 | 477 | 20355 HAMLET 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.9 | 1292.3 | 1350 | 95.2 | 498 | 20370 SO PINES 115 20371 CARTHAGE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.9 | 1292.3 | 1350 | 95.2 | 510 | 20381 RAEF SO 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.7 | 1292.3 | 1350 | 95.2 | 511 | 20386 CLIFFDAL 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.7 | 1292.3 | 1350 | 95.2 | 669 | 20525 M-LEJN#1 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.6 | 1292.3 | 1350 | 95.2 | 727 | 20584 GARLAND 230 20591 E4-YORK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1285.6 | 1292.3 | 1350 | 95.2 | 793 | 20664 DILLN MP 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.9 | 1292.3 | 1350 | 95.2 | 829 | 20708 C REIDPK 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.6 | 1292.3 | 1350 | 95.2 | 275 | 3Wnd: OPEN B$0024 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.6 | 1292.3 | 1350 | 95.2 | 276 | 3Wnd: OPEN B$0045 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.2 | 1292.3 | 1350 | 95.1 | 48 | 20001 BLEWETT 115 20004 TIL 1-4H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.1 | 1292.3 | 1350 | 95.1 | 106 | 20041 CF 5-6 F 230 20368 DEEPRV T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.2 | 1292.3 | 1350 | 95.1 | 245 | 20156 ROL/SQ T 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.4 | 1292.3 | 1350 | 95.1 | 246 | 20156 ROL/SQ T 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.7 | 1292.3 | 1350 | 95.1 | 280 | 20190 WAKE 230 20191 WENDELL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.1 | 1292.3 | 1350 | 95.1 | 282 | 20191 WENDELL 230 20200 ZEBULON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.3 | 1292.3 | 1350 | 95.1 | 365 | 20255 CLINTON 115 20256 CL FEREL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.4 | 1292.3 | 1350 | 95.1 | 401 | 20290 I-OLVRRB 115 20311 ASHEB S 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.5 | 1292.3 | 1350 | 95.1 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.4 | 1292.3 | 1350 | 95.1 | 443 | 20323 RAMS TAP 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.3 | 1292.3 | 1350 | 95.1 | 661 | 20519 M-TARAWA 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.3 | 1292.3 | 1350 | 95.1 | 677 | 20537 E9-JAX E 115 20538 E9-PINYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.7 | 1292.3 | 1350 | 95.1 | 695 | 20553 9TH&ORNG 230 20554 9THORG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.7 | 1292.3 | 1350 | 95.1 | 748 | 20616 BARNARD 115 20618 SUNSET P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.7 | 1292.3 | 1350 | 95.1 | 750 | 20617 CARL BCH 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1284.2 | 1292.3 | 1350 | 95.1 | 794 | 20665 I-NUCOR 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283 | 1292.3 | 1350 | 95 | 334 | 20230 WILSON 115 20235 PA-W-11 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.8 | 1292.3 | 1350 | 95 | 463 | 20346 RKH 115 20456 E11-RHAM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.3 | 1292.3 | 1350 | 95 | 489 | 20364 ABERDEEN 115 20365 CENTER P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.2 | 1292.3 | 1350 | 95 | 500 | 20373 S GARD T 230 20374 SANF GAR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.3 | 1292.3 | 1350 | 95 | 566 | 20435 MAXTON 115 20436 PEMBROKE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282 | 1292.3 | 1350 | 95 | 601 | 20469 PA-GLENB 115 20470 PA-NBCTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.1 | 1292.3 | 1350 | 95 | 632 | 20498 MR WILDW 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.6 | 1292.3 | 1350 | 95 | 648 | 20512 WALL SUB 115 20517 WALLACE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.9 | 1292.3 | 1350 | 95 | 705 | 20568 DELCO 115 20569 ICG-IPPR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1283.1 | 1292.3 | 1350 | 95 | 722 | 20580 WHTV TAP 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282.5 | 1292.3 | 1350 | 95 | 743 | 20601 CG-SOPRT 230 20611 SOUTH+PA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1281.2 | 1292.3 | 1350 | 94.9 | 293 | 20196 ERWIN 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1281.6 | 1292.3 | 1350 | 94.9 | 494 | 20368 DEEPRV T 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1281.3 | 1292.3 | 1350 | 94.9 | 499 | 20371 CARTHAGE 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280.5 | 1292.3 | 1350 | 94.9 | 513 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1281.3 | 1292.3 | 1350 | 94.9 | 526 | 20395 SPRING L 115 20400 E15-MAN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280.4 | 1292.3 | 1350 | 94.8 | 104 | 20041 CF 5-6 F 230 20297 JONESBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280 | 1292.3 | 1350 | 94.8 | 459 | 20345 RKH W 115 20346 RKH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1279.5 | 1292.3 | 1350 | 94.8 | 478 | 20356 ROCKFISH 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1279.5 | 1292.3 | 1350 | 94.8 | 490 | 20366 WEST END 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1280.4 | 1292.3 | 1350 | 94.8 | 821 | 20698 REIDPK T 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.5 | 1292.3 | 1350 | 94.7 | 479 | 20356 ROCKFISH 230 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.9 | 1292.3 | 1350 | 94.7 | 512 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.4 | 1292.3 | 1350 | 94.7 | 540 | 20411 RAEFORD 115 20414 RAEF TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.4 | 1292.3 | 1350 | 94.7 | 545 | 20414 RAEF TAP 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.4 | 1292.3 | 1350 | 94.7 | 563 | 20433 I-PLKLOF 115 20434 BUTLER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.8 | 1292.3 | 1350 | 94.7 | 565 | 20434 BUTLER 115 20435 MAXTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1278.1 | 1292.3 | 1350 | 94.7 | 675 | 20536 JAX CITY 115 20537 E9-JAX E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1277.7 | 1292.3 | 1350 | 94.6 | 441 | 20322 WDRMAN T 115 20395 SPRING L 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1277.3 | 1292.3 | 1350 | 94.6 | 481 | 20357 SH US#1 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1277.6 | 1292.3 | 1350 | 94.6 | 749 | 20616 BARNARD 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1277.7 | 1292.3 | 1350 | 94.6 | 29 | RKH-WADESBORO230_&_BLEW-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1275.1 | 1292.3 | 1350 | 94.5 | 442 | 20322 WDRMAN T 115 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1276.1 | 1292.3 | 1350 | 94.5 | 457 | 20344 WADESBOR 230 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1275.2 | 1292.3 | 1350 | 94.5 | 527 | 20398 M-FBWOOD 230 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1276 | 1292.3 | 1350 | 94.5 | 598 | 20466 NEW BERN 115 20469 PA-GLENB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1275.2 | 1292.3 | 1350 | 94.5 | 127 | 3Wnd: OPEN B$0014 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1274.8 | 1292.3 | 1350 | 94.4 | 432 | 20316 E10-ARAB 115 20418 E10-ROCK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1273.9 | 1292.3 | 1350 | 94.4 | 480 | 20357 SH US#1 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1274.6 | 1292.3 | 1350 | 94.4 | 502 | 3Wnd: OPEN B$0022 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1274.3 | 1292.3 | 1350 | 94.4 | 503 | 3Wnd: OPEN B$0046 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1273.7 | 1292.3 | 1350 | 94.3 | 431 | 20316 E10-ARAB 115 20411 RAEFORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1273.3 | 1292.3 | 1350 | 94.3 | 487 | 20362 WEST END 115 20364 ABERDEEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1271.5 | 1292.3 | 1350 | 94.2 | 642 | 20507 WOMMACK 115 20508 PA-KINST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.4 | 1292.3 | 1350 | 94.1 | 24 | CUMB-FAY230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.4 | 1292.3 | 1350 | 94.1 | 30 | RKH-WADESBORO230_&_RKH-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1269.3 | 1292.3 | 1350 | 94 | 429 | 20314 E3-CTRCH 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1268.4 | 1292.3 | 1350 | 94 | 469 | 20348 RKH 230 20378 RICHMOND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1269.6 | 1292.3 | 1350 | 94 | 470 | 20348 RKH 230 20378 RICHMOND 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1269 | 1292.3 | 1350 | 94 | 746 | 20615 BARNARD 230 20616 BARNARD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1268.3 | 1292.3 | 1350 | 93.9 | 428 | 20314 E3-CTRCH 230 20361 WEST END 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1267.3 | 1292.3 | 1350 | 93.9 | 27 | FAY-ROCKFISH230_&_FAY-HAMLET230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1266.2 | 1292.3 | 1350 | 93.8 | 28 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1263.9 | 1292.3 | 1350 | 93.6 | 504 | 20378 RICHMOND 230 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1261.9 | 1292.3 | 1350 | 93.5 | 555 | 20422 LBG CITY 230 20424 LAURINBG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.3 | 1292.3 | 1350 | 93.1 | 420 | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255.9 | 1292.3 | 1350 | 93 | 554 | 20422 LBG CITY 230 20423 LAUREL H 230 1
20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | LN | 632.1 | 456 | 637 | 99.2 | 513 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | LN | 609.4 | 456 | 637 | 95.7 | 25 | FAY-FAYE230_&_FAY-WSP230
20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | LN | 607.9 | 322.4 | 637 | 95.4 | 512 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20421 LAURINBG 115 20424 LAURINBG 230 1 | TR | 197.9 | 109.3 | 200 | 98.9 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20421 LAURINBG 115 20424 LAURINBG 230 2 | TR | 197.7 | 108.5 | 200 | 98.8 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20552 E WILM 230 20554 9THORG T 230 1 | LN | 576.7 | 180.4 | 590 | 97.7 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 142.9 | 142.9 | 150 | 95.3 |  | ** Base Case **
20683 BURNETTE 115 20302 E14-TROY 115 1 | LN | 257.3 | 155 | 269 | 95.6 | 464 | 20347 ABRDN RD 230 20348 RKH 230 1
B$0024 1.00 20183 WAKE 500 1 | TR | 983.6 | 634.5 | 1000 | 98.4 | 276 | 3Wnd: OPEN B$0045 2
B$0024 1.00 20190 WAKE 230 1 | TR | 960.1 | 625.2 | 1000 | 96 | 276 | 3Wnd: OPEN B$0045 2
B$0045 1.00 20183 WAKE 500 2 | TR | 983.3 | 634.1 | 1000 | 98.3 | 275 | 3Wnd: OPEN B$0024 1
B$0045 1.00 20190 WAKE 230 2 | TR | 959.9 | 624.8 | 1000 | 96 | 275 | 3Wnd: OPEN B$0024 1
Note on A18: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C18: PTI: Contingency MVA for Tran and Amp for Lines
Note on D18: PTI: Base Case Flow
Note on E18: PTI: Branch Rating
Note on F18: PTI: Loading in %
Note on G18: PTI: Contingency index
Note on H18: PTI: Contingency Description

## PEC Branch
Branch Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- TUE, APR 04 2006 9:47
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 SERIES RELEASED 6/05
Case.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\BaseCase\duk11s_PEC_Final+RICH-NEWPORT CHANGE.sav
Subsys.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\East.sub
Monit.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\East.mon
Contin.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File none
************** Report on violations ********************
Branches with MVA flow more than 94.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Ncon | Contingency
20039 SUT 3 F 230 20554 9THORG T 230 1 | LN | 673.8 | 232.1 | 590 | 107.7 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20185 FALLS 115 20182 FALLS 230 1 | TR | 304.1 | 212.2 | 300 | 101.4 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | TR | 299.1 | 212.2 | 300 | 99.7 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20552 E WILM 230 20554 9THORG T 230 1 | LN | 616.6 | 180.9 | 590 | 99.1 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 142.9 | 142.9 | 150 | 95.7 |  | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 142.9 | 142.9 | 150 | 95.2 |  | ** Base Case **
20421 LAURINBG 115 20424 LAURINBG 230 1 | TR | 189.8 | 104.8 | 200 | 94.9 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20421 LAURINBG 115 20424 LAURINBG 230 2 | TR | 189.5 | 104.1 | 200 | 94.8 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 159.9 | 77.7 | 170 | 94.1 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
Note on A18: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C18: PTI: Contingency MVA for Tran and Amp for Lines
Note on D18: PTI: Base Case Flow
Note on E18: PTI: Branch Rating
Note on F18: PTI: Loading in %
Note on G18: PTI: Contingency index
Note on H18: PTI: Contingency Description

## PEC Volt
Bus Voltage Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- TUE, APR 04 2006 9:47
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 SERIES RELEASED 6/05
Case.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\BaseCase\duk11s_PEC_Final+RICH-NEWPORT CHANGE.sav
Subsys.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\East.sub
Monit.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\East.mon
Contin.File C:\Documents and Settings\i30155\My Documents\JWest_BaseCases\PWG\PECMon-COn\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File none
************** Report on violations ********************
Buses with voltage violations
Bus # | Bus Name | KV | Area | Zone | ContVolt | BaseVolt | LowLimit | UppLimit | VoltDrop | VoltRise | Viol | Ncon | Contingency Description
20106 | WAKEFORE | 115 | 140 | 101 | 0.9103 | 0.972 | 0.92 | 9999 | 0.9234 | - | LD | 193 | 20111 E18-WK F 115 20185 FALLS 115 1
20107 | E18-WEMC | 69 | 140 | 102 | 0.8922 | 0.9553 | 0.92 | 9999 | 0.9075 | - | LD | 193 | 20111 E18-WK F 115 20185 FALLS 115 1
20107 | E18-WEMC | 69 | 140 | 102 | 0.9183 | 0.9553 | 0.92 | 9999 | 0.9075 | - | L | 192 | 20111 E18-WK F 115 20113 WF T NC1 115 1
20111 | E18-WK F | 115 | 140 | 102 | 0.9081 | 0.9757 | 0.92 | 9999 | 0.9269 | - | LD | 193 | 20111 E18-WK F 115 20185 FALLS 115 1
20113 | WF T NC1 | 115 | 140 | 101 | 0.9103 | 0.9721 | 0.92 | 9999 | 0.9235 | - | LD | 193 | 20111 E18-WK F 115 20185 FALLS 115 1
20176 | PA-SMFLD | 115 | 140 | 103 | 0.9126 | 0.9881 | 0.92 | 9999 | 0.9387 | - | LD | 268 | 20175 SMITHF T 115 20177 SELMA 115 1
20544 | HOLLY RG | 115 | 140 | 101 | 0.9193 | 0.9792 | 0.92 | 9999 | 0.9302 | - | LD | 684 | 20544 HOLLY RG 115 20545 CASTLE H 115 1
Note on A14: PTI: Bus Number
Note on B14: PTI: Bus Name
Note on C14: PTI: Voltage Base
Note on D14: PTI: Area Number
Note on E14: PTI: Zone
Note on F14: PTI: Contingent Voltage
Note on G14: PTI: Base Case Voltage
Note on H14: PTI: Low Limit For Range Limit
Note on I14: PTI: Upper Limit For Range Limit
Note on J14: PTI: Voltage Drop Limit
Note on K14: PTI: Voltage Rise Limit
Note on L14: PTI: Voltage Violation: L-low limit, D-Drop, H-Upper Limit, R-Rise
Note on M14: PTI: Contingency Index
Note on N14: PTI: Contingency Description

## 3200 MW BR1 DN BRANCH
Branch Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- WED, APR 26 2006 10:43
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 SERIES REL 6/05,BR1 DN TRM
Case.File J:\NC Stakeholders\2011S Study\Study Cases\TRMcases\duk11s_PEC_FinalNP_Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.sub
Monit.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.mon
Contin.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-Eastern System.EXC
************** Report on violations ********************
Branches with MVA flow more than 90.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Ncon | Contingency
B$0045 1.00 20183 WAKE 500 2 | TR | 908.7 | 586.5 | 1000 | 90.9 | 275 | 3Wnd: OPEN B$0024 1
B$0024 1.00 20183 WAKE 500 1 | TR | 909 | 586.9 | 1000 | 90.9 | 276 | 3Wnd: OPEN B$0045 2
20654 DILLON T 115 20632 MARION 115 1 | LN | 88.6 | 68.7 | 97 | 91.3 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20654 DILLON T 115 20632 MARION 115 1 | LN | 94.2 | 68.7 | 97 | 97.1 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 142.9 | 142.9 | 150 | 95.3 |  | ** Base Case **
20552 E WILM 230 20554 9THORG T 230 1 | LN | 545.8 | 247.9 | 590 | 92.5 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20421 LAURINBG 115 20424 LAURINBG 230 2 | TR | 195.3 | 107.3 | 200 | 97.6 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20421 LAURINBG 115 20424 LAURINBG 230 1 | TR | 195.5 | 108 | 200 | 97.8 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20387 P1-FAY 0 230 20392 FAY 115 2 | TR | 186.8 | 110.4 | 200 | 93.4 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20387 P1-FAY 0 230 20392 FAY 115 1 | TR | 186.9 | 110.6 | 200 | 93.4 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.4 | 1240.5 | 1350 | 90 | 27 | FAY-ROCKFISH230_&_FAY-HAMLET230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.8 | 1240.5 | 1350 | 90.1 | 746 | 20615 BARNARD 230 20616 BARNARD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1240.5 | 1350 | 90.3 | 30 | RKH-WADESBORO230_&_RKH-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.1 | 1240.5 | 1350 | 90.3 | 58 | 20009 HARRIS1N 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1240.5 | 1350 | 90.3 | 469 | 20348 RKH 230 20378 RICHMOND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1240.5 | 1350 | 90.3 | 642 | 20507 WOMMACK 115 20508 PA-KINST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1240.5 | 1350 | 90.4 | 138 | 20061 APEX US1 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.5 | 1240.5 | 1350 | 90.4 | 470 | 20348 RKH 230 20378 RICHMOND 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1221.8 | 1240.5 | 1350 | 90.5 | 431 | 20316 E10-ARAB 115 20411 RAEFORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1221.6 | 1240.5 | 1350 | 90.5 | 487 | 20362 WEST END 115 20364 ABERDEEN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.6 | 1240.5 | 1350 | 90.6 | 137 | 20061 APEX US1 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1222.8 | 1240.5 | 1350 | 90.6 | 428 | 20314 E3-CTRCH 230 20361 WEST END 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1240.5 | 1350 | 90.6 | 429 | 20314 E3-CTRCH 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1222.9 | 1240.5 | 1350 | 90.6 | 432 | 20316 E10-ARAB 115 20418 E10-ROCK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1240.5 | 1350 | 90.6 | 442 | 20322 WDRMAN T 115 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1240.5 | 1350 | 90.6 | 527 | 20398 M-FBWOOD 230 20399 FB WOODR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.9 | 1240.5 | 1350 | 90.7 | 24 | CUMB-FAY230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.4 | 1240.5 | 1350 | 90.7 | 127 | 3Wnd: OPEN B$0014 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.3 | 1240.5 | 1350 | 90.7 | 457 | 20344 WADESBOR 230 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224 | 1240.5 | 1350 | 90.7 | 598 | 20466 NEW BERN 115 20469 PA-GLENB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.8 | 1240.5 | 1350 | 90.8 | 441 | 20322 WDRMAN T 115 20395 SPRING L 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.5 | 1240.5 | 1350 | 90.8 | 502 | 3Wnd: OPEN B$0022 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.2 | 1240.5 | 1350 | 90.8 | 503 | 3Wnd: OPEN B$0046 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.9 | 1240.5 | 1350 | 90.8 | 675 | 20536 JAX CITY 115 20537 E9-JAX E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.8 | 1240.5 | 1350 | 90.8 | 749 | 20616 BARNARD 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.6 | 1240.5 | 1350 | 90.9 | 29 | RKH-WADESBORO230_&_BLEW-RKHW115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.1 | 1240.5 | 1350 | 90.9 | 479 | 20356 ROCKFISH 230 20415 RAEFORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.7 | 1240.5 | 1350 | 90.9 | 490 | 20366 WEST END 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.6 | 1240.5 | 1350 | 90.9 | 540 | 20411 RAEFORD 115 20414 RAEF TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.6 | 1240.5 | 1350 | 90.9 | 545 | 20414 RAEF TAP 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.6 | 1240.5 | 1350 | 90.9 | 563 | 20433 I-PLKLOF 115 20434 BUTLER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227 | 1240.5 | 1350 | 90.9 | 565 | 20434 BUTLER 115 20435 MAXTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.7 | 1240.5 | 1350 | 91 | 104 | 20041 CF 5-6 F 230 20297 JONESBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229 | 1240.5 | 1350 | 91 | 459 | 20345 RKH W 115 20346 RKH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228 | 1240.5 | 1350 | 91 | 478 | 20356 ROCKFISH 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.3 | 1240.5 | 1350 | 91 | 480 | 20357 SH US#1 230 20373 S GARD T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.9 | 1240.5 | 1350 | 91 | 519 | 20390 CUMBERLD 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.7 | 1240.5 | 1350 | 91 | 821 | 20698 REIDPK T 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.5 | 1240.5 | 1350 | 91.1 | 205 | 20122 REGNCYPK 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.5 | 1240.5 | 1350 | 91.1 | 499 | 20371 CARTHAGE 115 20372 E14-EAST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.8 | 1240.5 | 1350 | 91.1 | 512 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.4 | 1240.5 | 1350 | 91.1 | 526 | 20395 SPRING L 115 20400 E15-MAN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.5 | 1240.5 | 1350 | 91.1 | 566 | 20435 MAXTON 115 20436 PEMBROKE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230 | 1240.5 | 1350 | 91.1 | 601 | 20469 PA-GLENB 115 20470 PA-NBCTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.3 | 1240.5 | 1350 | 91.1 | 743 | 20601 CG-SOPRT 230 20611 SOUTH+PA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.3 | 1240.5 | 1350 | 91.2 | 280 | 20190 WAKE 230 20191 WENDELL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.7 | 1240.5 | 1350 | 91.2 | 282 | 20191 WENDELL 230 20200 ZEBULON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.3 | 1240.5 | 1350 | 91.2 | 293 | 20196 ERWIN 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.1 | 1240.5 | 1350 | 91.2 | 334 | 20230 WILSON 115 20235 PA-W-11 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.1 | 1240.5 | 1350 | 91.2 | 463 | 20346 RKH 115 20456 E11-RHAM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.8 | 1240.5 | 1350 | 91.2 | 481 | 20357 SH US#1 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.5 | 1240.5 | 1350 | 91.2 | 489 | 20364 ABERDEEN 115 20365 CENTER P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.4 | 1240.5 | 1350 | 91.2 | 500 | 20373 S GARD T 230 20374 SANF GAR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.1 | 1240.5 | 1350 | 91.2 | 632 | 20498 MR WILDW 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.5 | 1240.5 | 1350 | 91.2 | 648 | 20512 WALL SUB 115 20517 WALLACE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.4 | 1240.5 | 1350 | 91.2 | 672 | 20532 E4-KELLY 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.2 | 1240.5 | 1350 | 91.2 | 677 | 20537 E9-JAX E 115 20538 E9-PINYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.6 | 1240.5 | 1350 | 91.2 | 695 | 20553 9TH&ORNG 230 20554 9THORG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231 | 1240.5 | 1350 | 91.2 | 705 | 20568 DELCO 115 20569 ICG-IPPR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.3 | 1240.5 | 1350 | 91.2 | 722 | 20580 WHTV TAP 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.6 | 1240.5 | 1350 | 91.2 | 748 | 20616 BARNARD 115 20618 SUNSET P 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.7 | 1240.5 | 1350 | 91.2 | 750 | 20617 CARL BCH 115 20693 RIVER RD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233 | 1240.5 | 1350 | 91.3 | 48 | 20001 BLEWETT 115 20004 TIL 1-4H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.9 | 1240.5 | 1350 | 91.3 | 245 | 20156 ROL/SQ T 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232 | 1240.5 | 1350 | 91.3 | 246 | 20156 ROL/SQ T 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.4 | 1240.5 | 1350 | 91.3 | 365 | 20255 CLINTON 115 20256 CL FEREL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.7 | 1240.5 | 1350 | 91.3 | 401 | 20290 I-OLVRRB 115 20311 ASHEB S 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.6 | 1240.5 | 1350 | 91.3 | 443 | 20323 RAMS TAP 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.5 | 1240.5 | 1350 | 91.3 | 467 | 20348 RKH 230 20355 HAMLET 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233 | 1240.5 | 1350 | 91.3 | 477 | 20355 HAMLET 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233 | 1240.5 | 1350 | 91.3 | 498 | 20370 SO PINES 115 20371 CARTHAGE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.1 | 1240.5 | 1350 | 91.3 | 510 | 20381 RAEF SO 115 20417 E10-RAEF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.2 | 1240.5 | 1350 | 91.3 | 513 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.3 | 1240.5 | 1350 | 91.3 | 556 | 20424 LAURINBG 230 20444 ROWLND T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.5 | 1240.5 | 1350 | 91.3 | 572 | 20444 ROWLND T 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.3 | 1240.5 | 1350 | 91.3 | 661 | 20519 M-TARAWA 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.4 | 1240.5 | 1350 | 91.3 | 794 | 20665 I-NUCOR 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.1 | 1240.5 | 1350 | 91.3 | 829 | 20708 C REIDPK 230 20712 CASH RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.7 | 1240.5 | 1350 | 91.4 | 116 | 20047 WSP BUS 115 20440 E10-WLUM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.5 | 1240.5 | 1350 | 91.4 | 136 | 20061 APEX US1 230 20065 APEX US1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.5 | 1240.5 | 1350 | 91.4 | 144 | 20065 APEX US1 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.1 | 1240.5 | 1350 | 91.4 | 200 | 20120 CARY TAP 230 20121 CARY SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.7 | 1240.5 | 1350 | 91.4 | 213 | 20129 OAKDAL T 230 20135 OAKDALE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.5 | 1240.5 | 1350 | 91.4 | 267 | 20175 SMITHF T 115 20176 PA-SMFLD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.3 | 1240.5 | 1350 | 91.4 | 275 | 3Wnd: OPEN B$0024 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.3 | 1240.5 | 1350 | 91.4 | 276 | 3Wnd: OPEN B$0045 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234 | 1240.5 | 1350 | 91.4 | 297 | 20200 ZEBULON 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.4 | 1240.5 | 1350 | 91.4 | 301 | 20203 BAILEY T 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.2 | 1240.5 | 1350 | 91.4 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.6 | 1240.5 | 1350 | 91.4 | 492 | 20367 LONGST T 230 20384 M-FBLONG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.3 | 1240.5 | 1350 | 91.4 | 528 | 20400 E15-MAN 115 20460 E3-MANCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.2 | 1240.5 | 1350 | 91.4 | 559 | 20425 RED SP T 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.8 | 1240.5 | 1350 | 91.4 | 573 | 20446 WSPN SUB 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.3 | 1240.5 | 1350 | 91.4 | 576 | 20449 DILLON 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.4 | 1240.5 | 1350 | 91.4 | 581 | 20454 AURORA 230 20455 I-PCS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.1 | 1240.5 | 1350 | 91.4 | 644 | 20508 PA-KINST 115 20529 KINSTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.5 | 1240.5 | 1350 | 91.4 | 659 | 20518 WARSAW T 230 20522 WARSAW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.7 | 1240.5 | 1350 | 91.4 | 669 | 20525 M-LEJN#1 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.3 | 1240.5 | 1350 | 91.4 | 671 | 20532 E4-KELLY 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.8 | 1240.5 | 1350 | 91.4 | 727 | 20584 GARLAND 230 20591 E4-YORK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.8 | 1240.5 | 1350 | 91.4 | 793 | 20664 DILLN MP 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.5 | 1240.5 | 1350 | 91.4 | 853 | 844 6ENO 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.5 | 1240.5 | 1350 | 91.4 | 854 | 844 6ENO 230 20024 ROX 1-4F 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.4 | 1240.5 | 1350 | 91.4 | 880 | 43059 6BENNETT 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234 | 1240.5 | 1350 | 91.4 | 881 | 43010 6LUGOFF 230 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.6 | 1240.5 | 1350 | 91.5 | 25 | FAY-FAYE230_&_FAY-WSP230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.1 | 1240.5 | 1350 | 91.5 | 112 | 20046 WSPN BUS 230 20446 WSPN SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.9 | 1240.5 | 1350 | 91.5 | 139 | 20062 E4-TARHE 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.6 | 1240.5 | 1350 | 91.5 | 228 | 20141 WF T NC2 115 20607 PA-WF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.5 | 1240.5 | 1350 | 91.5 | 243 | 20154 ROLESVIL 230 20156 ROL/SQ T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.7 | 1240.5 | 1350 | 91.5 | 374 | 20262 E17-MT O 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.9 | 1240.5 | 1350 | 91.5 | 377 | 20265 E15-STED 115 20401 VANDER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.7 | 1240.5 | 1350 | 91.5 | 421 | 20309 BISCOE W 230 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.3 | 1240.5 | 1350 | 91.5 | 451 | 20334 BYNUM 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.5 | 1240.5 | 1350 | 91.5 | 458 | 20344 WADESBOR 230 20359 BOWMNSCH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.7 | 1240.5 | 1350 | 91.5 | 486 | 20362 WEST END 115 20363 PINEHRST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.4 | 1240.5 | 1350 | 91.5 | 495 | 20368 DEEPRV T 230 20376 DEEP RIV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.1 | 1240.5 | 1350 | 91.5 | 509 | 20381 RAEF SO 115 20413 RAEF SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.7 | 1240.5 | 1350 | 91.5 | 547 | 20416 MAXAPT T 115 20420 MAXT APT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.7 | 1240.5 | 1350 | 91.5 | 567 | 20436 PEMBROKE 115 20441 E10-PEMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.4 | 1240.5 | 1350 | 91.5 | 649 | 20512 WALL SUB 115 20548 E4-WALL 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.7 | 1240.5 | 1350 | 91.5 | 678 | 20538 E9-PINYG 115 20539 E9-HARMN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.2 | 1240.5 | 1350 | 91.5 | 679 | 20540 GEI&SW T 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.5 | 1240.5 | 1350 | 91.5 | 775 | 20647 MAR BYPS 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.7 | 1240.5 | 1350 | 91.5 | 783 | 20659 FLORENCE 115 20661 MT HOPE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.9 | 1240.5 | 1350 | 91.5 | 787 | 20660 DARLINGT 115 20669 DARLN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.2 | 1240.5 | 1350 | 91.5 | 837 | 20715 HARTSVIL 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.1 | 1240.5 | 1350 | 91.5 | 847 | 20725 CAMDEN 115 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.2 | 1240.5 | 1350 | 91.6 | 49 | 20001 BLEWETT 115 20345 RKH W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.2 | 1240.5 | 1350 | 91.6 | 158 | 20079 OXF S T 230 20080 OXFORD S 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.7 | 1240.5 | 1350 | 91.6 | 183 | 20100 HEND N T 115 20101 HEND NO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.6 | 1240.5 | 1350 | 91.6 | 186 | 20106 WAKEFORE 115 20107 E18-WEMC 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.6 | 1240.5 | 1350 | 91.6 | 187 | 20106 WAKEFORE 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.7 | 1240.5 | 1350 | 91.6 | 336 | 20231 GC/LEE T 115 20233 GOLDSB C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.7 | 1240.5 | 1350 | 91.6 | 337 | 20231 GC/LEE T 115 20239 GOLD C T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.5 | 1240.5 | 1350 | 91.6 | 370 | 20260 ROSEBORO 115 20265 E15-STED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236 | 1240.5 | 1350 | 91.6 | 424 | 20312 ASHEB E 115 20320 E14-GRCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.7 | 1240.5 | 1350 | 91.6 | 426 | 20313 ASHEBW T 115 20317 ASHEB W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.9 | 1240.5 | 1350 | 91.6 | 433 | 20318 E14-SPER 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.2 | 1240.5 | 1350 | 91.6 | 494 | 20368 DEEPRV T 230 20375 SANF HOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.6 | 1240.5 | 1350 | 91.6 | 511 | 20386 CLIFFDAL 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.2 | 1240.5 | 1350 | 91.6 | 570 | 20439 LUMBERTN 115 20606 CG-LUMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.8 | 1240.5 | 1350 | 91.6 | 620 | 20485 HAVELOCK 115 20486 M-CH PT1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.2 | 1240.5 | 1350 | 91.6 | 628 | 20493 ATL BCH 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.1 | 1240.5 | 1350 | 91.6 | 637 | 20501 SCOTT HL 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.6 | 1240.5 | 1350 | 91.6 | 716 | 20572 ELIZABTN 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.4 | 1240.5 | 1350 | 91.6 | 744 | 20611 SOUTH+PA 230 20612 I-ADM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.6 | 1240.5 | 1350 | 91.6 | 792 | 20664 DILLN MP 230 20667 DILN NTH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.2 | 1240.5 | 1350 | 91.6 | 840 | 20718 CHESTRFD 115 20719 CHERAW E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 26 | FAYE-FBWOOD230_&_SLOC_TAP-SLOCUMB115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.6 | 1240.5 | 1350 | 91.7 | 51 | 20004 TIL 1-4H 115 20341 MT GILED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 56 | 20009 HARRIS1N 230 20058 HOLLYSPG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 71 | 20020 BRUN 2 N 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 75 | 20022 BRUN 1 N 230 20046 WSPN BUS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 76 | 20022 BRUN 1 N 230 20354 I-ROCKY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.7 | 1240.5 | 1350 | 91.7 | 96 | 20035 SUT 1-2F 115 20557 I-GE WLM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 99 | 20039 SUT 3 F 230 20520 I-KOSA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 108 | 20044 ROB 1 F 115 20721 BETHNE T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 122 | 20052 CAPE F F 115 20134 MONCURE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.3 | 1240.5 | 1350 | 91.7 | 140 | 20062 E4-TARHE 230 20573 E4-POWEL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.4 | 1240.5 | 1350 | 91.7 | 142 | 20064 E6-WARTN 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 143 | 20064 E6-WARTN 115 20103 WARRENTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 203 | 20122 REGNCYPK 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.5 | 1240.5 | 1350 | 91.7 | 230 | 20142 ATLANTIC 115 20144 AVX TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.4 | 1240.5 | 1350 | 91.7 | 264 | 20171 AMBERLY 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 292 | 20196 ERWIN 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.3 | 1240.5 | 1350 | 91.7 | 295 | 20198 BAILEY 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.7 | 1240.5 | 1350 | 91.7 | 311 | 20207 NEWTON G 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 326 | 20224 PA-WRE-T 115 20225 PA-W-RE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.2 | 1240.5 | 1350 | 91.7 | 347 | 20238 BLACK CK 115 20293 W-3TOWNS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 353 | 20246 HEMLOCK 115 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 368 | 20258 CLINTN N 115 20259 E15-HALL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.7 | 1240.5 | 1350 | 91.7 | 369 | 20259 E15-HALL 115 20260 ROSEBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.2 | 1240.5 | 1350 | 91.7 | 380 | 20269 MTOLVSUB 115 20270 MT OLV W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 408 | 20296 CANDOR T 115 20306 CANDOR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.5 | 1240.5 | 1350 | 91.7 | 437 | 20320 E14-GRCH 115 20326 LIBERTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 440 | 20322 WDRMAN T 115 20394 E15-EUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.7 | 1240.5 | 1350 | 91.7 | 446 | 20327 E14-LIBR 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 447 | 20329 RAMSEUR 69.0 20330 I-RAMTEX 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 460 | 20346 RKH 115 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 474 | 20351 I-CORDVA 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 476 | 20354 I-ROCKY 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 493 | 20367 LONGST T 230 20386 CLIFFDAL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.3 | 1240.5 | 1350 | 91.7 | 514 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.3 | 1240.5 | 1350 | 91.7 | 515 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 524 | 20392 FAY 115 20407 E15-BEAR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 530 | 20401 VANDER 115 20502 I-VANDAK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 536 | 20407 E15-BEAR 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.6 | 1240.5 | 1350 | 91.7 | 538 | 20408 BEARD 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.2 | 1240.5 | 1350 | 91.7 | 549 | 20419 WAGRAMSW 115 20426 I-STV&GU 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 562 | 20430 RED SPRG 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.2 | 1240.5 | 1350 | 91.7 | 578 | 20451 PA-GRNVL 230 20474 DUP KIN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.3 | 1240.5 | 1350 | 91.7 | 587 | 20461 E16-SLVR 230 20462 BAYBORO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 588 | 20461 E16-SLVR 230 20463 NB WEST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.4 | 1240.5 | 1350 | 91.7 | 589 | 20463 NB WEST 230 20465 NEW BERN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 590 | 20464 BRIDGETN 115 20466 NEW BERN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238 | 1240.5 | 1350 | 91.7 | 607 | 20474 DUP KIN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.2 | 1240.5 | 1350 | 91.7 | 608 | 20475 WEYER T 115 20476 ICG-WYHS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 633 | 20499 E2-MAYVL 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 660 | 20519 M-TARAWA 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 662 | 20519 M-TARAWA 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 668 | 20524 JACKSONV 230 20540 GEI&SW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 680 | 20540 GEI&SW T 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238 | 1240.5 | 1350 | 91.7 | 681 | 20541 M-GEIGER 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.4 | 1240.5 | 1350 | 91.7 | 688 | 20549 TOPSAIL 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.7 | 1240.5 | 1350 | 91.7 | 690 | 20550 CSTL HYN 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 696 | 20556 TOPSL T 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 728 | 20585 WH IND T 115 20586 I-GAPCWH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.1 | 1240.5 | 1350 | 91.7 | 734 | 20588 CHADBN T 115 20589 CHADBORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1240.5 | 1350 | 91.7 | 736 | 20590 TABOR T 115 20596 TABOR C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.6 | 1240.5 | 1350 | 91.7 | 745 | 20613 E1-SO WH 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 810 | 20686 SUMTER 115 20687 EASTOV T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 814 | 20687 EASTOV T 115 20689 I-SUMIND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.5 | 1240.5 | 1350 | 91.7 | 830 | 20709 HARTSN T 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.5 | 1240.5 | 1350 | 91.7 | 831 | 20709 HARTSN T 115 20717 I-SONOCO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.9 | 1240.5 | 1350 | 91.7 | 835 | 20713 JEFFSN T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.3 | 1240.5 | 1350 | 91.7 | 836 | 20713 JEFFSN T 115 20720 PAGELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.5 | 1240.5 | 1350 | 91.7 | 841 | 20721 BETHNE T 115 20722 BETHUNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 101 | 20039 SUT 3 F 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.9 | 1240.5 | 1350 | 91.8 | 106 | 20041 CF 5-6 F 230 20368 DEEPRV T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.6 | 1240.5 | 1350 | 91.8 | 125 | 20052 CAPE F F 115 20295 I-HONEYW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.2 | 1240.5 | 1350 | 91.8 | 131 | 20058 HOLLYSPG 230 20133 BELLS LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 178 | 20094 YANCY T 230 20095 YANCYVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 218 | 20132 RAL SO 115 20158 GUILML T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.2 | 1240.5 | 1350 | 91.8 | 220 | 20134 MONCURE 115 20158 GUILML T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 261 | 20166 ZEBULON 69.0 20167 E18-EMIT 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 262 | 20166 ZEBULON 69.0 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 285 | 20193 FOUR OAK 230 20194 BENSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 286 | 20194 BENSON 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.8 | 1240.5 | 1350 | 91.8 | 287 | 20195 I-BENPGI 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 342 | 20237 E9-W ONS 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 343 | 20237 E9-W ONS 230 20521 CATHRNLK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 354 | 20247 GA PAC T 230 20249 I-GA PAC 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 371 | 20261 LEE 115 20264 E+GAS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 434 | 20318 E14-SPER 115 20353 I-UN&TIE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 456 | 20341 MT GILED 115 20442 I-MG IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 461 | 20346 RKH 115 20348 RKH 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 491 | 20367 LONGST T 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.2 | 1240.5 | 1350 | 91.8 | 508 | 20380 M-FBKNOX 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 525 | 20393 SLOCUMB 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.8 | 1240.5 | 1350 | 91.8 | 537 | 20408 BEARD 115 20409 E15-WADE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 544 | 20411 RAEFORD 115 20425 RED SP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 583 | 20454 AURORA 230 20461 E16-SLVR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 593 | 20465 NEW BERN 230 20471 CCWDCG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.4 | 1240.5 | 1350 | 91.8 | 603 | 20471 CCWDCG T 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.9 | 1240.5 | 1350 | 91.8 | 619 | 20484 HAVELOCK 230 20499 E2-MAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.7 | 1240.5 | 1350 | 91.8 | 652 | 20514 I-OXYCHM 115 20533 ID/OCC T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.9 | 1240.5 | 1350 | 91.8 | 654 | 20515 WALLACE 230 20516 I-BASF 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.9 | 1240.5 | 1350 | 91.8 | 657 | 20516 I-BASF 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.8 | 1240.5 | 1350 | 91.8 | 663 | 20520 I-KOSA 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 665 | 20524 JACKSONV 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1240.5 | 1350 | 91.8 | 717 | 20573 E4-POWEL 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.2 | 1240.5 | 1350 | 91.8 | 723 | 20581 WHITEVIL 115 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.1 | 1240.5 | 1350 | 91.8 | 806 | 20680 MANNIG T 115 20685 MANNING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239.1 | 1240.5 | 1350 | 91.8 | 820 | 20695 SHAW AFB 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.9 | 1240.5 | 1350 | 91.8 | 848 | 20725 CAMDEN 115 20731 I-DUP CA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.5 | 1240.5 | 1350 | 91.9 |  | ** Base Case **
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242 | 1240.5 | 1350 | 92 | 13 | FALLS-HONEYCUT230_&_FALLS-LAKESTON115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 14 | FALLS-LAKESTON115_&_CHSTNTHL-NEUSE115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.8 | 1240.5 | 1350 | 92 | 18 | MILB-CLAYTON115_&_MILB-PERSTP115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 23 | BISCOEW-BISCOESUB115_&_SPRINGT-I_FNDRY_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.1 | 1240.5 | 1350 | 92 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 44 | LEE-CLINTON230_&_LEE-FRIENDSHIP_T_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 52 | 20004 TIL 1-4H 115 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.2 | 1240.5 | 1350 | 92 | 53 | 20004 TIL 1-4H 115 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 67 | 20018 ROB 2 N 230 20666 NUCOR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.8 | 1240.5 | 1350 | 92 | 68 | 20018 ROB 2 N 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 74 | 20020 BRUN 2 N 230 20615 BARNARD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 109 | 20044 ROB 1 F 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 115 | 20047 WSP BUS 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.6 | 1240.5 | 1350 | 92 | 121 | 20050 PA-GRN W 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.6 | 1240.5 | 1350 | 92 | 128 | 20057 DARL CO 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.6 | 1240.5 | 1350 | 92 | 132 | 20059 E18-KITT 115 20089 HENDERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 133 | 20059 E18-KITT 115 20096 YOUNGSVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 156 | 20077 SIX FORK 230 20083 HONEYCUT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.6 | 1240.5 | 1350 | 92 | 161 | 20082 I-NCCENT 230 20125 CARALEIG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 162 | 20083 HONEYCUT 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 163 | 20084 I-NOVO 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242 | 1240.5 | 1350 | 92 | 164 | 20084 I-NOVO 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 166 | 20086 E12-HYCO 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 167 | 20086 E12-HYCO 115 20093 CONCORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 174 | 20090 E12-ROX 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 177 | 20093 CONCORD 115 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.6 | 1240.5 | 1350 | 92 | 180 | 20096 YOUNGSVL 115 20141 WF T NC2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.6 | 1240.5 | 1350 | 92 | 184 | 20100 HEND N T 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 189 | 20108 LOUISBRG 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 202 | 20120 CARY TAP 230 20173 TRI FRST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.1 | 1240.5 | 1350 | 92 | 206 | 20124 METHOD 230 20129 OAKDAL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 209 | 20125 CARALEIG 230 20130 EAST ST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 240 | 20151 WHITEOAK 230 20186 EDMONDSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 257 | 20163 MILBURNE 115 20170 CLAYTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 291 | 20196 ERWIN 230 20215 BUIES CK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 299 | 20202 ERWINSUB 115 20208 ERWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.6 | 1240.5 | 1350 | 92 | 307 | 20205 CLINTON 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.2 | 1240.5 | 1350 | 92 | 315 | 20213 FUQUAY 230 20214 ANGIER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 316 | 20214 ANGIER 230 20215 BUIES CK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.8 | 1240.5 | 1350 | 92 | 404 | 20292 E14-ETHR 115 20294 BISCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.6 | 1240.5 | 1350 | 92 | 405 | 20292 E14-ETHR 115 20303 SEAGROVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.2 | 1240.5 | 1350 | 92 | 406 | 20294 BISCOSUB 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 475 | 20352 BURLCR T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 507 | 20379 M-FBMAIN 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.8 | 1240.5 | 1350 | 92 | 575 | 20448 FAIRMONT 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.5 | 1240.5 | 1350 | 92 | 594 | 20465 NEW BERN 230 20484 HAVELOCK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 595 | 20465 NEW BERN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 596 | 20465 NEW BERN 230 20506 DOVER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 634 | 20500 WOMMACK 230 20506 DOVER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 640 | 20505 ROSE HIL 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.8 | 1240.5 | 1350 | 92 | 715 | 20571 ELIZAB T 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 725 | 20582 DELCO 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.9 | 1240.5 | 1350 | 92 | 735 | 20588 CHADBN T 115 20590 TABOR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 737 | 20590 TABOR T 115 20597 E1-CHRYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.5 | 1240.5 | 1350 | 92 | 738 | 20597 E1-CHRYG 115 20598 FAIR B T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1240.5 | 1350 | 92 | 761 | 20632 MARION 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.1 | 1240.5 | 1350 | 92 | 770 | 20641 I-STONE 115 20642 DELTA T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.1 | 1240.5 | 1350 | 92 | 772 | 20642 DELTA T 115 20644 PAMPLICO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1240.5 | 1350 | 92 | 779 | 20655 FLOR SO 115 20656 I-ESAB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.5 | 1240.5 | 1350 | 92 | 780 | 20656 I-ESAB 115 20657 GE TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.6 | 1240.5 | 1350 | 92 | 782 | 20657 GE TAP 115 20659 FLORENCE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.5 | 1240.5 | 1350 | 92 | 862 | 44702 3KERR 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.6 | 1240.5 | 1350 | 92 | 875 | 43005 6DARLING 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.5 | 1240.5 | 1350 | 92 | 877 | 42003 3EASTOVE 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.3 | 1240.5 | 1350 | 92 | 883 | 2511 BADIN 100 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.2 | 1240.5 | 1350 | 92 | 884 | 2511 BADIN 100 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.7 | 1240.5 | 1350 | 92.1 | 9 | METH-NCCENT230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.5 | 1240.5 | 1350 | 92.1 | 10 | NCCENT-CARALI230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.5 | 1240.5 | 1350 | 92.1 | 45 | WILSON-PA_WILSON#1_115KV_PODS
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.2 | 1240.5 | 1350 | 92.1 | 57 | 20009 HARRIS1N 230 20204 DUNCAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.9 | 1240.5 | 1350 | 92.1 | 60 | 20009 HARRIS1N 230 20338 E15-BRDW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.7 | 1240.5 | 1350 | 92.1 | 73 | 20020 BRUN 2 N 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.8 | 1240.5 | 1350 | 92.1 | 111 | 20046 WSPN BUS 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.2 | 1240.5 | 1350 | 92.1 | 120 | 20050 PA-GRN W 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243 | 1240.5 | 1350 | 92.1 | 155 | 20077 SIX FORK 230 20078 WD VALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.9 | 1240.5 | 1350 | 92.1 | 157 | 20078 WD VALLY 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.8 | 1240.5 | 1350 | 92.1 | 160 | 20082 I-NCCENT 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.3 | 1240.5 | 1350 | 92.1 | 179 | 20094 YANCY T 230 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.4 | 1240.5 | 1350 | 92.1 | 199 | 20119 PRISON F 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.9 | 1240.5 | 1350 | 92.1 | 201 | 20120 CARY TAP 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.4 | 1240.5 | 1350 | 92.1 | 239 | 20151 WHITEOAK 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244 | 1240.5 | 1350 | 92.1 | 253 | 20162 MILBURNE 230 20178 AUBURN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.3 | 1240.5 | 1350 | 92.1 | 271 | 20178 AUBURN 230 20179 WILS MIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.8 | 1240.5 | 1350 | 92.1 | 272 | 20179 WILS MIL 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.8 | 1240.5 | 1350 | 92.1 | 302 | 20204 DUNCAN 230 20213 FUQUAY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.7 | 1240.5 | 1350 | 92.1 | 325 | 20222 ROCKY MT 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.9 | 1240.5 | 1350 | 92.1 | 330 | 20228 WILSON 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.9 | 1240.5 | 1350 | 92.1 | 386 | 20274 EKRN+CGK 115 20310 E17-SARE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.1 | 1240.5 | 1350 | 92.1 | 454 | 20338 E15-BRDW 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244 | 1240.5 | 1350 | 92.1 | 577 | 20451 PA-GRNVL 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.2 | 1240.5 | 1350 | 92.1 | 579 | 20453 PA-WASH 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.7 | 1240.5 | 1350 | 92.1 | 740 | 20598 FAIR B T 115 20629 NICHOLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.4 | 1240.5 | 1350 | 92.1 | 755 | 20629 NICHOLS 115 20630 MULLINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243 | 1240.5 | 1350 | 92.1 | 764 | 20633 INDST T 115 20635 I-DUP FL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243 | 1240.5 | 1350 | 92.1 | 765 | 20633 INDST T 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.3 | 1240.5 | 1350 | 92.1 | 767 | 20635 I-DUP FL 115 20641 I-STONE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.9 | 1240.5 | 1350 | 92.1 | 773 | 20644 PAMPLICO 115 20645 HEMINGWA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.8 | 1240.5 | 1350 | 92.1 | 774 | 20645 HEMINGWA 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.9 | 1240.5 | 1350 | 92.1 | 826 | 20703 SUMTER N 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.8 | 1240.5 | 1350 | 92.1 | 855 | 52577 05EDANV1 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.7 | 1240.5 | 1350 | 92.1 | 858 | 44697 6HALIFAX 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.9 | 1240.5 | 1350 | 92.1 | 873 | 43007 3HEMING1 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.4 | 1240.5 | 1350 | 92.2 | 147 | 20067 MAYOSUSW 230 20068 RXBOWMAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.4 | 1240.5 | 1350 | 92.2 | 148 | 20067 MAYOSUSW 230 20088 HENDERSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.9 | 1240.5 | 1350 | 92.2 | 149 | 20068 RXBOWMAN 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244 | 1240.5 | 1350 | 92.2 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.2 | 1240.5 | 1350 | 92.2 | 196 | 20117 DURHAM 230 20118 RDU AIRP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.5 | 1240.5 | 1350 | 92.2 | 197 | 20118 RDU AIRP 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.1 | 1240.5 | 1350 | 92.2 | 198 | 20119 PRISON F 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.8 | 1240.5 | 1350 | 92.2 | 210 | 20126 MORRISVI 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.1 | 1240.5 | 1350 | 92.2 | 278 | 20188 PA-SELMA 230 20192 SELMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.2 | 1240.5 | 1350 | 92.2 | 279 | 20188 PA-SELMA 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.6 | 1240.5 | 1350 | 92.2 | 281 | 20190 WAKE 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.8 | 1240.5 | 1350 | 92.2 | 422 | 20310 E17-SARE 115 20605 CG-KORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.7 | 1240.5 | 1350 | 92.2 | 756 | 20630 MULLINS 115 20632 MARION 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.2 | 1240.5 | 1350 | 92.2 | 762 | 20632 MARION 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.3 | 1240.5 | 1350 | 92.2 | 822 | 20699 SUMMER T 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.1 | 1240.5 | 1350 | 92.2 | 861 | 52578 05EDANV2 230 20094 YANCY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1244.9 | 1240.5 | 1350 | 92.2 | 878 | 42001 6SANTEE 230 20699 SUMMER T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.5 | 1240.5 | 1350 | 92.3 | 70 | 20018 ROB 2 N 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.4 | 1240.5 | 1350 | 92.3 | 211 | 20126 MORRISVI 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.8 | 1240.5 | 1350 | 92.3 | 250 | 20161 FOXCROFT 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.6 | 1240.5 | 1350 | 92.3 | 254 | 20162 MILBURNE 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.7 | 1240.5 | 1350 | 92.3 | 719 | 20578 CG-ELIZ 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.7 | 1240.5 | 1350 | 92.3 | 742 | 20601 CG-SOPRT 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.1 | 1240.5 | 1350 | 92.3 | 809 | 20684 ALICE DR 230 20703 SUMTER N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.3 | 1240.5 | 1350 | 92.3 | 825 | 20700 SUMTER 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.7 | 1240.5 | 1350 | 92.4 | 175 | 20091 BRIERCK 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247 | 1240.5 | 1350 | 92.4 | 176 | 20091 BRIERCK 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.2 | 1240.5 | 1350 | 92.4 | 249 | 20160 PINE LK 230 20161 FOXCROFT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.8 | 1240.5 | 1350 | 92.4 | 602 | 20471 CCWDCG T 230 20472 CG-CC WD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.9 | 1240.5 | 1350 | 92.4 | 808 | 20684 ALICE DR 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248 | 1240.5 | 1350 | 92.4 | 832 | 20710 HARTS T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.5 | 1240.5 | 1350 | 92.4 | 856 | 43014 6S BETH 230 20057 DARL CO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.4 | 1240.5 | 1350 | 92.4 | 870 | 44574 6EVERETS 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.5 | 1240.5 | 1350 | 92.5 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.2 | 1240.5 | 1350 | 92.5 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.1 | 1240.5 | 1350 | 92.5 | 19 | MILB-WHITEOAK230_&_MILB-AUBURN230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.5 | 1240.5 | 1350 | 92.5 | 21 | TILLERY-BADIN1&2_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249 | 1240.5 | 1350 | 92.5 | 46 | RKYMT-NASH230_&_RKYMT-EDGCMB230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.3 | 1240.5 | 1350 | 92.5 | 62 | 20015 MAYO 1F 500 20071 PERSON 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.3 | 1240.5 | 1350 | 92.5 | 152 | 3Wnd: OPEN B$0011 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.3 | 1240.5 | 1350 | 92.5 | 168 | 20087 HEND E 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.6 | 1240.5 | 1350 | 92.5 | 357 | 20248 I-ANSONV 230 20358 BOWMAN T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.6 | 1240.5 | 1350 | 92.5 | 482 | 20358 BOWMAN T 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.3 | 1240.5 | 1350 | 92.5 | 866 | 44591 6NASH 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.3 | 1240.5 | 1350 | 92.5 | 868 | 542 6OAKBORO 230 20248 I-ANSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.9 | 1240.5 | 1350 | 92.5 | 882 | 542 6OAKBORO 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.4 | 1240.5 | 1350 | 92.6 | 36 | SUMT-WDGFLD230_&_GOLDT-KNGHWY115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.4 | 1240.5 | 1350 | 92.6 | 37 | SUMT-WDGFLD230_&_SUMT-GOLDT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.5 | 1240.5 | 1350 | 92.6 | 47 | GRNVL-CHOCWNTY230_&_GRNVL-EVERETT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1249.9 | 1240.5 | 1350 | 92.6 | 247 | 20157 HOMESTED 230 20160 PINE LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.6 | 1240.5 | 1350 | 92.6 | 777 | 20653 CASHUA 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.5 | 1240.5 | 1350 | 92.6 | 824 | 20700 SUMTER 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.3 | 1240.5 | 1350 | 92.7 | 85 | 20024 ROX 1-4F 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.9 | 1240.5 | 1350 | 92.7 | 107 | 20044 ROB 1 F 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.8 | 1240.5 | 1350 | 92.7 | 151 | 20070 PERSON 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.6 | 1240.5 | 1350 | 92.7 | 165 | 20085 OXFORD N 230 20087 HEND E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1252.6 | 1240.5 | 1350 | 92.8 | 20 | MILB-FALLS230_&_MILB-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1253.4 | 1240.5 | 1350 | 92.8 | 146 | 20066 FALLS23 230 20157 HOMESTED 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1252.9 | 1240.5 | 1350 | 92.8 | 413 | 20301 TROY 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1252.4 | 1240.5 | 1350 | 92.8 | 778 | 20653 CASHUA 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1252.9 | 1240.5 | 1350 | 92.8 | 788 | 20662 FLORENCE 230 20663 LATTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1254.1 | 1240.5 | 1350 | 92.9 | 16 | FALLS-MILB230_&_PINELK-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1254.6 | 1240.5 | 1350 | 92.9 | 145 | 20066 FALLS23 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1253.8 | 1240.5 | 1350 | 92.9 | 159 | 20079 OXF S T 230 20085 OXFORD N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1254.7 | 1240.5 | 1350 | 92.9 | 414 | 20301 TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1253.8 | 1240.5 | 1350 | 92.9 | 798 | 20671 SARDIS 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1254.8 | 1240.5 | 1350 | 92.9 | 799 | 20671 SARDIS 230 20674 OLANTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255.5 | 1240.5 | 1350 | 93 | 1 | ROX-EDANVL230_&_CONCORD-YANCYVLT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255.5 | 1240.5 | 1350 | 93 | 150 | 20070 PERSON 230 20079 OXF S T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255 | 1240.5 | 1350 | 93 | 732 | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255.6 | 1240.5 | 1350 | 93 | 800 | 20674 OLANTA 230 20675 LAKE CTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1256.3 | 1240.5 | 1350 | 93.1 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.2 | 1240.5 | 1350 | 93.1 | 15 | FALLS-MILB230_&_HOMESTED-PINELK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.2 | 1240.5 | 1350 | 93.1 | 39 | MARION-MARION(SCPSA)230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.2 | 1240.5 | 1350 | 93.1 | 50 | 20004 TIL 1-4H 115 20302 E14-TROY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1256.8 | 1240.5 | 1350 | 93.1 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1256.8 | 1240.5 | 1350 | 93.1 | 154 | 20073 BLUE RDG 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1256.2 | 1240.5 | 1350 | 93.1 | 415 | 20302 E14-TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.5 | 1240.5 | 1350 | 93.1 | 557 | 20424 LAURINBG 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.3 | 1240.5 | 1350 | 93.1 | 801 | 20675 LAKE CTY 230 20676 KINGST N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.6 | 1240.5 | 1350 | 93.2 | 2 | ROX-EDANVLN230_&_YANCYVLT-EDANVL230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1258 | 1240.5 | 1350 | 93.2 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.8 | 1240.5 | 1350 | 93.2 | 733 | 20587 E1-CHADP 230 20631 MARION 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1258.9 | 1240.5 | 1350 | 93.2 | 876 | 43008 6KNGSTRE 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1259.8 | 1240.5 | 1350 | 93.3 | 153 | 20073 BLUE RDG 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1259.2 | 1240.5 | 1350 | 93.3 | 802 | 20676 KINGST N 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1259.6 | 1240.5 | 1350 | 93.3 | 828 | 20706 BENETSVL 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1260.9 | 1240.5 | 1350 | 93.4 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1261.2 | 1240.5 | 1350 | 93.4 | 17 | FALLS-MILB230_&_FALLS23-HOMESTED230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1260.6 | 1240.5 | 1350 | 93.4 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1261.2 | 1240.5 | 1350 | 93.4 | 879 | 42002 6WATEREE 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1261.6 | 1240.5 | 1350 | 93.5 | 471 | 20348 RKH 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1263.1 | 1240.5 | 1350 | 93.6 | 860 | 845 6E.DURHM 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1265.3 | 1240.5 | 1350 | 93.7 | 6 | ROX-FALLS230_&_PER-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1265.8 | 1240.5 | 1350 | 93.8 | 827 | 20705 SOCTY HL 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1267.2 | 1240.5 | 1350 | 93.9 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1267.1 | 1240.5 | 1350 | 93.9 | 795 | 20668 I-TALLY 230 20705 SOCTY HL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1267.4 | 1240.5 | 1350 | 93.9 | 863 | 845 6E.DURHM 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1268.3 | 1240.5 | 1350 | 94 | 5 | ROX-FALLS230_&_FALLS23-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1269.1 | 1240.5 | 1350 | 94 | 126 | 20054 DURHAM 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1268.5 | 1240.5 | 1350 | 94 | 129 | 20057 DARL CO 230 20668 I-TALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.8 | 1240.5 | 1350 | 94.1 | 465 | 20348 RKH 230 20349 PH SH 2W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.9 | 1240.5 | 1350 | 94.1 | 466 | 20348 RKH 230 20350 PH SH 1B 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.8 | 1240.5 | 1350 | 94.1 | 472 | 20349 PH SH 2W 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1270.9 | 1240.5 | 1350 | 94.1 | 473 | 20350 PH SH 1B 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1272.2 | 1240.5 | 1350 | 94.2 | 69 | 20018 ROB 2 N 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1274.4 | 1240.5 | 1350 | 94.4 | 31 | BOWMANT-IANSON230_&_ANSON-OAKBORO230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1274.3 | 1240.5 | 1350 | 94.4 | 34 | ANSON-OAKBORO230_&_ANSON-BOWMANT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1275.7 | 1240.5 | 1350 | 94.5 | 32 | OAKBORO-ANSON230_&_OAKBORO-IANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1275.2 | 1240.5 | 1350 | 94.5 | 35 | ROB-NUCOR230_&_ROB-REIDPK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1286.4 | 1240.5 | 1350 | 95.3 | 864 | 44902 8CARSON 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1299.9 | 1240.5 | 1350 | 96.3 | 61 | 20015 MAYO 1F 500 20054 DURHAM 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1388.1 | 1240.5 | 1350 | 102.8 | 33 | PHSH1-ANSON230_&_PHSH2-ANSON230
20185 FALLS 115 20182 FALLS 230 1 | TR | 270.3 | 209.7 | 300 | 90.1 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20185 FALLS 115 20182 FALLS 230 1 | TR | 278.5 | 209.7 | 300 | 92.8 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20185 FALLS 115 20182 FALLS 230 1 | TR | 305.1 | 209.7 | 300 | 101.7 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20182 FALLS 230 1 | TR | 310.1 | 209.7 | 300 | 103.4 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 159.7 | 71.4 | 170 | 94 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20168 YONKERS 115 20163 MILBURNE 115 1 | LN | 172.5 | 52.3 | 190 | 90.8 | 223 | 20137 METHOD 115 20150 I-NCSU S 115 1
20155 CHSTNT H 115 20163 MILBURNE 115 1 | LN | 148 | 21.3 | 158 | 93.7 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20039 SUT 3 F 230 20554 9THORG T 230 1 | LN | 593.5 | 299.4 | 590 | 100.6 | 41 | BR1-BARCK230_&_BR2-BARCRK230
Note on A18: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C18: PTI: Contingency MVA for Tran and Amp for Lines
Note on D18: PTI: Base Case Flow
Note on E18: PTI: Branch Rating
Note on F18: PTI: Loading in %
Note on G18: PTI: Contingency index
Note on H18: PTI: Contingency Description

## 3200 MW HR DN BRANCH
Branch Violations
MUST 8.0.2 -- Managing and Utilizing System Transmission -- WED, APR 26 2006 11:01
2011 PEC-PWG SUMMER PEAK BASE CASE - UPDATED 03/03/06
SERC/VST 2010S CASE FROM 2005 SERIES REL 6/05, HAR DN TRM
Case.File J:\NC Stakeholders\2011S Study\Study Cases\TRMcases\duk11s_PEC_FinalNP-HarDnTRM.sav
Subsys.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.sub
Monit.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\East.mon
Contin.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-EAST SYSTEM ONLY--COMBINED--2011S.CON
Exclud.File J:\NC Stakeholders\2011S Study\CaseDataToDuke\PWG-Eastern System.EXC
************** Report on violations ********************
Branches with MVA flow more than 90.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Ncon | Contingency
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | LN | 256.6 | 154.5 | 269 | 95.4 | 464 | 20347 ABRDN RD 230 20348 RKH 230 1
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | LN | 249.3 | 154.5 | 269 | 92.7 | 420 | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20039 SUT 3 F 230 20554 9THORG T 230 1 | LN | 614.8 | 230.3 | 590 | 104.2 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20155 CHSTNT H 115 20163 MILBURNE 115 1 | LN | 148.7 | 22 | 158 | 94.1 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20168 YONKERS 115 20163 MILBURNE 115 1 | LN | 173.3 | 63.7 | 190 | 91.2 | 223 | 20137 METHOD 115 20150 I-NCSU S 115 1
20185 FALLS 115 20111 E18-WK F 115 1 | LN | 155.2 | 65.8 | 170 | 91.3 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20185 FALLS 115 20182 FALLS 230 1 | TR | 312.2 | 209.4 | 300 | 104.1 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | TR | 307.2 | 209.4 | 300 | 102.4 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20182 FALLS 230 1 | TR | 277.6 | 209.4 | 300 | 92.5 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20290 I-OLVRRB 115 20304 E14-ULAH 115 1 | LN | 127.8 | 57.4 | 138 | 92.6 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20304 E14-ULAH 115 20303 SEAGROVE 115 1 | LN | 149.4 | 78.2 | 148 | 100.9 | 419 | 20309 BISCOE W 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1367.3 | 1221.9 | 1350 | 101.3 | 33 | PHSH1-ANSON230_&_PHSH2-ANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1282 | 1221.9 | 1350 | 95 | 61 | 20015 MAYO 1F 500 20054 DURHAM 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1271.9 | 1221.9 | 1350 | 94.2 | 864 | 44902 8CARSON 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1260 | 1221.9 | 1350 | 93.3 | 35 | ROB-NUCOR230_&_ROB-REIDPK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1257.1 | 1221.9 | 1350 | 93.1 | 69 | 20018 ROB 2 N 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1255.3 | 1221.9 | 1350 | 93 | 32 | OAKBORO-ANSON230_&_OAKBORO-IANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1253.9 | 1221.9 | 1350 | 92.9 | 31 | BOWMANT-IANSON230_&_ANSON-OAKBORO230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1253.9 | 1221.9 | 1350 | 92.9 | 34 | ANSON-OAKBORO230_&_ANSON-BOWMANT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1252.8 | 1221.9 | 1350 | 92.8 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.8 | 1221.9 | 1350 | 92.7 | 465 | 20348 RKH 230 20349 PH SH 2W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.9 | 1221.9 | 1350 | 92.7 | 466 | 20348 RKH 230 20350 PH SH 1B 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.8 | 1221.9 | 1350 | 92.7 | 472 | 20349 PH SH 2W 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.9 | 1221.9 | 1350 | 92.7 | 473 | 20350 PH SH 1B 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1251.3 | 1221.9 | 1350 | 92.7 | 863 | 845 6E.DURHM 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1250.4 | 1221.9 | 1350 | 92.6 | 5 | ROX-FALLS230_&_FALLS23-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1248.9 | 1221.9 | 1350 | 92.5 | 129 | 20057 DARL CO 230 20668 I-TALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.3 | 1221.9 | 1350 | 92.4 | 6 | ROX-FALLS230_&_PER-CGROX230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247.4 | 1221.9 | 1350 | 92.4 | 795 | 20668 I-TALLY 230 20705 SOCTY HL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1247 | 1221.9 | 1350 | 92.4 | 860 | 845 6E.DURHM 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.6 | 1221.9 | 1350 | 92.3 | 471 | 20348 RKH 230 20698 REIDPK T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1246.2 | 1221.9 | 1350 | 92.3 | 827 | 20705 SOCTY HL 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1245.2 | 1221.9 | 1350 | 92.2 | 126 | 20054 DURHAM 500 20183 WAKE 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1243.6 | 1221.9 | 1350 | 92.1 | 153 | 20073 BLUE RDG 230 20076 LEESVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.7 | 1221.9 | 1350 | 92 | 4 | PER-RXBOWMAN230_&_PER-OXFORDST230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.4 | 1221.9 | 1350 | 92 | 17 | FALLS-MILB230_&_FALLS23-HOMESTED230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.5 | 1221.9 | 1350 | 92 | 828 | 20706 BENETSVL 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1242.1 | 1221.9 | 1350 | 92 | 879 | 42002 6WATEREE 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.7 | 1221.9 | 1350 | 91.9 | 2 | ROX-EDANVLN230_&_YANCYVLT-EDANVL230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1241.2 | 1221.9 | 1350 | 91.9 | 50 | 20004 TIL 1-4H 115 20302 E14-TROY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.6 | 1221.9 | 1350 | 91.9 | 154 | 20073 BLUE RDG 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.2 | 1221.9 | 1350 | 91.9 | 415 | 20302 E14-TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.5 | 1221.9 | 1350 | 91.9 | 557 | 20424 LAURINBG 230 20707 MCCOLL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240.2 | 1221.9 | 1350 | 91.9 | 802 | 20676 KINGST N 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1240 | 1221.9 | 1350 | 91.9 | 876 | 43008 6KNGSTRE 230 20677 KINGSTRE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.6 | 1221.9 | 1350 | 91.8 | 414 | 20301 TROY 115 20683 BURNETTE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1239 | 1221.9 | 1350 | 91.8 | 791 | 20663 LATTA 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.6 | 1221.9 | 1350 | 91.7 | 1 | ROX-EDANVL230_&_CONCORD-YANCYVLT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1221.9 | 1350 | 91.7 | 15 | FALLS-MILB230_&_HOMESTED-PINELK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1238.4 | 1221.9 | 1350 | 91.7 | 801 | 20675 LAKE CTY 230 20676 KINGST N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1237.2 | 1221.9 | 1350 | 91.6 | 3 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.2 | 1221.9 | 1350 | 91.6 | 39 | MARION-MARION(SCPSA)230_1&2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.3 | 1221.9 | 1350 | 91.6 | 145 | 20066 FALLS23 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.3 | 1221.9 | 1350 | 91.6 | 150 | 20070 PERSON 230 20079 OXF S T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.8 | 1221.9 | 1350 | 91.6 | 413 | 20301 TROY 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.1 | 1221.9 | 1350 | 91.6 | 733 | 20587 E1-CHADP 230 20631 MARION 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1236.7 | 1221.9 | 1350 | 91.6 | 800 | 20674 OLANTA 230 20675 LAKE CTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.4 | 1221.9 | 1350 | 91.5 | 16 | FALLS-MILB230_&_PINELK-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235 | 1221.9 | 1350 | 91.5 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.3 | 1221.9 | 1350 | 91.5 | 113 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235 | 1221.9 | 1350 | 91.5 | 146 | 20066 FALLS23 230 20157 HOMESTED 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.7 | 1221.9 | 1350 | 91.5 | 159 | 20079 OXF S T 230 20085 OXFORD N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1234.9 | 1221.9 | 1350 | 91.5 | 798 | 20671 SARDIS 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1235.9 | 1221.9 | 1350 | 91.5 | 799 | 20671 SARDIS 230 20674 OLANTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.8 | 1221.9 | 1350 | 91.4 | 20 | MILB-FALLS230_&_MILB-FOXCROFT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.5 | 1221.9 | 1350 | 91.4 | 151 | 20070 PERSON 230 20097 CG-ROX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.3 | 1221.9 | 1350 | 91.4 | 732 | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.5 | 1221.9 | 1350 | 91.4 | 778 | 20653 CASHUA 230 20673 EBENEZER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.1 | 1221.9 | 1350 | 91.3 | 21 | TILLERY-BADIN1&2_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233.1 | 1221.9 | 1350 | 91.3 | 85 | 20024 ROX 1-4F 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1233 | 1221.9 | 1350 | 91.3 | 107 | 20044 ROB 1 F 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.5 | 1221.9 | 1350 | 91.3 | 165 | 20085 OXFORD N 230 20087 HEND E 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1232.7 | 1221.9 | 1350 | 91.3 | 788 | 20662 FLORENCE 230 20663 LATTA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.6 | 1221.9 | 1350 | 91.2 | 36 | SUMT-WDGFLD230_&_GOLDT-KNGHWY115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.6 | 1221.9 | 1350 | 91.2 | 37 | SUMT-WDGFLD230_&_SUMT-GOLDT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.6 | 1221.9 | 1350 | 91.2 | 62 | 20015 MAYO 1F 500 20071 PERSON 500 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.6 | 1221.9 | 1350 | 91.2 | 152 | 3Wnd: OPEN B$0011 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.3 | 1221.9 | 1350 | 91.2 | 175 | 20091 BRIERCK 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.6 | 1221.9 | 1350 | 91.2 | 176 | 20091 BRIERCK 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.5 | 1221.9 | 1350 | 91.2 | 247 | 20157 HOMESTED 230 20160 PINE LK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.7 | 1221.9 | 1350 | 91.2 | 777 | 20653 CASHUA 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1231.7 | 1221.9 | 1350 | 91.2 | 824 | 20700 SUMTER 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.6 | 1221.9 | 1350 | 91.2 | 866 | 44591 6NASH 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.3 | 1221.9 | 1350 | 91.1 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.9 | 1221.9 | 1350 | 91.1 | 8 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.5 | 1221.9 | 1350 | 91.1 | 46 | RKYMT-NASH230_&_RKYMT-EDGCMB230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.3 | 1221.9 | 1350 | 91.1 | 168 | 20087 HEND E 230 20222 ROCKY MT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230 | 1221.9 | 1350 | 91.1 | 211 | 20126 MORRISVI 230 20159 RTP 23KV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.6 | 1221.9 | 1350 | 91.1 | 357 | 20248 I-ANSONV 230 20358 BOWMAN T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.6 | 1221.9 | 1350 | 91.1 | 482 | 20358 BOWMAN T 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.1 | 1221.9 | 1350 | 91.1 | 832 | 20710 HARTS T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1230.3 | 1221.9 | 1350 | 91.1 | 868 | 542 6OAKBORO 230 20248 I-ANSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.9 | 1221.9 | 1350 | 91.1 | 882 | 542 6OAKBORO 230 20985 ANSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.6 | 1221.9 | 1350 | 91 | 47 | GRNVL-CHOCWNTY230_&_GRNVL-EVERETT230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228 | 1221.9 | 1350 | 91 | 111 | 20046 WSPN BUS 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228 | 1221.9 | 1350 | 91 | 205 | 20122 REGNCYPK 230 20211 APEX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.1 | 1221.9 | 1350 | 91 | 206 | 20124 METHOD 230 20129 OAKDAL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.3 | 1221.9 | 1350 | 91 | 210 | 20126 MORRISVI 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.8 | 1221.9 | 1350 | 91 | 249 | 20160 PINE LK 230 20161 FOXCROFT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.2 | 1221.9 | 1350 | 91 | 602 | 20471 CCWDCG T 230 20472 CG-CC WD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1229.1 | 1221.9 | 1350 | 91 | 808 | 20684 ALICE DR 230 20702 WEDGEFLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1228.4 | 1221.9 | 1350 | 91 | 856 | 43014 6S BETH 230 20057 DARL CO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.8 | 1221.9 | 1350 | 90.9 | 19 | MILB-WHITEOAK230_&_MILB-AUBURN230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.6 | 1221.9 | 1350 | 90.9 | 70 | 20018 ROB 2 N 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.2 | 1221.9 | 1350 | 90.9 | 196 | 20117 DURHAM 230 20118 RDU AIRP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.5 | 1221.9 | 1350 | 90.9 | 197 | 20118 RDU AIRP 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.3 | 1221.9 | 1350 | 90.9 | 214 | 20129 OAKDAL T 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.5 | 1221.9 | 1350 | 90.9 | 250 | 20161 FOXCROFT 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.7 | 1221.9 | 1350 | 90.9 | 254 | 20162 MILBURNE 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.1 | 1221.9 | 1350 | 90.9 | 719 | 20578 CG-ELIZ 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.7 | 1221.9 | 1350 | 90.9 | 742 | 20601 CG-SOPRT 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.3 | 1221.9 | 1350 | 90.9 | 809 | 20684 ALICE DR 230 20703 SUMTER N 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.4 | 1221.9 | 1350 | 90.9 | 825 | 20700 SUMTER 230 20728 ELLIOT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1227.3 | 1221.9 | 1350 | 90.9 | 870 | 44574 6EVERETS 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.8 | 1221.9 | 1350 | 90.8 | 147 | 20067 MAYOSUSW 230 20068 RXBOWMAN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.9 | 1221.9 | 1350 | 90.8 | 148 | 20067 MAYOSUSW 230 20088 HENDERSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.3 | 1221.9 | 1350 | 90.8 | 149 | 20068 RXBOWMAN 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.5 | 1221.9 | 1350 | 90.8 | 173 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.2 | 1221.9 | 1350 | 90.8 | 198 | 20119 PRISON F 230 20123 TRENTON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.4 | 1221.9 | 1350 | 90.8 | 199 | 20119 PRISON F 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.4 | 1221.9 | 1350 | 90.8 | 201 | 20120 CARY TAP 230 20128 EVANS RD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.5 | 1221.9 | 1350 | 90.8 | 203 | 20122 REGNCYPK 230 20136 PINEY PL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.4 | 1221.9 | 1350 | 90.8 | 386 | 20274 EKRN+CGK 115 20310 E17-SARE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.2 | 1221.9 | 1350 | 90.8 | 422 | 20310 E17-SARE 115 20605 CG-KORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.4 | 1221.9 | 1350 | 90.8 | 717 | 20573 E4-POWEL 230 20600 WHITEVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.7 | 1221.9 | 1350 | 90.8 | 756 | 20630 MULLINS 115 20632 MARION 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.3 | 1221.9 | 1350 | 90.8 | 762 | 20632 MARION 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.1 | 1221.9 | 1350 | 90.8 | 774 | 20645 HEMINGWA 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.7 | 1221.9 | 1350 | 90.8 | 822 | 20699 SUMMER T 230 20700 SUMTER 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.6 | 1221.9 | 1350 | 90.8 | 855 | 52577 05EDANV1 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.4 | 1221.9 | 1350 | 90.8 | 858 | 44697 6HALIFAX 230 20070 PERSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.9 | 1221.9 | 1350 | 90.8 | 861 | 52578 05EDANV2 230 20094 YANCY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.2 | 1221.9 | 1350 | 90.8 | 873 | 43007 3HEMING1 115 20646 I-TPERWR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1226.3 | 1221.9 | 1350 | 90.8 | 878 | 42001 6SANTEE 230 20699 SUMMER T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.7 | 9 | METH-NCCENT230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224 | 1221.9 | 1350 | 90.7 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224 | 1221.9 | 1350 | 90.7 | 23 | BISCOEW-BISCOESUB115_&_SPRINGT-I_FNDRY_115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.6 | 1221.9 | 1350 | 90.7 | 45 | WILSON-PA_WILSON#1_115KV_PODS
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.5 | 1221.9 | 1350 | 90.7 | 52 | 20004 TIL 1-4H 115 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.3 | 1221.9 | 1350 | 90.7 | 53 | 20004 TIL 1-4H 115 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.6 | 1221.9 | 1350 | 90.7 | 115 | 20047 WSP BUS 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.9 | 1221.9 | 1350 | 90.7 | 120 | 20050 PA-GRN W 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 132 | 20059 E18-KITT 115 20089 HENDERSN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.9 | 1221.9 | 1350 | 90.7 | 133 | 20059 E18-KITT 115 20096 YOUNGSVL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 155 | 20077 SIX FORK 230 20078 WD VALLY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225 | 1221.9 | 1350 | 90.7 | 157 | 20078 WD VALLY 230 20117 DURHAM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.9 | 1221.9 | 1350 | 90.7 | 167 | 20086 E12-HYCO 115 20093 CONCORD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.1 | 1221.9 | 1350 | 90.7 | 179 | 20094 YANCY T 230 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225 | 1221.9 | 1350 | 90.7 | 202 | 20120 CARY TAP 230 20173 TRI FRST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.3 | 1221.9 | 1350 | 90.7 | 226 | 20140 PANTH BR 230 20190 WAKE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.7 | 234 | 20145 NEUSE 115 20185 FALLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.8 | 1221.9 | 1350 | 90.7 | 239 | 20151 WHITEOAK 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.1 | 1221.9 | 1350 | 90.7 | 253 | 20162 MILBURNE 230 20178 AUBURN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.6 | 1221.9 | 1350 | 90.7 | 278 | 20188 PA-SELMA 230 20192 SELMA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.8 | 1221.9 | 1350 | 90.7 | 279 | 20188 PA-SELMA 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1225.1 | 1221.9 | 1350 | 90.7 | 281 | 20190 WAKE 230 20199 ARCHLDGE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.9 | 1221.9 | 1350 | 90.7 | 325 | 20222 ROCKY MT 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.6 | 1221.9 | 1350 | 90.7 | 330 | 20228 WILSON 230 20229 FARMVILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.9 | 1221.9 | 1350 | 90.7 | 406 | 20294 BISCOSUB 115 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.4 | 1221.9 | 1350 | 90.7 | 475 | 20352 BURLCR T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 577 | 20451 PA-GRNVL 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.7 | 726 | 20582 DELCO 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.4 | 1221.9 | 1350 | 90.7 | 755 | 20629 NICHOLS 115 20630 MULLINS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 764 | 20633 INDST T 115 20635 I-DUP FL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 765 | 20633 INDST T 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.7 | 1221.9 | 1350 | 90.7 | 767 | 20635 I-DUP FL 115 20641 I-STONE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.2 | 1221.9 | 1350 | 90.7 | 773 | 20644 PAMPLICO 115 20645 HEMINGWA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.9 | 1221.9 | 1350 | 90.7 | 780 | 20656 I-ESAB 115 20657 GE TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224 | 1221.9 | 1350 | 90.7 | 782 | 20657 GE TAP 115 20659 FLORENCE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.1 | 1221.9 | 1350 | 90.7 | 826 | 20703 SUMTER N 230 20704 BISHOPVI 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224 | 1221.9 | 1350 | 90.7 | 862 | 44702 3KERR 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.5 | 1221.9 | 1350 | 90.7 | 883 | 2511 BADIN 100 20342 BADIN #1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1224.3 | 1221.9 | 1350 | 90.7 | 884 | 2511 BADIN 100 20343 BADIN #2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.6 | 1221.9 | 1350 | 90.6 | 10 | NCCENT-CARALI230_&_RAL-NCSU115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 12 | METH-TRYONHL115_&_METH-RALSO115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.3 | 1221.9 | 1350 | 90.6 | 13 | FALLS-HONEYCUT230_&_FALLS-LAKESTON115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 14 | FALLS-LAKESTON115_&_CHSTNTHL-NEUSE115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 18 | MILB-CLAYTON115_&_MILB-PERSTP115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.6 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1221.9 | 1350 | 90.6 | 68 | 20018 ROB 2 N 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 72 | 20020 BRUN 2 N 230 20603 E1-PROSP 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.6 | 1221.9 | 1350 | 90.6 | 73 | 20020 BRUN 2 N 230 20604 E1-STHPT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 77 | 20022 BRUN 1 N 230 20610 SO-ADM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 109 | 20044 ROB 1 F 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 121 | 20050 PA-GRN W 230 20451 PA-GRNVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 128 | 20057 DARL CO 230 20662 FLORENCE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.6 | 1221.9 | 1350 | 90.6 | 140 | 20062 E4-TARHE 230 20573 E4-POWEL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 156 | 20077 SIX FORK 230 20083 HONEYCUT 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 160 | 20082 I-NCCENT 230 20124 METHOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 162 | 20083 HONEYCUT 230 20182 FALLS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.7 | 1221.9 | 1350 | 90.6 | 163 | 20084 I-NOVO 115 20105 FRANKLIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.3 | 1221.9 | 1350 | 90.6 | 164 | 20084 I-NOVO 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.6 | 166 | 20086 E12-HYCO 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 174 | 20090 E12-ROX 115 20092 ROXBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.7 | 1221.9 | 1350 | 90.6 | 177 | 20093 CONCORD 115 20098 CONCORD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1221.9 | 1350 | 90.6 | 180 | 20096 YOUNGSVL 115 20141 WF T NC2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 184 | 20100 HEND N T 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 189 | 20108 LOUISBRG 115 20112 E18-LSBG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 217 | 20132 RAL SO 115 20137 METHOD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 219 | 20133 BELLS LK 230 20140 PANTH BR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.7 | 1221.9 | 1350 | 90.6 | 240 | 20151 WHITEOAK 230 20186 EDMONDSN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 257 | 20163 MILBURNE 115 20170 CLAYTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.7 | 1221.9 | 1350 | 90.6 | 266 | 20173 TRI FRST 230 20210 APEXPOD4 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 271 | 20178 AUBURN 230 20179 WILS MIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 272 | 20179 WILS MIL 230 20251 LEE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1222.9 | 1221.9 | 1350 | 90.6 | 305 | 20205 CLINTON 230 20255 CLINTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 404 | 20292 E14-ETHR 115 20294 BISCOSUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 405 | 20292 E14-ETHR 115 20303 SEAGROVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 416 | 20303 SEAGROVE 115 20304 E14-ULAH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1221.9 | 1350 | 90.6 | 462 | 20346 RKH 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.2 | 1221.9 | 1350 | 90.6 | 561 | 20429 E10-RENN 115 20432 PA-LMB#2 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 575 | 20448 FAIRMONT 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 579 | 20453 PA-WASH 230 20457 CHOCWNTY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 594 | 20465 NEW BERN 230 20484 HAVELOCK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.6 | 1221.9 | 1350 | 90.6 | 671 | 20532 E4-KELLY 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.1 | 1221.9 | 1350 | 90.6 | 715 | 20571 ELIZAB T 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 737 | 20590 TABOR T 115 20597 E1-CHRYG 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 738 | 20597 E1-CHRYG 115 20598 FAIR B T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.7 | 1221.9 | 1350 | 90.6 | 740 | 20598 FAIR B T 115 20629 NICHOLS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.5 | 1221.9 | 1350 | 90.6 | 770 | 20641 I-STONE 115 20642 DELTA T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.4 | 1221.9 | 1350 | 90.6 | 772 | 20642 DELTA T 115 20644 PAMPLICO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223.8 | 1221.9 | 1350 | 90.6 | 779 | 20655 FLOR SO 115 20656 I-ESAB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 875 | 43005 6DARLING 230 20672 SEGARS M 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1223 | 1221.9 | 1350 | 90.6 | 877 | 42003 3EASTOVE 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1221.9 | 1221.9 | 1350 | 90.5 |  | ** Base Case **
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.8 | 1221.9 | 1350 | 90.4 | 71 | 20020 BRUN 2 N 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.2 | 1221.9 | 1350 | 90.4 | 101 | 20039 SUT 3 F 230 20582 DELCO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.2 | 1221.9 | 1350 | 90.4 | 122 | 20052 CAPE F F 115 20134 MONCURE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.1 | 1221.9 | 1350 | 90.4 | 125 | 20052 CAPE F F 115 20295 I-HONEYW 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.5 | 1221.9 | 1350 | 90.4 | 178 | 20094 YANCY T 230 20095 YANCYVIL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.6 | 1221.9 | 1350 | 90.4 | 216 | 20131 WORTHDAL 230 20162 MILBURNE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.2 | 1221.9 | 1350 | 90.4 | 261 | 20166 ZEBULON 69.0 20167 E18-EMIT 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.2 | 1221.9 | 1350 | 90.4 | 262 | 20166 ZEBULON 69.0 20201 ZEBULON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 268 | 20175 SMITHF T 115 20177 SELMA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 286 | 20194 BENSON 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 287 | 20195 I-BENPGI 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.7 | 1221.9 | 1350 | 90.4 | 292 | 20196 ERWIN 230 20217 BENPGI T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.7 | 1221.9 | 1350 | 90.4 | 300 | 20202 ERWINSUB 115 20209 ERWIN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.7 | 1221.9 | 1350 | 90.4 | 313 | 20209 ERWIN T 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.9 | 1221.9 | 1350 | 90.4 | 326 | 20224 PA-WRE-T 115 20225 PA-W-RE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.8 | 1221.9 | 1350 | 90.4 | 342 | 20237 E9-W ONS 230 20515 WALLACE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.8 | 1221.9 | 1350 | 90.4 | 343 | 20237 E9-W ONS 230 20521 CATHRNLK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.4 | 1221.9 | 1350 | 90.4 | 354 | 20247 GA PAC T 230 20249 I-GA PAC 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 368 | 20258 CLINTN N 115 20259 E15-HALL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 371 | 20261 LEE 115 20264 E+GAS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.2 | 1221.9 | 1350 | 90.4 | 410 | 20299 SC HWY64 230 20332 ASHEB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.7 | 1221.9 | 1350 | 90.4 | 411 | 20299 SC HWY64 230 20340 SILER C 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.5 | 1221.9 | 1350 | 90.4 | 434 | 20318 E14-SPER 115 20353 I-UN&TIE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.1 | 1221.9 | 1350 | 90.4 | 447 | 20329 RAMSEUR 69.0 20330 I-RAMTEX 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.1 | 1221.9 | 1350 | 90.4 | 456 | 20341 MT GILED 115 20442 I-MG IND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220 | 1221.9 | 1350 | 90.4 | 460 | 20346 RKH 115 20348 RKH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.8 | 1221.9 | 1350 | 90.4 | 461 | 20346 RKH 115 20348 RKH 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.8 | 1221.9 | 1350 | 90.4 | 474 | 20351 I-CORDVA 115 20352 BURLCR T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 507 | 20379 M-FBMAIN 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.5 | 1221.9 | 1350 | 90.4 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.5 | 1221.9 | 1350 | 90.4 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.4 | 1221.9 | 1350 | 90.4 | 525 | 20393 SLOCUMB 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.4 | 1221.9 | 1350 | 90.4 | 539 | 20409 E15-WADE 115 20410 GODWIN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.9 | 1221.9 | 1350 | 90.4 | 583 | 20454 AURORA 230 20461 E16-SLVR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 584 | 20454 AURORA 230 20467 E16-EDWD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.8 | 1221.9 | 1350 | 90.4 | 608 | 20475 WEYER T 115 20476 ICG-WYHS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.8 | 1221.9 | 1350 | 90.4 | 619 | 20484 HAVELOCK 230 20499 E2-MAYVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 640 | 20505 ROSE HIL 230 20518 WARSAW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220 | 1221.9 | 1350 | 90.4 | 641 | 20505 ROSE HIL 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 652 | 20514 I-OXYCHM 115 20533 ID/OCC T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 664 | 20521 CATHRNLK 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 682 | 20543 E9-FOLKS 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.9 | 1221.9 | 1350 | 90.4 | 684 | 20544 HOLLY RG 115 20545 CASTLE H 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.8 | 1221.9 | 1350 | 90.4 | 685 | 20544 HOLLY RG 115 20546 E9-TOPSL 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.9 | 1221.9 | 1350 | 90.4 | 728 | 20585 WH IND T 115 20586 I-GAPCWH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.9 | 1221.9 | 1350 | 90.4 | 736 | 20590 TABOR T 115 20596 TABOR C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.1 | 1221.9 | 1350 | 90.4 | 745 | 20613 E1-SO WH 115 20623 WHTV SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.6 | 1221.9 | 1350 | 90.4 | 806 | 20680 MANNIG T 115 20685 MANNING 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220 | 1221.9 | 1350 | 90.4 | 810 | 20686 SUMTER 115 20687 EASTOV T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220 | 1221.9 | 1350 | 90.4 | 814 | 20687 EASTOV T 115 20689 I-SUMIND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.6 | 1221.9 | 1350 | 90.4 | 820 | 20695 SHAW AFB 115 20696 SHAW TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220 | 1221.9 | 1350 | 90.4 | 841 | 20721 BETHNE T 115 20722 BETHUNE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1220.3 | 1221.9 | 1350 | 90.4 | 848 | 20725 CAMDEN 115 20731 I-DUP CA 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 26 | FAYE-FBWOOD230_&_SLOC_TAP-SLOCUMB115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 51 | 20004 TIL 1-4H 115 20341 MT GILED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 96 | 20035 SUT 1-2F 115 20557 I-GE WLM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.9 | 1221.9 | 1350 | 90.3 | 99 | 20039 SUT 3 F 230 20520 I-KOSA 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 108 | 20044 ROB 1 F 115 20721 BETHNE T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 112 | 20046 WSPN BUS 230 20446 WSPN SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.9 | 1221.9 | 1350 | 90.3 | 142 | 20064 E6-WARTN 115 20102 WARREN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.4 | 1221.9 | 1350 | 90.3 | 143 | 20064 E6-WARTN 115 20103 WARRENTN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 158 | 20079 OXF S T 230 20080 OXFORD S 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 230 | 20142 ATLANTIC 115 20144 AVX TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.8 | 1221.9 | 1350 | 90.3 | 264 | 20171 AMBERLY 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.8 | 1221.9 | 1350 | 90.3 | 295 | 20198 BAILEY 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 311 | 20207 NEWTON G 230 20218 NEWTGR T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.7 | 1221.9 | 1350 | 90.3 | 347 | 20238 BLACK CK 115 20293 W-3TOWNS 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.4 | 1221.9 | 1350 | 90.3 | 353 | 20246 HEMLOCK 115 20261 LEE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 369 | 20259 E15-HALL 115 20260 ROSEBORO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.6 | 1221.9 | 1350 | 90.3 | 380 | 20269 MTOLVSUB 115 20270 MT OLV W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 408 | 20296 CANDOR T 115 20306 CANDOR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.4 | 1221.9 | 1350 | 90.3 | 433 | 20318 E14-SPER 115 20324 SPERO T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 437 | 20320 E14-GRCH 115 20326 LIBERTY 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.4 | 1221.9 | 1350 | 90.3 | 440 | 20322 WDRMAN T 115 20394 E15-EUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 446 | 20327 E14-LIBR 115 20328 RAMSEUR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.5 | 1221.9 | 1350 | 90.3 | 506 | 20379 M-FBMAIN 230 20380 M-FBKNOX 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 519 | 20390 CUMBERLD 230 20584 GARLAND 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 524 | 20392 FAY 115 20407 E15-BEAR 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.6 | 1221.9 | 1350 | 90.3 | 530 | 20401 VANDER 115 20502 I-VANDAK 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.9 | 1221.9 | 1350 | 90.3 | 536 | 20407 E15-BEAR 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 537 | 20408 BEARD 115 20409 E15-WADE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 538 | 20408 BEARD 115 20427 SLOC TAP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.7 | 1221.9 | 1350 | 90.3 | 549 | 20419 WAGRAMSW 115 20426 I-STV&GU 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.4 | 1221.9 | 1350 | 90.3 | 562 | 20430 RED SPRG 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.8 | 1221.9 | 1350 | 90.3 | 578 | 20451 PA-GRNVL 230 20474 DUP KIN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.9 | 1221.9 | 1350 | 90.3 | 587 | 20461 E16-SLVR 230 20462 BAYBORO 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.9 | 1221.9 | 1350 | 90.3 | 588 | 20461 E16-SLVR 230 20463 NB WEST 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 590 | 20464 BRIDGETN 115 20466 NEW BERN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.5 | 1221.9 | 1350 | 90.3 | 593 | 20465 NEW BERN 230 20471 CCWDCG T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.1 | 1221.9 | 1350 | 90.3 | 603 | 20471 CCWDCG T 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 607 | 20474 DUP KIN 230 20500 WOMMACK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.4 | 1221.9 | 1350 | 90.3 | 620 | 20485 HAVELOCK 115 20486 M-CH PT1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.5 | 1221.9 | 1350 | 90.3 | 633 | 20499 E2-MAYVL 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 637 | 20501 SCOTT HL 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 654 | 20515 WALLACE 230 20516 I-BASF 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 656 | 20515 WALLACE 230 20551 E4-BEVRG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 657 | 20516 I-BASF 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 660 | 20519 M-TARAWA 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 662 | 20519 M-TARAWA 230 20527 SWANSBOR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 663 | 20520 I-KOSA 230 20534 I-PRXR W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.8 | 1221.9 | 1350 | 90.3 | 665 | 20524 JACKSONV 230 20528 RHEMS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.2 | 1221.9 | 1350 | 90.3 | 668 | 20524 JACKSONV 230 20540 GEI&SW T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 680 | 20540 GEI&SW T 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.6 | 1221.9 | 1350 | 90.3 | 681 | 20541 M-GEIGER 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 688 | 20549 TOPSAIL 230 20556 TOPSL T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.5 | 1221.9 | 1350 | 90.3 | 690 | 20550 CSTL HYN 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.6 | 1221.9 | 1350 | 90.3 | 696 | 20556 TOPSL T 230 20564 SCOTT T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.6 | 1221.9 | 1350 | 90.3 | 734 | 20588 CHADBN T 115 20589 CHADBORN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 830 | 20709 HARTSN T 115 20710 HARTS T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219 | 1221.9 | 1350 | 90.3 | 831 | 20709 HARTSN T 115 20717 I-SONOCO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.3 | 1221.9 | 1350 | 90.3 | 835 | 20713 JEFFSN T 115 20718 CHESTRFD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1219.7 | 1221.9 | 1350 | 90.3 | 836 | 20713 JEFFSN T 115 20720 PAGELAND 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.7 | 1221.9 | 1350 | 90.3 | 840 | 20718 CHESTRFD 115 20719 CHERAW E 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218 | 1221.9 | 1350 | 90.2 | 76 | 20022 BRUN 1 N 230 20354 I-ROCKY 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.4 | 1221.9 | 1350 | 90.2 | 138 | 20061 APEX US1 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.2 | 1221.9 | 1350 | 90.2 | 183 | 20100 HEND N T 115 20101 HEND NO 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 186 | 20106 WAKEFORE 115 20107 E18-WEMC 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 187 | 20106 WAKEFORE 115 20113 WF T NC1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 336 | 20231 GC/LEE T 115 20233 GOLDSB C 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 337 | 20231 GC/LEE T 115 20239 GOLD C T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.2 | 1221.9 | 1350 | 90.2 | 370 | 20260 ROSEBORO 115 20265 E15-STED 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.6 | 1221.9 | 1350 | 90.2 | 377 | 20265 E15-STED 115 20401 VANDER 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.5 | 1221.9 | 1350 | 90.2 | 424 | 20312 ASHEB E 115 20320 E14-GRCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.2 | 1221.9 | 1350 | 90.2 | 426 | 20313 ASHEBW T 115 20317 ASHEB W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 476 | 20354 I-ROCKY 230 20524 JACKSONV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.2 | 1221.9 | 1350 | 90.2 | 486 | 20362 WEST END 115 20363 PINEHRST 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.5 | 1221.9 | 1350 | 90.2 | 491 | 20367 LONGST T 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.8 | 1221.9 | 1350 | 90.2 | 508 | 20380 M-FBKNOX 230 20382 BON DOON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.6 | 1221.9 | 1350 | 90.2 | 514 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.6 | 1221.9 | 1350 | 90.2 | 515 | 20387 P1-FAY 0 230 20390 CUMBERLD 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.1 | 1221.9 | 1350 | 90.2 | 547 | 20416 MAXAPT T 115 20420 MAXT APT 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.1 | 1221.9 | 1350 | 90.2 | 567 | 20436 PEMBROKE 115 20441 E10-PEMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.7 | 1221.9 | 1350 | 90.2 | 570 | 20439 LUMBERTN 115 20606 CG-LUMB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.9 | 1221.9 | 1350 | 90.2 | 573 | 20446 WSPN SUB 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.9 | 1221.9 | 1350 | 90.2 | 589 | 20463 NB WEST 230 20465 NEW BERN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.8 | 1221.9 | 1350 | 90.2 | 628 | 20493 ATL BCH 115 20531 E2-ATL B 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 716 | 20572 ELIZABTN 115 20602 ELZ CG T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 744 | 20611 SOUTH+PA 230 20612 I-ADM 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.1 | 1221.9 | 1350 | 90.2 | 783 | 20659 FLORENCE 115 20661 MT HOPE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217.4 | 1221.9 | 1350 | 90.2 | 787 | 20660 DARLINGT 115 20669 DARLN T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1218.1 | 1221.9 | 1350 | 90.2 | 792 | 20664 DILLN MP 230 20667 DILN NTH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.9 | 1221.9 | 1350 | 90.1 | 25 | FAY-FAYE230_&_FAY-WSP230
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.5 | 1221.9 | 1350 | 90.1 | 49 | 20001 BLEWETT 115 20345 RKH W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 58 | 20009 HARRIS1N 230 20212 NEW HILL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.7 | 1221.9 | 1350 | 90.1 | 60 | 20009 HARRIS1N 230 20338 E15-BRDW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.9 | 1221.9 | 1350 | 90.1 | 136 | 20061 APEX US1 230 20065 APEX US1 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.9 | 1221.9 | 1350 | 90.1 | 144 | 20065 APEX US1 115 20180 GREEN LV 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217 | 1221.9 | 1350 | 90.1 | 228 | 20141 WF T NC2 115 20607 PA-WF 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217 | 1221.9 | 1350 | 90.1 | 243 | 20154 ROLESVIL 230 20156 ROL/SQ T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216 | 1221.9 | 1350 | 90.1 | 267 | 20175 SMITHF T 115 20176 PA-SMFLD 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 297 | 20200 ZEBULON 230 20203 BAILEY T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.5 | 1221.9 | 1350 | 90.1 | 301 | 20203 BAILEY T 230 20228 WILSON 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.3 | 1221.9 | 1350 | 90.1 | 374 | 20262 E17-MT O 115 20278 MT OLIVE 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.9 | 1221.9 | 1350 | 90.1 | 421 | 20309 BISCOE W 230 20428 BISCOE W 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.8 | 1221.9 | 1350 | 90.1 | 451 | 20334 BYNUM 230 20337 BYNUM T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216 | 1221.9 | 1350 | 90.1 | 454 | 20338 E15-BRDW 230 20398 M-FBWOOD 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217 | 1221.9 | 1350 | 90.1 | 458 | 20344 WADESBOR 230 20359 BOWMNSCH 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 492 | 20367 LONGST T 230 20384 M-FBLONG 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.6 | 1221.9 | 1350 | 90.1 | 493 | 20367 LONGST T 230 20386 CLIFFDAL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.7 | 1221.9 | 1350 | 90.1 | 495 | 20368 DEEPRV T 230 20376 DEEP RIV 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.6 | 1221.9 | 1350 | 90.1 | 509 | 20381 RAEF SO 115 20413 RAEF SUB 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.8 | 1221.9 | 1350 | 90.1 | 528 | 20400 E15-MAN 115 20460 E3-MANCH 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.2 | 1221.9 | 1350 | 90.1 | 556 | 20424 LAURINBG 230 20444 ROWLND T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.4 | 1221.9 | 1350 | 90.1 | 572 | 20444 ROWLND T 230 20450 PA-LMB#3 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.8 | 1221.9 | 1350 | 90.1 | 576 | 20449 DILLON 115 20654 DILLON T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 581 | 20454 AURORA 230 20455 I-PCS 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.7 | 1221.9 | 1350 | 90.1 | 644 | 20508 PA-KINST 115 20529 KINSTON 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217 | 1221.9 | 1350 | 90.1 | 649 | 20512 WALL SUB 115 20548 E4-WALL 69.0 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 659 | 20518 WARSAW T 230 20522 WARSAW 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.4 | 1221.9 | 1350 | 90.1 | 678 | 20538 E9-PINYG 115 20539 E9-HARMN 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.8 | 1221.9 | 1350 | 90.1 | 679 | 20540 GEI&SW T 230 20542 E9-SO W 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1217 | 1221.9 | 1350 | 90.1 | 775 | 20647 MAR BYPS 115 20650 MARBYP T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.7 | 1221.9 | 1350 | 90.1 | 837 | 20715 HARTSVIL 115 20727 ROB-FL T 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.4 | 1221.9 | 1350 | 90.1 | 847 | 20725 CAMDEN 115 20730 CAMDEN 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1216.1 | 1221.9 | 1350 | 90.1 | 880 | 43059 6BENNETT 230 20706 BENETSVL 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.3 | 1221.9 | 1350 | 90 | 116 | 20047 WSP BUS 115 20440 E10-WLUM 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.5 | 1221.9 | 1350 | 90 | 200 | 20120 CARY TAP 230 20121 CARY SUB 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.2 | 1221.9 | 1350 | 90 | 213 | 20129 OAKDAL T 230 20135 OAKDALE 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1214.9 | 1221.9 | 1350 | 90 | 477 | 20355 HAMLET 230 20387 P1-FAY 0 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.4 | 1221.9 | 1350 | 90 | 511 | 20386 CLIFFDAL 230 20388 P3-FAYRR 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.7 | 1221.9 | 1350 | 90 | 559 | 20425 RED SP T 115 20445 E10-RDSP 115 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.4 | 1221.9 | 1350 | 90 | 669 | 20525 M-LEJN#1 230 20526 M-LEJN#2 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.2 | 1221.9 | 1350 | 90 | 727 | 20584 GARLAND 230 20591 E4-YORK 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.3 | 1221.9 | 1350 | 90 | 793 | 20664 DILLN MP 230 20682 DILLMP T 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.1 | 1221.9 | 1350 | 90 | 853 | 844 6ENO 230 20024 ROX 1-4F 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.1 | 1221.9 | 1350 | 90 | 854 | 844 6ENO 230 20024 ROX 1-4F 230 2
20377 RICHMOND 500 337 8NEWPORT 500 1 | LN | 1215.3 | 1221.9 | 1350 | 90 | 881 | 43010 6LUGOFF 230 20730 CAMDEN 230 1
20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | LN | 620.6 | 452.7 | 637 | 97.4 | 513 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | LN | 596.8 | 452.7 | 637 | 93.7 | 25 | FAY-FAYE230_&_FAY-WSP230
20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | LN | 590.5 | 307.6 | 637 | 92.7 | 512 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20387 P1-FAY 0 230 20392 FAY 115 1 | TR | 180.3 | 106.8 | 200 | 90.2 | 517 | 20387 P1-FAY 0 230 20392 FAY 115 2
20387 P1-FAY 0 230 20392 FAY 115 2 | TR | 180.2 | 106.5 | 200 | 90.1 | 516 | 20387 P1-FAY 0 230 20392 FAY 115 1
20421 LAURINBG 115 20424 LAURINBG 230 1 | TR | 198.9 | 109.8 | 200 | 99.5 | 551 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20421 LAURINBG 115 20424 LAURINBG 230 2 | TR | 198.7 | 109.1 | 200 | 99.3 | 550 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20552 E WILM 230 20554 9THORG T 230 1 | LN | 565.6 | 179 | 590 | 95.9 | 41 | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | TR | 142.9 | 142.9 | 150 | 95.2 |  | ** Base Case **
20683 BURNETTE 115 20302 E14-TROY 115 1 | LN | 248.7 | 146.7 | 269 | 92.5 | 464 | 20347 ABRDN RD 230 20348 RKH 230 1
B$0024 1.00 20183 WAKE 500 1 | TR | 955.2 | 616.4 | 1000 | 95.5 | 276 | 3Wnd: OPEN B$0045 2
B$0024 1.00 20190 WAKE 230 1 | TR | 932.5 | 607.4 | 1000 | 93.3 | 276 | 3Wnd: OPEN B$0045 2
B$0045 1.00 20183 WAKE 500 2 | TR | 954.9 | 616 | 1000 | 95.5 | 275 | 3Wnd: OPEN B$0024 1
B$0045 1.00 20190 WAKE 230 2 | TR | 932.2 | 606.9 | 1000 | 93.2 | 275 | 3Wnd: OPEN B$0024 1
Note on A18: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C18: PTI: Contingency MVA for Tran and Amp for Lines
Note on D18: PTI: Base Case Flow
Note on E18: PTI: Branch Rating
Note on F18: PTI: Loading in %
Note on G18: PTI: Contingency index
Note on H18: PTI: Contingency Description