Project Name: London Creek 230 kV Lines

Project Description

Increase capacity of line to alleviate congestion.

| Projected In-Service Date 2015 - 2016 |  |
| --- | --- |

| Estimated Cost |  |
| --- | --- |

Narrative Description of the Need for this Project

The London Creek Lines will achieve 100% of their conductor rating in the 2015-2016 timeframe. The lines are most heavily loaded when there is a Oconee unit outage for the loss of the parallel line. The line is sensitive to south to north transfers. Increased import from SOCO lowers loading on the London Creek lines.

Transmission Solutions Considered

Bundle the line Reactors

Why this Project was Selected as the Preferred Solution