## Branch Violations
Branches with MVA flow more than 90.0 % of nominal rating |  | Base 3600MW Import |  | DK TRM + 600MW Import |  | SCEG TRM + 600MW Import |  | SCPSA TRM + 600MW Import |  | VAP TRM + 600MW Import |  | SOCO TRM + 600MW Import |  | TVA TRM + 600MW Import |  | AEP TRM + 600MW Import
** From bus ** ** To bus ** CKT | Rating | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | HR DN | BR1 DN | Contingency
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | 269 | 96.5 | 83.1 | 105.6 | 91.6 | 104.4 | 90.1 | 103.7 |  | 100.4 |  | 104.3 |  | 103.9 |  | 102.6 |  | 20347 ABRDN RD 230 20348 RKH 230 1
20004 TIL 1-4H 115 20302 E14-TROY 115 1 | 269 | 93.7 | 80.5 | 102.8 |  | 101.5 |  | 100.9 |  | 97.6 |  | 101.5 |  | 101 |  | 99.7 |  | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20039 SUT 3 F 230 20554 9THORG T 230 1 | 590 | 106.1 | 101.7 | 106.6 | 102.3 | 107.3 | 102.8 | 107.3 | 103 | 105.8 | 101.7 | 106.9 | 102.5 | 106.7 | 102.4 | 106.4 | 102.2 | BR1-BARCK230_&_BR2-BARCRK230
20039 SUT 3 F 230 20582 DELCO 230 1 | 478 | 88.5 | 68.1 | 98.9 |  | 102 |  | 102 | 90.3 | 96.7 |  | 100.6 |  | 99.9 |  | 98.6 |  | BR1-BARCK230_&_BR2-BARCRK230
20047 WSP BUS 115 20406 ST PAULS 115 1 | 119 | 82.4 | 67.2 |  |  | 91.6 |  | 93.1 | [9 empty] | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
20047 WSP BUS 115 20406 ST PAULS 115 1 | 119 | 81.5 | 66.3 |  |  | 90.6 |  | 92.1 | [9 empty] | FAY-ROCKFISH230_&_FAY-HAMLET230
20066 FALLS23 230 20097 CG-ROX 230 1 | 423 | 86.8 | 85.9 | 94.8 | 93.8 | 93.2 | 92 | 92.6 |  | 93 | 91.9 | 93.9 | 92.8 | 94.1 | 93 | 94.6 | 93.4 | 20015 MAYO 1F 500 20054 DURHAM 500 1
20073 BLUE RDG 230 20124 METHOD 230 1 | 637 | 78.8 | 70.4 | 95.1 |  |  |  |  | 91.4 | [8 empty] | 845 6E.DURHM 230 20117 DURHAM 230 1
20076 LEESVILL 230 845 6E.DURHM 230 1 | 745 | 81.6 | 74.3 | 95.8 | [13 empty] | 845 6E.DURHM 230 20117 DURHAM 230 1
20089 HENDERSN 115 20105 FRANKLIN 115 1 | 201 | 86 | 87.3 |  | 91 |  | 90.3 |  | 90.1 |  |  |  | 90.5 |  | 90.5 |  | 90.5 | 20111 E18-WK F 115 20185 FALLS 115 1
20091 BRIERCK 230 10117 DURHAM 230 1 |  | 93.2 | 74.9 | 106.2 |  | 99.3 |  | 99.3 |  | 100.2 |  | 100.3 |  | 100.6 |  | 101 |  | METHOD-PRISONF230_&_METHOD-BLUERDG230
20091 BRIERCK 230 10159 RTP 23KV 230 1 |  | 88.7 | 70.5 | 98.3 |  | 94.8 |  | 94.8 |  | 95.7 |  | 95.8 |  | 96.1 |  | 96.5 |  | METHOD-PRISONF230_&_METHOD-BLUERDG230
20126 MORRISVI 230 20159 RTP 23KV 1 |  | 84.6 | 66.5 | 94.1 |  | 90.6 |  | 90.6 |  | 91.5 |  | 91.6 |  | 91.9 |  | 92.3
20137 METHOD 115 20124 METHOD 230 1 | 300 | 78.7 | 85 |  | 90 | [12 empty] | 20124 METHOD 230 20137 METHOD 115 2
20137 METHOD 115 20124 METHOD 230 2 | 300 | 78.8 | 85.1 |  | 90.1 | [12 empty] | 20124 METHOD 230 20137 METHOD 115 1
20137 METHOD 115 20150 I-NCSU S 115 1 | 190 | 89.3 | 88.7 | 90.3 |  | 90.4 |  | 90.3 |  |  |  | 90.6 |  | 90.3 |  | 90.6 |  | 20163 MILBURNE 115 20168 YONKERS 115 1
20155 CHSTNT H 115 20163 MILBURNE 115 1 | 158 | 94.3 | 93.9 | 95.6 | 95.2 | 95.7 | 95.2 | 95.6 | 95.1 | 95.2 | 94.8 | 95.7 | 95.2 | 95.6 | 95.2 | 95.5 | 95.1 | 20145 NEUSE 115 20185 FALLS 115 1
20168 YONKERS 115 20163 MILBURNE 115 1 | 190 | 91.3 | 91 | 92.5 | 92.2 | 92.6 | 92.2 | 92.5 | 92.1 | 92.2 | 91.8 | 92.6 | 92.2 | 92.5 | 92.1 | 92.4 | 92.1 | 20137 METHOD 115 20150 I-NCSU S 115 1
20185 FALLS 115 20111 E18-WK F 115 1 | 170 | 92 | 94.7 | 94.7 | 97.6 | 94.2 | 97.1 | 94 | 97 | 92.2 | 95 | 94 | 97 | 93.9 | 96.9 | 93.6 | 96.5 | 20089 HENDERSN 115 20105 FRANKLIN 115 1
20185 FALLS 115 20111 E18-WK F 115 1 | 170 | 87.8 | 90.6 | 90.3 | 93.3 |  | 92.8 |  | 92.7 |  | 90.7 |  | 92.7 |  | 92.6 |  | 92.2 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20111 E18-WK F 115 1 | 170 | 87.5 | 90.3 | 90 | 93 |  | 92.5 |  | 92.4 |  | 90.4 |  | 92.4 |  | 92.3 |  | 91.9 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | 300 | 104.7 | 104.1 | 106.7 | 106.2 | 106.1 | 105.5 | 106 | 105.4 | 105.6 | 105.1 | 106.2 | 105.6 | 106.3 | 105.7 | 106.3 | 105.7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
20185 FALLS 115 20182 FALLS 230 1 | 300 | 103 | 102.4 | 105.1 | 104.5 | 104.4 | 103.8 | 104.3 | 103.7 | 104 | 103.4 | 104.6 | 104 | 104.6 | 104 | 104.6 | 104.1 | HNDRSN-FRNKLNTN115_&_E18_KITT-YNGSVL115
20185 FALLS 115 20182 FALLS 230 1 | 300 | 93 | 93.2 | 94.2 | 94.5 | 93.5 | 93.9 | 93.5 | 93.8 | 91.9 | 92.2 | 93.3 | 93.8 | 93.3 | 93.7 | 93.2 | 93.5 | PER-RXBOWMAN230_&_PER-OXFORDST230
20185 FALLS 115 20182 FALLS 230 1 | 300 | 87.3 | 88.6 | 92.5 | 93.9 | 91.1 | 92.5 | 90.9 | 92.3 |  | 91.3 | 91.2 | 92.6 | 91.2 | 92.6 | 91.1 | 92.5 | FALLS-MILB230_&_FALLS23-HOMESTED230
20185 FALLS 115 20182 FALLS 230 1 | 300 | 86.3 | 87.7 | 91.5 | 93 | 90.1 | 91.5 |  | 91.3 |  | 90.4 | 90.7 | 91.7 |  | 91.7 | 90.2 | 91.6 | FALLS-MILB230_&_HOMESTED-PINELK230
20185 FALLS 115 20182 FALLS 230 1 | 300 | 90.2 | 90.5 | 91.4 | 92.2 | 90.8 | 91.1 | 90.7 | 91 |  |  |  | 91 | 90.6 | 90.9 | 90.4 | 90.7 | HNDRSN-MAYOSUSW230_&_OXFORDN-HENDE230
20185 FALLS 115 20182 FALLS 230 1 | 300 | 85.6 | 87 | 90.8 | 91.8 |  | 90.8 |  | 90.5 |  |  | 90.3 | 90.9 |  | 90.9 |  | 90.8 | FALLS-MILB230_&_PINELK-FOXCROFT230
20185 FALLS 115 20182 FALLS 230 1 | 300 | 85.2 | 86.6 | 90.4 | 91.7 |  | 90.4 |  | 90.2 |  |  |  | 90.5 |  | 90.5 |  | 90.4 | MILB-FALLS230_&_MILB-FOXCROFT230
20290 I-OLVRRB 115 20304 E14-ULAH 115 1 | 138 | 91.8 | 76 | 97.9 |  | 98.6 |  | 98.4 |  | 94.6 |  | 97.9 |  | 97.4 |  | 96.2 |  | 20309 BISCOE W 230 20332 ASHEB 230 1
20303 SEAGROVE 115 20304 E14-ULAH 115 1 | 148 | 100.3 | 84.9 | 106.4 | 90.6 | 107.1 | 91.2 | 106.9 | 91.1 | 103.2 |  | 106.4 | 90.6 | 105.9 | 90.1 | 104.8 |  | 20309 BISCOE W 230 20332 ASHEB 230 1
20314 E3-CTRCH 230 20361 WEST END 230 1 | 507 | 86.9 | 70.4 | 92.8 |  | 96 |  | 95.9 |  |  |  | 94.6 |  | 93.8 |  | 91.9 |  | 20377 RICHMOND 500 20391 CUMBERLD 500 1
20314 E3-CTRCH 230 20373 S GARD T 230 1 | 507 | 84.5 | 68.1 | 90.4 |  | 93.5 |  | 93.4 |  |  |  | 92.1 |  | 91.3 |  |  |  | 20377 RICHMOND 500 20391 CUMBERLD 500 1
20349 PH SH 2W 230 20985 ANSON 230 1 | 398 | 92.2 | 93.2 | 102.6 | 103.2 | 98.1 | 98.7 | 95.7 | 96.4 | 96.6 | 97.4 | 100.8 | 101.3 | 100.7 | 101.3 | 99.5 | 100.1 | 337 8NEWPORT 500 20377 RICHMOND 500 1
20349 PH SH 2W 230 20985 ANSON 230 1 | 398 | 85.5 | 86.7 | 95.9 | 96.9 |  | 90.8 |  |  |  | 90.7 | 92.7 | 93.7 | 92.8 | 93.8 | 92 | 93 | 20348 RKH 230 20350 PH SH 1B 230 1
20349 PH SH 2W 230 20985 ANSON 230 1 | 398 | 85.5 | 86.7 | 95.9 | 96.9 |  | 90.8 |  |  |  | 90.7 | 92.7 | 93.7 | 92.8 | 93.8 | 92 | 93 | 20350 PH SH 1B 230 20985 ANSON 230 1
20350 PH SH 1B 230 20985 ANSON 230 1 | 398 | 92.4 | 93.4 | 102.8 | 103.4 | 98.3 | 98.8 | 95.9 | 96.6 | 96.7 | 97.6 | 101 | 101.1 | 100.9 | 101.5 | 99.7 | 100.3 | 337 8NEWPORT 500 20377 RICHMOND 500 1
20350 PH SH 1B 230 20985 ANSON 230 1 | 398 | 85.5 | 86.8 | 96 | 97 |  | 90.9 |  |  |  | 90.8 | 92.8 | 93.7 | 92.9 | 93.8 | 92.1 | 93.1 | 20348 RKH 230 20349 PH SH 2W 230 1
20350 PH SH 1B 230 20985 ANSON 230 1 | 398 | 85.5 | 86.8 | 96 | 97 |  | 90.9 |  |  |  | 90.8 | 92.9 | 93.7 | 92.9 | 93.8 | 92.1 | 93.1 | 20349 PH SH 2W 230 20985 ANSON 230 1
20360 ELLERBE 230 20361 WEST END 230 1 | 507 | 86.9 | 73.4 | 90.5 |  | 92.6 |  | 92.8 |  |  |  | 91.7 |  | 91.2 |  | 90.2 |  | 20348 RKH 230 20361 WEST END 230 1
20377 RICHMOND 500 337 8NEWPORT 500 1 | 1350 | 108.1 | 109.6 | 117.1 | 118.5 | 114.3 | 115.8 | 112.3 | 113.73 | 112.4 | 113.8 | 117 | 118.5 | 116.7 | 118.2 | 115.2 | 116.7 | PHSH1-ANSON230_&_PHSH2-ANSON230
20377 RICHMOND 500 337 8NEWPORT 500 1 | 1350 | 99.8 | 102 | 108.8 | 110.2 | 107.1 | 107.8 | 105.1 | 106.1 | 106.4 | 107.1 | 109.7 | 110.3 | 109.6 | 110.1 | 108.5 | 109.1 | OAKBORO-ANSON230_&_OAKBORO-IANSON230
20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | 637 | 93.4 | 69.1 | 99 |  | 102.7 |  | 103.6 |  | 97.6 |  | 101.1 |  | 100.4 | 103.4 | 99 |  | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1
20387 P1-FAY 0 230 20392 FAY 115 1 | 200 | 91.4 | 95.4 | 99.4 | 103.4 | 99.5 | 103.6 | 99.4 | 103.5 | 98.3 | 102.3 | 99.4 | 103.4 | 99.3 |  | 99 | 103 | 20387 P1-FAY 0 230 20392 FAY 115 2
20387 P1-FAY 0 230 20392 FAY 115 2 | 200 | 91.3 | 95.3 | 99.3 | 103.3 | 99.4 | 103.5 | 99.3 | 103.4 | 98.3 | 102.2 | 99.4 | 103.4 | 99.3 |  | 98.9 | 102.9 | 20387 P1-FAY 0 230 20392 FAY 115 1
20388 P3-FAYRR 230 20387 P1-FAY 0 230 1 | 637 | 97.4 | 73.9 | 101.7 |  | 105.1 |  | 105.9 |  | 100.5 |  | 103.6 |  | 102.9 |  | 101.8 |  | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1
20388 P3-FAYRR 230 20387 P1-FAY 0 230 1 | 637 | 93.8 | 72 | 98.2 |  | 101 |  | 101.6 |  | 97 |  | 99.8 |  | 99.2 |  | 98.2 |  | FAY-FAYE230_&_FAY-WSP230
20391 CUMBERLD 500 B$0005 1.00 1 | 1000 | 78 | 84.8 |  | 90.6 | [7 empty] | 90.4 |  | 90.3 |  |  | 20183 WAKE 500 20391 CUMBERLD 500 1
20401 VANDER 115 20265 E15-STED 115 1 | 163 | 65.4 | 77.4 |  |  |  | 91.2 |  | 91.5 |  |  |  | 90.4 |  | 90 |  |  | 20196 ERWIN 230 20197 DUNN 230 1
20421 LAURINBG 115 20424 LAURINBG 230 1 | 200 | 98.6 | 96.8 | 100.3 | 98.5 | 102.8 | 101 | 103.8 | 102 | 99.7 | 97.9 | 101.3 | 99.6 | 100.9 | 99.2 | 100.3 | 98.5 | 20421 LAURINBG 115 20424 LAURINBG 230 2
20421 LAURINBG 115 20424 LAURINBG 230 2 | 200 | 98.5 | 96.7 | 100.2 | 98.4 | 102.7 | 100.9 | 103.6 | 101.9 | 99.6 | 97.8 | 101.2 | 99.4 | 100.8 | 99.1 | 100.2 | 98.4 | 20421 LAURINBG 115 20424 LAURINBG 230 1
20428 BISCOE W 115 20301 TROY 115 1 | 269 | 83.8 | 70.7 | 92.6 |  | 91.4 |  | 90.7 |  |  |  | 91.2 |  | 90.9 |  |  |  | 20347 ABRDN RD 230 20348 RKH 230 1
20554 9THORG T 230 20552 E WILM 230 1 | 590 | 97.5 | 93.1 | 98 | 93.7 | 98.7 | 94.3 | 98.7 | 94.4 | 97.3 | 93.1 | 98.3 | 93.9 | 98.1 | 93.8 | 97.8 | 93.6 | BR1-BARCK230_&_BR2-BARCRK230
20577 MURRAYVL 230 20552 E WILM 230 1 | 590 | 90 | 85.7 | 90.4 |  | 91.1 |  | 91.1 |  |  |  | 90.7 |  | 90.5 |  | 90.2 |  | BR1-BARCK230_&_BR2-BARCRK230
20615 BARNARD 230 20616 BARNARD 115 1 | 150 | 95.3 | 95.2 | 95.2 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.2 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.2 | 95.3 | ** Base Case **
20632 MARION 115 20630 MULLINS 115 1 | 179 | 69.5 | 81.9 |  |  |  | 94.8 |  | 97.4 |  |  |  | 90.6 |  |  |  |  | 20587 E1-CHADP 230 20631 MARION 230 1
20632 MARION 115 20630 MULLINS 115 1 | 179 | 70.4 | 85.9 |  | 90.5 |  | 94.7 |  | 96 |  |  |  | 92.2 |  | 91.6 |  | 90.5 | 20581 WHITEVIL 115 20600 WHITEVIL 230 1
20632 MARION 115 20630 MULLINS 115 1 | 179 | 65.6 | 78 |  |  |  | 90.8 |  | 93.4 | [8 empty] | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20638 WDSB T 230 20348 RKH 230 1 | 539 | 100 | 87.2 | 103.6 | 90.5 | 105.7 | 92.6 | 105.8 | 92.7 | 102.1 |  | 104.8 | 91.7 | 104.3 | 91.2 | 103.3 | 90.2 | 20348 RKH 230 20361 WEST END 230 1
20638 WDSB T 230 20360 ELLERBE 230 1 | 507 | 91.8 | 78.2 | 95.4 |  | 97.5 |  | 97.7 |  | 93.8 |  | 96.6 |  | 96.1 |  | 95.1 |  | 20348 RKH 230 20361 WEST END 230 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 84.5 | 94.9 | 91.4 | 100.6 | 103.5 | 112.7 | 108.3 | 117.4 |  | 99.1 | 96.5 | 105.7 | 94.7 | 103.9 | 92.1 | 101.3 | 20663 LATTA 230 20682 DILLMP T 230 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 79.9 | 90.2 |  | 95.8 | 98.8 | 107.9 | 103.5 | 112.6 |  | 94.4 | 91.7 | 100.9 |  | 99.1 |  | 96.5 | 20046 WSPN BUS 230 20682 DILLMP T 230 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 79.8 | 86.3 |  | 92.5 | 93.5 | 104 | 98.2 | 108.6 |  | 90.9 |  | 97.3 |  | 95.6 |  | 93.1 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
20654 DILLON T 115 20632 MARION 115 1 | 97 | 79.8 | 85.4 |  | 90.6 | 97.1 | 100.2 | 100.7 | 103.8 |  |  | 91.5 | 94.3 |  | 93.1 |  | 90.8 | 20046 WSPN BUS 230 20047 WSP BUS 115 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 72.1 | 80.9 |  |  |  | 96.1 | 92.2 | 100.1 |  |  |  | 90.3 |  |  |  |  | 20587 E1-CHADP 230 20600 WHITEVIL 230 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 74.4 | 80.7 |  |  | 90.2 | 94.8 | 93 | 97.7 |  |  |  | 90 |  |  |  |  | 337 8NEWPORT 500 20377 RICHMOND 500 1
20654 DILLON T 115 20632 MARION 115 1 | 97 | 74.2 | 83.1 |  |  | 90.4 | 98.3 | 94.5 | 102.4 |  |  |  | 92.5 |  | 91.1 |  |  | 20587 E1-CHADP 230 20631 MARION 230 1
20662 FLORENCE 230 20663 LATTA 230 1 | 507 | 67.1 | 77.8 |  |  |  | 90.8 |  | 92 | [8 empty] | MARION-MARION(SCPSA)230_1&2
20683 BURNETTE 115 20301 TROY 115 1 | 269 | 89.1 | 75.8 | 98 |  | 96.8 |  | 96.1 |  | 92.9 |  | 96.7 |  | 96.3 |  | 95 |  | 20347 ABRDN RD 230 20348 RKH 230 1
20683 BURNETTE 115 20301 TROY 115 1 | 269 | 86.3 | 73.2 | 95.2 |  | 93.9 |  | 93.3 |  | 90.1 |  | 93.9 |  | 93.4 |  | 92.2 |  | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20683 BURNETTE 115 20302 E14-TROY 115 1 | 269 | 93.5 | 80.2 | 102.6 |  | 101.4 |  | 100.7 |  | 97.4 |  | 101.3 |  | 100.9 |  | 99.6 |  | 20347 ABRDN RD 230 20348 RKH 230 1
20683 BURNETTE 115 20302 E14-TROY 115 1 | 269 | 90.8 | 77.6 | 99.8 |  | 98.5 |  | 97.9 |  | 94.7 |  | 98.4 |  | 98 |  | 96.7 |  | 20309 BISCOE W 230 20347 ABRDN RD 230 1
20725 CAMDEN 115 20716 CAMCTY02 115 1 | 108 | 85.3 | 82.9 |  |  | 98.6 | 96.1 | 98.6 | 96.2 | [8 empty] | 20725 CAMDEN 115 20731 I-DUP CA 115 1
20725 CAMDEN 115 20731 I-DUP CA 115 1 | 108 | 83.3 | 80.2 |  |  | 98 | 94.7 | 98.4 | 95.2 | [8 empty] | 20716 CAMCTY02 115 20725 CAMDEN 115 1
B$0024 1.00 20183 WAKE 500 1 | 1000 | 97.6 | 93.4 | 106.7 | 102.4 | 106.9 | 102.7 | 106.8 | 102.5 | 108.8 | 104.6 | 107.4 | 103.2 | 107.6 | 103.5 | 108.1 | 104 | 3Wnd: OPEN B$0045 2
B$0024 1.00 20190 WAKE 230 1 | 1000 | 95.3 | 91.2 | 103.6 | 99.6 | 103.9 | 99.9 | 103.8 | 99.7 | 105.9 | 101.8 | 104.4 | 100.4 | 104.6 | 100.7 | 105.1 | 101.2 | 3Wnd: OPEN B$0045 2
B$0045 1.00 20183 WAKE 500 2 | 1000 | 97.5 | 93.3 | 106.6 | 102.4 | 106.8 | 102.7 | 106.7 | 102.5 | 108.7 | 104.5 | 107.4 | 103.2 | 107.6 | 103.4 | 108.1 | 103.9 | 3Wnd: OPEN B$0024 1
B$0045 1.00 20190 WAKE 230 2 | 1000 | 95.2 | 91.1 | 103.6 | 99.6 | 103.8 | 99.9 | 103.7 | 99.7 | 105.8 | 101.8 | 104.3 | 100.4 | 104.6 | 100.7 | 105.1 | 101.1 | 3Wnd: OPEN B$0024 1
Note on A3: PTI: ** From bus ** ** To bus ** Circuit Type
Note on B3: PTI: Branch Rating
Note on E3: PTI: Loading in %
Note on F3: PTI: Loading in %
Note on G3: PTI: Loading in %
Note on H3: PTI: Loading in %
Note on I3: PTI: Loading in %
Note on J3: PTI: Loading in %
Note on K3: PTI: Loading in %
Note on L3: PTI: Loading in %
Note on M3: PTI: Loading in %
Note on N3: PTI: Loading in %
Note on O3: PTI: Loading in %
Note on P3: PTI: Loading in %
Note on Q3: PTI: Loading in %
Note on R3: PTI: Loading in %
Note on S3: PTI: Contingency Description