Project Name:	Antioch 500/230 kV transformers

Project Description

Increase transformer capacity to alleviate congestion.

| Projected In-Service Date for Base Reliability Plan | 2014 |
| --- | --- |
| Earliest Projected In-Service Date For Resource Supply Option | 2011 600 MW Import from AEP to Duke and 1200 MW Import from AEP (600 MW to Duke, 600 MW to CPLE) |
| Project Lead Time |  |
| Estimated Cost |  |

Narrative Description of the Need for this Project

The Antioch banks will achieve 100% of their present rating (840 MVA) in the 2011-2014 timeframe. Loss of the parallel bank when there is a generation deficiency in Duke’s northern region causes the highest loading. North to south transfers into the Duke control area increase bank loading and further decrease import capability.

Transmission Solutions Considered

First, perform testing/analysis to eliminate the stray flux heating concern and allow re-rating of the banks closer to their original design. Then based on outcome of testing/analysis, replace the banks with higher capacity banks, if necessary.

Why this Project was Selected as the Preferred Solution

The banks have an ~ 7% OTDF. For each incremental increase in the rating by 7 MVA, there will be an increase in transfer capability of 100 MW.