Project Name:	Falls 230 kV Substation, Install #2 230/115 kV transformer

Project Description

Install #2 230/115 kV 300 MVA transformer.

| Projected In-Service Date for Base Reliability Plan | June 2013 |
| --- | --- |
| Earliest Projected In-Service Date For Resource Supply Option | June 2012 600 MW Import to CPLE from Duke |
| Project Lead Time | 5 years |
| Estimated Cost | $5 M |

Narrative Description of the Need for this Project

By summer of 2013, if both Henderson-Franklinton 115 kV & Henderson – Falls 115 kV common tower lines are outaged, the loading on the Falls 230/115 kV transformer will exceed its rating. Worst 600 MW Resource Supply option is for an import to CPLE from Duke where the added loading would require this project to be completed in June 2012.

Transmission Solutions Considered

Additional area transmission lines were considered and projected to cost in excess of a second 230/115 kV transformer. Investigation determined that this transformer does have a 65 degree rise rating (112% of 55 degree rise rating) that can be utilized up to 109%.

Why this Project was Selected as the Preferred Solution

Installation of a second 230/115 kV 300 MVA transformer will alleviate the bank overload under this contingency. The in-service dated utilizes the 65 degree rise rating up to 109%.