## Duke Summary
Transmission Facility | Worst-Case Information | Base | Anson | Roxboro | Tillery-Blewett | 1200ImportDukeCPLE_AEP | Roxboro_1200ImportDukeCPLE_AEP | 1200ImportDukeCPLE_AEPVP | Roxboro_1200ImportDukeCPLE_AEPVP | 600ImportDuke_AEP | Roxboro_600ImportDuke_AEP | 600ImportDuke_SOCO | Roxboro_600ImportDuke_SOCO | 600ImportDuke_TVA | Roxboro_600ImportDuke_TVA | 600ImportDuke_SCEG | Roxboro_600ImportDuke_SCEG | 600ImportDuke_SCPSA | Roxboro_600ImportDuke_SCPSA | 600ImportDuke_CPLE | Roxboro_600ImportDuke_CPLE | 600ImportCPLE_AEP | 600ImportCPLE_VP | 600ImportCPLE_SCEG | 600ImportCPLE_SCPSA | 600ImportCPLE_Duke | PEC TRM Brunswick 1 Down | PEC TRM Harris Down | PEC TRM Brunswick 1 Down 600ImportCPLE_Duke | PEC TRM Harris Down 600ImportCPLE_Duke | PEC TRM Brunswick 1 Down 1200 AEP | PEC TRM Harris Down 1200 AEP | PEC TRM Brunswick 1 Down 1200 VPAEP | PEC TRM Harris Down 1200 VPAEP | Duke 1200 to CPLE | Duke 1200 to CPLE Roxboro 4 Down | PEC TRM Brunswick 1 Down 1200 DKCPLE | PEC TRM Harris Down 1200 DKCPLE | COMMENTS | Transmission Facility
| Post-Contingency Loading (MVA) | 70.9 | 81.8 | 87.5 | 73.1 | 64.8 | 79.2 | 65.8 | 76.1 | 74.7 | 91.4 | 78.1 | 97.9 | 76.2 | 96 | 87.9 | 107.6 | 88.9 | 108.6 | 90.4 | 93 | 60 | 60.2 | 74.7 | 75.6 | 58.1 | - | - | - | - | - | - | - | - | - | - | - | - | Cont Rating 58.5 MVA - Should use 12 Hour Rating 71.2 MVA
Wateree 100 kV Line | % Facility Rating | 113.3% | 130.7% | 139.7% | 116.8% | 111.5% | 127.1% | 105.3% | 121.7% | 119.4% | 145.9% | 124.9% | 156.9% | 121.8% | 153.8% | 140.5% | 172.5% | 142.1% | 174.1% | 144.3% | 148.3% | 102.6% | 102.9% | 119.5% | 121.1% | 99.4% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | (75°, 90° Hot Line Crossing) 2/0 Cu Conductor Limited | Wateree 100 kV Line
(Wateree-Great Falls) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2012 | - | - | - | - | - | - | - | - | - | - | - | - | Hot Line Crossing Correction Only 78.1 MVA | (Wateree-Great Falls)
| Contingency | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | CdckGm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Catawba 2 Generator | Cat1Gm w/ Catawba 2 Generator | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Wateree 100 kV Line | Cat1Gm w/ Catawba 2 Generator | - | - | - | - | - | - | - | - | - | - | - | - | Reconductor Required - Operating Guide Available
| Post-Contingency Loading (MVA) | 503.2 | 499.5 | 522.7 | 503.7 | 496 | 509.6 | 492.8 | 506.5 | 494.7 | 514.1 | 504 | 529.7 | 501.5 | 519.8 | 505 | 530.7 | 504.5 | 530.3 | 498.8 | 506 | 504.8 | 501.3 | 514.3 | 513.8 | 453 | - | - | - | - | - | - | - | - | 457.6 | - | - | - | 12 Hour Rating 478 MVA
Westport 230 kV Line | % Facility Rating | 103.2% | 102.6% | 107.4% | 103.3% | 101.9% | 104.8% | 101.1% | 104.1% | 101.5% | 105.5% | 103.4% | 109% | 102.9% | 106.9% | 103.6% | 109.2% | 103.4% | 109.1% | 102.2% | 103.7% | 103.7% | 102.8% | 105.7% | 105.6% | 92.8% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 93.5% | < 90% | < 90% | < 90% | CT/5-M Ratio Limited | Westport 230 kV Line
(Marshall-McGuire) | Year Upgrade Required | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2015 | - | - | - | - | - | - | - | - | 2015 | - | - | - | 1272 ACSR Conductor 617.5 MVA | (Marshall-McGuire)
| Contingency | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | Mar3Gm w/ Godbey 500 kV Line | - | - | - | - | - | - | - | - | Mar3Gm w/ Godbey 500 kV Line | - | - | - | CT Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | 758.7 | 763.8 | 761 | 761.3 | 838.2 | 840.9 | 824.9 | 827.6 | 803.3 | 805.4 | 783.6 | 791.7 | 791 | 793 | 771.7 | 779.8 | 770.9 | 779 | 767.2 | 767.8 | 794.7 | 780.8 | 763.1 | 762.2 | - | - | - | - | - | 819.9 | 824.2 | 806.3 | 810.7 | - | - | - | - | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 90.3% | 90.9% | 90.6% | 90.6% | 99.8% | 100.1% | 98.2% | 98.5% | 95.6% | 95.9% | 93.3% | 94.3% | 94.2% | 94.4% | 91.9% | 92.8% | 91.8% | 92.7% | 91.3% | 91.4% | 94.6% | 93% | 90.8% | 90.7% | < 90% | < 90% | < 90% | < 90% | < 90% | 97.6% | 98.1% | 96% | 96.5% | < 90% | < 90% | < 90% | < 90% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 1 | Year Upgrade Required | 2017 | 2016 | 2016 | 2016 | 2012 | 2011 | 2012 | 2012 | 2014 | 2014 | 2015 | 2014 | 2015 | 2014 | 2016 | 2015 | 2016 | 2015 | 2016 | 2016 | 2014 | 2015 | 2016 | 2016 | - | - | - | - | - | 2013 | 2012 | 2014 | 2013 | - | - | - | - | Transformer 840 MVA (Stray Flux Issues???) | Transformer Bank 1
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | - | - | - | - | - | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | - | - | - | - | Increased Transformer Capacity Required in 2011
| Post-Contingency Loading (MVA) | 801.2 | 806.6 | 803.6 | 804 | 885.3 | 888.1 | 871.2 | 874.1 | 848.3 | 850.7 | 827.6 | 836.2 | 835.4 | 837.5 | 815 | 823.6 | 814.2 | 822.7 | 810.3 | 810.8 | 839.3 | 824.6 | 805.9 | 805 | 796.6 | 787.4 | 792.2 | - | - | 865.9 | 870.6 | 851.5 | 856.2 | 772.4 | - | - | - | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 95.4% | 96% | 95.7% | 95.7% | 105.4% | 105.7% | 103.7% | 104.1% | 101% | 101.3% | 98.5% | 99.5% | 99.5% | 99.7% | 97% | 98% | 96.9% | 97.9% | 96.5% | 96.5% | 99.9% | 98.2% | 95.9% | 95.8% | 94.8% | 93.7% | 94.3% | < 90% | < 90% | 103.1% | 103.6% | 101.5% | 101.9% | 92% | < 90% | < 90% | < 90% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 2 | Year Upgrade Required | 2014 | 2014 | 2014 | 2014 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2012 | 2012 | 2012 | 2012 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2012 | 2012 | 2014 | 2014 | 2014 | 2015 | 2014 | - | - | 2011 | 2011 | 2011 | 2011 | 2016 | - | - | - | Transformer 840 MVA (Stray Flux Issues???) | Transformer Bank 2
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Mar3Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | - | - | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | - | - | - | Increased Transformer Capacity Required in 2011
| Post-Contingency Loading (MVA) | 1862.7 | 1859.4 | 1913.2 | 1862.8 | 1825.8 | 1860.3 | 1802.2 | 1837.5 | 1792.4 | 1844.9 | 1813.8 | 1869.7 | 1809.1 | 1859.9 | 1806.1 | 1858.7 | 1800.3 | 1853.1 | 1772.5 | 1783.1 | 1896.2 | 1872.3 | 1909.8 | 1904.2 | 1971.6 | 1980.3 | 1993.6 | 1931.6 | 1940.3 | 1872 | 1882.1 | 1852.6 | 1865.8 | 2019.1 | 1958.8 | 1840.4 | 1940.9 | 12 Hour Rating 1904.3 MVA
Godbey 500 kV Line | % Facility Rating | 95.1% | 95% | 98.3% | 95.1% | 93.4% | 95.7% | 92% | 94.2% | 91.3% | 94.4% | 92.6% | 95.6% | 92.3% | 95.4% | 92.1% | 95.2% | 91.8% | 94.8% | 90% | 91% | 97.2% | 95.7% | 98.1% | 97.7% | 101.9% | 102.4% | 103.8% | 101.1% | 102.6% | 97.7% | 99.2% | 96.1% | 97.5% | 105.5% | 101.4% | 96.6% | 105.1% | CT/5 Ratio Limited | Godbey 500 kV Line
(Woodleaf-Pleasant Garden) | Year Upgrade Required | 2014 | 2014 | 2012 | 2014 | 2015 | 2014 | 2016 | 2015 | 2016 | 2014 | 2015 | 2014 | 2016 | 2014 | 2016 | 2014 | 2016 | 2014 | 2017 | 2016 | 2013 | 2014 | 2012 | 2013 | 2011 | 2011 | 2011 | 2011 | 2011 | 2013 | 2012 | 2014 | 2013 | 2011 | 2011 | 2013 | 2011 | 2-2515 ACSR Conductor 4718 MVA | (Woodleaf-Pleasant Garden)
| Contingency | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Cat1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Belews Creek 1 Generator | Richmond-Newport 500 kV Line | CT Upgrade pushes out to 2018
| Post-Contingency Loading (MVA) | 1320.5 | 1319 | 1289.2 | 1319.7 | 1325.7 | 1299 | 1293.1 | 1266.8 | - | - | 1272.4 | - | 1270.2 | - | - | - | - | - | - | - | 1393.7 | 1361.6 | 1385.8 | 1370 | 1448.3 | 1628.1 | 1606.3 | 1694.5 | 1667.2 | 1630.3 | 1539.8 | 1602.8 | 1577.7 | 1526.2 | 1493.9 | 1791.4 | 1764.6 | PEC Phase Angle Rating 1350 MVA
Richmond 500 kV Line | % Facility Rating | 94.9% | 95.1% | 93.1% | 94.8% | 95.5% | 93.7% | 92.9% | 91.1% | < 90% | < 90% | 91.3% | < 90% | 91.1% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 100.7% | 98.1% | 100.5% | 99.3% | 105.4% | 119.3% | 118.3% | 126% | 125.2% | 120.6% | 113.1% | 117.9% | 116.9% | 111.5% | 108.7% | 135.5% | 134.9% | PEC Phase Angle Requirement Limited | Richmond 500 kV Line
(Richmond-Newport) | Year Upgrade Required | 2014 | 2014 | 2015 | 2014 | 2014 | 2015 | 2015 | 2016 | - | - | 2016 | - | 2016 | - | - | - | - | - | - | - | 2011 | 2012 | 2011 | 2012 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 3000 A Communication Trap at Richmond (PEC) 2598 MVA | (Richmond-Newport)
| Contingency | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | - | - | Mcg1Gm w/ Godbey 500 kV Line | - | Mcg1Gm w/ Godbey 500 kV Line | - | - | - | - | - | - | - | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Guardian 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | WatrGm w/ Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Phase Angle Solution required in 2011
| Post-Contingency Loading (MVA) | 101.5 | 103.1 | 100.5 | 101.6 | 109.3 | 108.6 | 107.8 | 107.1 | 105.7 | 104.8 | 104.2 | 103.2 | 107.4 | 105.1 | 101.8 | 100.8 | 101.7 | 100.7 | 101.9 | 101.6 | 105 | 103.5 | 101.1 | 100.9 | 100.1 | 116.6 | 116.4 | 116 | 115.8 | 125.6 | 125.5 | 124 | 123.8 | - | - | 110.5 | 110.2 | LTE Rating 108.3 MVA
Horseshoe 115/100 kV | % Facility Rating | 93.8% | 95.2% | 92.8% | 93.8% | 100.9% | 100.3% | 99.5% | 98.9% | 97.6% | 96.7% | 96.2% | 95.3% | 99.2% | 97% | 94% | 93.1% | 93.9% | 93% | 94.1% | 93.8% | 96.9% | 95.6% | 93.3% | 93.2% | 92.4% | 107.6% | 107.5% | 107.1% | 106.9% | 116% | 115.8% | 114.5% | 114.4% | < 90% | < 90% | 102% | 101.8% | 300 Cu Limited | Horseshoe 115/100 kV
Transformer | Year Upgrade Required | 2015 | 2014 | 2015 | 2015 | 2011 | 2011 | 2012 | 2012 | 2013 | 2013 | 2013 | 2014 | 2012 | 2013 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2013 | 2014 | 2015 | 2015 | 2015 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | - | - | 2011 | 2011 | Transformer 134.5 MVA | Transformer
| Contingency | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | - | - | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | 300 Cu, 1/2" Cu Pipe, 600 Cu Switch Upgrades pushes to 2022
| Post-Contingency Loading (MVA) | - | - | 783.4 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 760.2 | - | 770.8 | 767.7 | 804.1 | 815.3 | 835.6 | 892.4 | 912.3 | 789.1 | 809.4 | 773.1 | 793.5 | 853.2 | 844.1 | 931.9 | 950.6 | 12 Hour Rating 840 MVA
Parkwoood 500/230 kV | % Facility Rating | < 90% | < 90% | 93.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.5% | < 90% | 91.8% | 91.4% | 95.7% | 97.1% | 99.5% | 106.2% | 108.6% | 93.9% | 96.4% | 92% | 94.5% | 101.6% | 100.5% | 110.9% | 113.2% | Transformer Limited | Parkwoood 500/230 kV
Transformer Bank 5 | Year Upgrade Required | - | - | 2015 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2017 | - | 2016 | 2016 | 2014 | 2013 | 2012 | 2011 | 2011 | 2015 | 2013 | 2016 | 2016 | 2011 | 2011 | 2011 | 2011 | Transformer 840 MVA (Stray Flux Issues???) | Transformer Bank 5
| Contingency | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Increased Transformer Capacity Required in 2014
| Post-Contingency Loading (MVA) | 745 | 737.8 | 790.2 | 741.5 | 721.5 | 752.9 | - | 736.2 | - | 745 | - | 757.2 | - | 754.5 | - | 759.9 | - | 752.5 | - | - | 767.1 | 750.2 | 777.5 | 774.6 | 811.3 | 822.7 | 843.2 | 900.4 | 920.5 | 822.7 | 816.7 | 780.1 | 800.6 | 860.9 | 851.8 | 940.4 | 959.1 | 12 Hour Rating 796.7 MVA
Parkwoood 500/230 kV | % Facility Rating | 93.5% | 92.6% | 99.2% | 93.1% | 90.6% | 94.5% | < 90% | 92.4% | < 90% | 93.5% | < 90% | 95% | < 90% | 94.7% | < 90% | 95.4% | < 90% | 94.5% | < 90% | < 90% | 96.3% | 94.2% | 97.6% | 97.2% | 101.8% | 103.3% | 105.8% | 113% | 115.5% | 103.3% | 102.5% | 97.9% | 100.5% | 108.1% | 106.9% | 118% | 120.4% | CT/5 Ratio Limited | Parkwoood 500/230 kV
Transformer Bank 6 | Year Upgrade Required | 2015 | 2015 | 2012 | 2015 | 2016 | 2014 | - | 2014 | - | 2015 | - | 2014 | - | 2014 | - | 2014 | - | 2014 | - | - | 2013 | 2015 | 2013 | 2013 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2013 | 2011 | 2011 | 2011 | 2011 | 2011 | Transformer 1152.7 MVA | Transformer Bank 6
| Contingency | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | - | - | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Oco1Gm w/ Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | CT Upgrade pushes out to 2024
| Post-Contingency Loading (MVA) | 419.2 | 412.9 | 414.5 | 417.7 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 412.7 | 417.1 | - | - | 425.5 | - | - | - | - | - | - | - | - | 417.5 | - | - | - | 12 Hour Rating 452.5 MVA
London Creek 230 kV | % Facility Rating | 92.1% | 90.8% | 91.1% | 91.8% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.7% | 91.7% | < 90% | < 90% | 93.6% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 91.3% | < 90% | < 90% | < 90% | 795 ACSR Conductor Limited | London Creek 230 kV
(Peach Valley-Riverview) | Year Upgrade Required | 2016 | 2016 | 2016 | 2016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 2016 | - | - | 2015 | - | - | - | - | - | - | - | - | 2016 | - | - | - | Reconductor Required in 2015 | (Peach Valley-Riverview)
| Contingency | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | - | - | Oco1Gm w/ London Creek 230 kV Line | - | - | - | - | - | - | - | - | Oco1Gm w/ London Creek 230 kV Line | - | - | -
| Post-Contingency Loading (MVA) | 438.6 | 438.8 | 437.4 | 439.6 | 446.8 | 445.8 | 445.6 | 444.8 | 443 | 441.8 | 441.1 | 440 | 441 | 440.5 | 438.9 | 437.9 | 439.2 | 438 | 438.8 | 438.4 | 442.4 | 441.1 | 438.2 | 438.5 | 435.9 | - | - | - | - | - | - | - | - | - | - | - | - | 12 Hour Rating 478 MVA
Dooley 230 kV Line | % Facility Rating | 90.7% | 90.8% | 90.5% | 90.9% | 92.7% | 92.6% | 92.4% | 92.3% | 91.8% | 91.7% | 91.5% | 91.4% | 91.6% | 91.5% | 91% | 90.9% | 91.1% | 90.9% | 90.9% | 90.8% | 91.6% | 91.3% | 90.8% | 90.8% | 90.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | CT/5-M Ratio Limited | Dooley 230 kV Line
(Marshall-Winecoff) | Year Upgrade Required | 2016 | 2016 | 2017 | 2016 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2017 | - | - | - | - | - | - | - | - | - | - | - | - | 1272 ACSR Conductor 617.5 MVA | (Marshall-Winecoff)
| Contingency | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | Cat1Gm w/ Dooley 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | CT Upgrade pushes out to 2024
| Post-Contingency Loading (MVA) | 380.8 | 393.5 | 379.2 | 382.9 | 391.4 | 389.7 | 388.3 | 386.6 | 384.5 | 382.9 | 388.2 | 384.3 | 387.4 | 385.7 | 387.6 | 383.6 | 384.8 | 380.9 | - | - | 387.8 | 384.7 | 391 | 388.2 | 390.1 | - | - | - | - | - | 409.8 | - | - | 393.4 | - | - | 412.3 | Cont Rating 436.9 MVA - Should use 12 Hour Rating 478 MVA
Sandy Ridge 230 kV Line | % Facility Rating | 90.4% | 93.9% | 90% | 90.9% | 93.2% | 92.9% | 92.4% | 92% | 91.4% | 91.1% | 92.4% | 91.4% | 92.2% | 91.8% | 92.2% | 91.3% | 91.5% | 90.6% | < 90% | < 90% | 92.2% | 91.4% | 93% | 92.3% | 93% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.1% | < 90% | < 90% | 93.1% | < 90% | < 90% | 91.2% | CT/5 Ratio, CT/5-M Ratio, and 51XYZ Relay Limited | Sandy Ridge 230 kV Line
(Newport-Morning Star) | Year Upgrade Required | 2017 | 2015 | 2017 | 2016 | 2015 | 2015 | 2015 | 2016 | 2016 | 2016 | 2015 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | - | - | 2016 | 2016 | 2015 | 2016 | 2015 | - | - | - | - | - | 2017 | - | - | 2015 | - | - | 2016 | 954 ACSR Conductor 506.7 MVA | (Newport-Morning Star)
| Contingency | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | - | - | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | - | - | - | - | - | Richmond-Newport 500 kV Line | - | - | Mcg1Gm w/ Richmond-Newport 500 kV Line | - | - | Richmond-Newport 500 kV Line | 12 Hour Rating pushes out to 2019
| Post-Contingency Loading (MVA) | - | 421.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 398.8 | 455.8 | 457.3 | 485.8 | 487.3 | 465.2 | 466.7 | 457.5 | 459 | 427.2 | - | 522.4 | 522 | Cont Rating 437 MVA - Should use 12 Hour Rating 482 MVA
Harrisburg 230 kV Line | % Facility Rating | < 90% | 96.4% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 91.5% | 94.6% | 95% | 100.9% | 101.3% | 96.9% | 97.3% | 95.2% | 95.6% | 97.6% | < 90% | 108.3% | 108.3% | 750 Cu and 1" Cu Pipe Limited | Harrisburg 230 kV Line
(Harrisburg-Oakboro) | Year Upgrade Required | - | 2013 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 2014 | 2014 | 2011 | 2011 | 2013 | 2013 | 2014 | 2014 | 2013 | - | 2011 | 2011 | 954 ACSR Conductor 506.7 MVA | (Harrisburg-Oakboro)
| Contingency | - | Oco3Gm w/ Harrisburg 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Bel1Gm w/ Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Harrisburg 230 kV Line | Bel1Gm w/ Harrisburg 230 kV Line | - | Harrisburg 230 kV Line | Harrisburg 230 kV Line | 12 Hour Rating pushes out to 2018
| Post-Contingency Loading (MVA) | - | 87.1 | 88.7 | - | - | 86.7 | - | 86.8 | 86.5 | 90.4 | 89.2 | 93.1 | 87.3 | 91.2 | 97.5 | 101.4 | 92.5 | 96.4 | 90.3 | 91 | - | - | 93.5 | 88.5 | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 Hour Rating 96 MVA - Should use 12 Hour Rating 109.3 MVA
Clark Hill 115/100 kV | % Facility Rating | < 90% | 90.7% | 92.4% | < 90% | < 90% | 90.3% | < 90% | 90.5% | 90.1% | 94.2% | 93% | 91% | 90.9% | 95% | 101.6% | 105.6% | 96.4% | 100.4% | 94% | 94.8% | < 90% | < 90% | 97.4% | 92.2% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 556 ACSR Limited (Clearances to be measured) | Clark Hill 115/100 kV
Transformer | Year Upgrade Required | - | 2016 | 2015 | - | - | 2017 | - | 2017 | 2017 | 2015 | 2015 | 2013 | 2016 | 2014 | 2011 | 2011 | 2013 | 2011 | 2015 | 2014 | - | - | 2013 | 2016 | - | - | - | - | - | - | - | - | - | - | - | - | - | Transformer 173.3 MVA | Transformer
| Contingency | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | Oco1Gm w/ Whitewater 500 kV Line | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | Oco1Gm w/ Whitewater 500 kV Line | Oco1Gm w/ Whitewater 500 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 Hour Rating Correction pushes out to 2015
| Post-Contingency Loading (MVA) | - | - | 822.9 | - | - | - | - | - | - | - | - | 823.8 | - | 819.5 | - | 829.3 | - | 828.8 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 827.8 | - | - | - | 12 Hour Rating 889 MVA
Stamey 230 kV Line | % Facility Rating | < 90% | < 90% | 90.5% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.8% | < 90% | 90.3% | < 90% | 91.4% | < 90% | 91.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.9% | < 90% | < 90% | < 90% | 1600 Al Switch Limited | Stamey 230 kV Line
(Marshall-Stamey) | Year Upgrade Required | - | - | 2017 | - | - | - | - | - | - | - | - | 2016 | - | 2017 | - | 2016 | - | 2016 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | - | - | - | 2-954 ACSR Conductor 1176 MVA | (Marshall-Stamey)
| Contingency | - | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | - | - | - | - | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Bel1Gm w/ Stamey 230 kV Line | - | - | - | 1600 Al Switch Upgrade pushes out to 2020
| Post-Contingency Loading (MVA) | - | - | - | - | 723.3 | 725.9 | 709.9 | 712.6 | 688 | 690.2 | 668.2 | 676.3 | 675.6 | 677.6 | 656.1 | 664.3 | - | 663.5 | - | - | 679.4 | 665.3 | - | - | - | - | - | - | - | 706 | 710.4 | 692.2 | 696.7 | - | - | - | - | 12 Hour Rating 717 MVA
Clingman 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 99.8% | 100.3% | 97.7% | 98.2% | 94.6% | 95% | 91.8% | 93% | 92.8% | 93.2% | 90% | 91.3% | < 90% | 91.1% | < 90% | < 90% | 93.3% | 91.2% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 97.6% | 98.4% | 95.5% | 96.3% | < 90% | < 90% | < 90% | < 90% | CT/5 Ratio Limited | Clingman 230 kV Line
(Antioch-Mitchell River) | Year Upgrade Required | - | - | - | - | 2012 | 2011 | 2013 | 2012 | 2014 | 2014 | 2016 | 2015 | 2015 | 2015 | 2017 | 2016 | - | 2016 | - | - | 2015 | 2016 | - | - | - | - | - | - | - | 2013 | 2012 | 2014 | 2013 | - | - | - | - | 2-954 ACSR Conductor 1176 MVA | (Antioch-Mitchell River)
| Contingency | - | - | - | - | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | Mar3Gm w/ Clingman 230 kV Line | - | Mar3Gm w/ Clingman 230 kV Line | - | - | Bel1Gm w/ Clingman 230 kV Line | Bel1Gm w/ Clingman 230 kV Line | - | - | - | - | - | - | - | Clingman 230 kV Line | Clingman 230 kV Line | Clingman 230 kV Line | Clingman 230 kV Line | - | - | - | - | CT Upgrade pushes out to 2026
| Post-Contingency Loading (MVA) | - | - | - | - | 95.5 | 95.4 | 95 | 94.8 | 94.3 | 94.1 | 94.2 | 94 | 94.7 | 94.5 | - | - | - | - | - | - | 93.9 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Cont Rating 108.3 MVA - Should use 12 Hour Rating 118.6 MVA
Rugby 100 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | 91.8% | 91.6% | 91.2% | 91.1% | 90.5% | 90.4% | 90.5% | 90.3% | 91% | 90.8% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.1% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 300 Cu Limited | Rugby 100 kV Line
(Horseshoe-Pisgah) | Year Upgrade Required | - | - | - | - | 2016 | 2016 | 2016 | 2016 | 2017 | 2017 | 2017 | 2017 | 2016 | 2016 | - | - | - | - | - | - | 2017 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 477 ACSR Conductor 139.4 MVA | (Horseshoe-Pisgah)
| Contingency | - | - | - | - | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | Cli5Gm w/ Asheville 115 kV Line | - | - | - | - | - | - | Cli5Gm w/ Asheville 115 kV Line | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 12 Hour Rating pushes out to 2020
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 449 | - | - | 446.1 | 450.5 | - | - | - | - | 457.8 | - | 464.8 | 467.7 | 12 Hour Rating 478 MVA
Pleasant Garden 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 92.9% | < 90% | < 90% | 92.8% | 94.4% | < 90% | < 90% | < 90% | < 90% | 95.1% | < 90% | 97.6% | 99.4% | CT/5 Ratio Limited | Pleasant Garden 230 kV Line
(Belews Creek-Bob White Tap) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2015 | - | - | 2015 | 2014 | - | - | - | - | 2014 | - | 2013 | 2012 | 2156 ACSR Conductor 851.7 MVA | (Belews Creek-Bob White Tap)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ Godbey 500 kV Line | - | - | Godbey 500 kV Line | Godbey 500 kV Line | - | - | - | - | Oco1Gm w/ Godbey 500 kV Line | - | Godbey 500 kV Line | Godbey 500 kV Line | CT Upgrade pushes out to 2039
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 448.6 | - | - | - | - | - | - | - | - | 443.8 | - | - | - | 12 Hour Rating 478 MVA
Jocassee 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 91.3% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.1% | < 90% | < 90% | < 90% | CT/5 Ratio Limited | Jocassee 230 kV Line
(Oconee-Jocassee) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | - | - | - | - | - | - | - | - | 2017 | - | - | - | 2156 ACSR Conductor 851.7 MVA | (Oconee-Jocassee)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Oco1Gm w/ Katoma 500 kV Line | - | - | - | - | - | - | - | - | Oco1Gm w/ Katoma 500 kV Line | - | - | - | CT Upgrade pushes out to 2030
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 1270 | 1290.6 | 1293.7 | 1313.8 | - | - | - | - | 1289.5 | 1290.8 | 1320.9 | 1338.7 | 12 Hour Rating 1385.6 MVA
Parkwood 500 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 90.7% | 92.6% | 93.1% | 95.2% | < 90% | < 90% | < 90% | < 90% | 92.8% | 92.3% | 95.7% | 97.8% | 51XYZ Relay Limited | Parkwood 500 kV Line
(Parkwood-Pleasant Garden) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2016 | 2015 | 2015 | 2014 | - | - | - | - | 2015 | 2016 | 2014 | 2013 | 2-2515 ACSR Conductor 3739.4 MVA | (Parkwood-Pleasant Garden)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | - | - | - | - | Bel1gm w/ Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | Pleasant Garden 500/230 kV Transformer | 51XYZ Relays Upgrades (Blocked) pushes out to 2025
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 433.7 | 441.2 | - | - | - | - | - | - | - | - | 12 Hour Rating 478 MVA
Albright 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 96% | 99.9% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | CT/5 Ratio Limited | Albright 230 kV Line
(Eno-Pleasant Garden) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014 | 2012 | - | - | - | - | - | - | - | - | 954 ACSR Conductor 506.7 MVA | (Eno-Pleasant Garden)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Parkwood 500 kV Line | Parkwood 500 kV Line | - | - | - | - | - | - | - | - | Reconductor Required in 2014
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 678.3 | 723 | 12 Hour Rating 745 MVA
Method 230 kV Line | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 93.6% | 100.7% | CP&L Conductor Limited at 797 MVA (In Service 2008s) | Method 230 kV Line
(East Durham-Leesville) | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2015 | 2011 | 2-1272 ACSR Conductor 797 MVA | (East Durham-Leesville)
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Durham 230 kV Line | Durham 230 kV Line | 12 Hour Rating Correction pushes out to 2015
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.6 | 12 Hour Rating 100 MVA
Badin 115/100 kV | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 99.6% | Transformer Limited | Badin 115/100 kV
Transformer Bank 1 | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2012 | Transformer 100 MVA | Transformer Bank 1
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Richmond-Newport 500 kV Line | Increased Transformer Capacity Required in 2012
| Post-Contingency Loading (MVA) | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.6 | 12 Hour Rating 100 MVA
Badin 115/100 kV | % Facility Rating | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | < 90% | 94.6% | Transformer Limited | Badin 115/100 kV
Transformer Bank 2 | Year Upgrade Required | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 2014 | Transformer 100 MVA | Transformer Bank 2
| Contingency | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | Richmond-Newport 500 kV Line | Increased Transformer Capacity Required in 2014

## Base
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 133 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 56 | Not in original screening
[25 empty] | 189 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
DAN3GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.1 | 161.3 | 542 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.4 | 164.1 | 136.8 | 129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 247.2 | 120 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 74.6 | 118.5 | 110.8 | 49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96 | 214.3 | 105.4 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.2 | 112.4 | 105.1 | 51 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.2 | 503.2 | 103.2 | 68 | 478 | 250.2 | 388 | 79 | 1 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.2 | 503.2 | 103.2 | 69 | 478 | 250.2 | 388 | 79 | 2 | -24.2 | 2011 | 2019 | 8 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.2 | 24.2
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.3 | 306.1 | 102 | 1886 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.2 | 314.8 | 96.9 | 423 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2013 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 501.2 | 801.2 | 95.4 | 82 | 840 | 457.1 | 731.3 | 87.1 | 44 | -8.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 69.9 | 8.3
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 111 | -14.8 | 2014 | 2019 | 5 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.1 | 14.8
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.9 | 189.9 | 95 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.2 | 156 | 94.6 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 108.3 | 49.9 | 89.5 | 82.7 | 44 | -11.1 | 2015 | 2017 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12 | 11.1
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 435 | 745 | 93.5 | 87 | 796.7 | 390.3 | 670 | 84.1 | 44 | -9.4 | 2015 | 2016 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 75 | 9.4
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.5 | 364.5 | 93.5 | 554 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.5 | 139.4 | 93.2 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 71 | 188.2 | 92.9 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 452.5 | 277.7 | 420.8 | 91.4 | 45 | -0.7 | 2016 | 2012 | -4 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -1.6 | 0.7
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 43.5 | 86.2 | 91.6 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.2 | 438.6 | 90.7 | 252 | 478 | 313 | 411.3 | 84.6 | 44 | -6.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.3 | 6.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 478 | 330.1 | 367.5 | 78.9 | 1124 | -11.5 | 2017 | 2015 | -2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 13.3 | 11.5
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 418 | 758.7 | 90.3 | 44 | 840 | 381.2 | 692.7 | 82.5 | 40 | -7.8 | 2017 | 2017 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 66 | 7.8
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.3 | 963.3 | 90.3 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.1 | 165.2 | 90.3 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 27 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 3 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 30 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening
[25 empty] | 34 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 65.9 | 112.6 | 910 | 58.5 | - | 52.1 | 89.1 | 706 | -23.5 | 2011 | 2013 | 2 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 13.8 | 23.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464 | 97.1 | 232 | 478 | - | 380.4 | 79.6 | 100 | -17.5 | 2013 | 2019 | 6 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 83.6 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1804.3 | 94.8 | 910 | 1904.3 | - | 1541.1 | 80.9 | 868 | -13.9 | 2014 | 2018 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.2 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976.7 | 91.5 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.3 | 91.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Base Case | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Base\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Base Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 11 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 6 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Base Case | [5 empty] | 2007 Summer Screening | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Base Case
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.3 | 94.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.1 | 91.6 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976.7
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.8 | 91.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.3 | #N/A | 973.3
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Anson
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.4 | 1657.6 | 201.7 | 5292 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 511 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 110.3 | 220.4 | 147 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 109.7 | 220.4 | 147 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -22.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.9 | 163.8 | 136.8 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 617 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 56.3 | 81.8 | 130.7 | 660 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -17.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126 | 244 | 120.2 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 80 | 124.6 | 116.3 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -5.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 65.2 | 116.7 | 109.1 | 87 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.8 | 214.2 | 105.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 328.9 | 499.5 | 102.6 | 61 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 328.9 | 499.5 | 102.6 | 62 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 111.5 | 23.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.9 | 305.8 | 101.9 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 49.2 | 92.5 | 98.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -6.6 | 2012 | 2016 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 299.9 | 315.1 | 97 | 429 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 285.6 | 421.8 | 96.4 | 171 | 437 | 249.4 | 367.6 | 83.9 | 85 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 676 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 285.6 | 421.8 | 96.4 | 215 | 437 | 248.6 | 366.8 | 83.9 | 128 | -12.5 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 71.9 | 24.2
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.2 | 192.2 | 96.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.4 | 192 | 96 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 504.6 | 806.6 | 96 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.6 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 75.3 | 8.9
OCO3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 103.1 | 95.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.4 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 13.6 | 12.5
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1039.7 | 1319 | 95.1 | 8318 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1685.2 | 1859.4 | 95 | 7802 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.1 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 258.8 | 14.7
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76 | 155.8 | 94.4 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 146.4 | 187.9 | 94 | 54 | 200 | 140 | 176.3 | 88.1 | 12 | -5.9 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 351.8 | 393.5 | 93.9 | 1999 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -3.5 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 26 | 15
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 188.1 | 93 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 430.8 | 737.8 | 92.6 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.9 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 67.8 | 8.5
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.7 | 97.9 | 91.5 | 34 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.1 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420.8 | 763.8 | 90.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.6 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 71.1 | 8.4
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.4 | 438.8 | 90.8 | 258 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.5 | 6.2
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 279 | 412.9 | 90.8 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -7.9 | -0.6
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.7 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 53 | 90.6 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -12.1 | 2016 | 2024 | 8 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 73.3 | 125.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -12.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 21.2 | 36.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 459.8 | 96.2 | 232 | 478 | - | 464 | 97.1 | 232 | 0.9 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 79.4 | 16.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1800.2 | 94.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 259.1 | 13.6
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.4 | 91.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.2 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Anson | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Anson\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Anson Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Anson | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Anson
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CLI5GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
CLI5GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.1 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.4
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLI5GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 974.2
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.1 | 90.7 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.4 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.6 | 14.1 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 7 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 14 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
NANTGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1656.4 | 201.5 | 5676 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.3 | 161.4 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 765 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 60.3 | 87.5 | 139.7 | 808 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -26.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.8 | 163.2 | 136.2 | 94 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.5 | 243.2 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 82 | 126.3 | 117.9 | 68 | 108 | 74.6 | 118.5 | 110.8 | 49 | -7.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.8 | 117.5 | 109.9 | 89 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345 | 522.7 | 107.4 | 94 | 478 | 333.2 | 503.2 | 103.2 | 68 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345 | 522.7 | 107.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 69 | -4.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 134.7 | 28.4
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.5 | 213.6 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51.5 | 94.4 | 100.2 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -8.6 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76 | 134.1 | 100 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 461.7 | 790.2 | 99.2 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -5.7 | 2012 | 2015 | 3 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 120.2 | 15.1
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213 | 296.2 | 98.7 | 1830 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.3 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1751.8 | 1913.2 | 98.3 | 7908 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -3.2 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 312.6 | 18
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.9 | 195.4 | 97.7 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.2 | 195.1 | 97.6 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.8 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 304.2 | 314.8 | 96.9 | 614 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 148 | 193.3 | 96.7 | 62 | 200 | 140 | 176.3 | 88.1 | 12 | -8.6 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 343.3 | 373.9 | 95.9 | 726 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 502.8 | 803.6 | 95.7 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.3 | 8.6
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 446 | 783.4 | 93.3 | 52 | 840 | 420.2 | 738.3 | 87.9 | 44 | -5.4 | 2015 | 2018 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 119.4 | 14.2
DAN3GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 251.1 | 438.8 | 93.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -4.7 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.3 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.2 | 153.9 | 93.1 | 174 | 170 | 76.2 | 156 | 94.6 | 172 | 1.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1001.9 | 1289.2 | 93.1 | 5946 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 320.2 | 426.8 | 92.8 | 1162 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.3 | 100.5 | 92.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11 | 10.1
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.4 | 187.5 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 46.3 | 98.7 | 92.3 | 39 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 132 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 88.1 | 109.8 | 92 | 644 | 119 | 72.3 | 93 | 77.8 | 192 | -14.2 | 2016 | 2024 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 280.2 | 414.5 | 91.1 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -6.3 | -0.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.3 | 761 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.3 | 8.1
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 494.3 | 822.9 | 90.5 | 49 | 889 | 486.6 | 810.2 | 89 | 44 | -1.5 | 2017 | 2017 | 0 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 67.8 | 8.9
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.3 | 437.4 | 90.5 | 235 | 478 | 334.2 | 438.6 | 90.7 | 252 | 0.2 | 2017 | 2016 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.1 | 5.9
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 338.5 | 379.2 | 90 | 2133 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | 0.4 | 2017 | 2017 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 11.7 | 11.1
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 56.7 | 96.9 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -18.4 | 2013 | 2024 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.5 | 94.4 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77 | 131.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -19 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 24.9 | 42.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 99.9 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 476.2 | 99.6 | 244 | 478 | - | 464 | 97.1 | 232 | -2.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.8 | 20
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1873.1 | 98.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -3.6 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 332 | 17.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 68.4 | 96.1 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -15.7 | 2014 | 2023 | 9 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 24.6 | 34.5 | 87.5 | 56.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.2 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.9
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.7 | 92.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -4.1 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15.2 | 15.8 | #N/A | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.7 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960 | 983
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## Tillery-Blewett
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 10 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.2 | 1657.7 | 201.7 | 5099 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.1 | 161.3 | 529 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.3 | 216.5 | 144.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.6 | 216.5 | 144.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48 | 164.1 | 137.1 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | -0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 126.2 | 244.3 | 120.4 | 172 | 201 | 126 | 247.2 | 120 | 172 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 231 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 48 | 73.1 | 116.8 | 274 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -3.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 75.8 | 119.8 | 112 | 51 | 108 | 74.6 | 118.5 | 110.8 | 49 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.5 | 113.3 | 106 | 52 | 108 | 64.2 | 112.4 | 105.1 | 51 | -0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 96.1 | 214.7 | 105.8 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 333.8 | 503.7 | 103.3 | 69 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 333.8 | 503.7 | 103.3 | 70 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 115.7 | 24.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.1 | 306 | 102 | 1887 | 300 | 213.3 | 306.1 | 102 | 1886 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 423 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 503 | 804 | 95.7 | 82 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.3 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 72.7 | 8.6
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1690 | 1862.8 | 95.1 | 7752 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 262.2 | 14.8
TURNGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.8 | 189.7 | 94.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.1 | 189.5 | 94.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1035.9 | 1319.7 | 94.8 | 8025 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.6 | 155.9 | 94.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.2 | 365.7 | 93.8 | 580 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.9 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.8 | 188.3 | 93.1 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 433 | 741.5 | 93.1 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | 0.4 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 71.5 | 9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 44.7 | 87.6 | 93 | 8 | 95 | 43.5 | 86.2 | 91.6 | 5 | -1.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 282.3 | 417.7 | 91.8 | 46 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.3 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.1 | 0.4
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.9 | 382.9 | 90.9 | 2162 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.5 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.4 | 12
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335 | 439.6 | 90.9 | 261 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 28.3 | 6.3
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 419.5 | 761.3 | 90.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.3 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 68.6 | 8.1
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.1 | 963.1 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CLIFGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 67.4 | 115.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -2.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 15.3 | 26.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 464.7 | 97.2 | 232 | 478 | - | 464 | 97.1 | 232 | -0.1 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 84.3 | 17.6
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1805 | 94.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 263.9 | 13.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976 | 91.5 | 910 | 1067 | - | 976.7 | 91.5 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972.8 | 91.2 | 910 | 1067 | - | 973.3 | 91.2 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Tillery-Blewett | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Tillery-Blewett\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Tillery-Blewett Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Tillery-Blewett | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Tillery-Blewett
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.6
CAT1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
CLIFGM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.3 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976
CAT1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.8 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.1 | #N/A | 972.8
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 660.6 | 1675.7 | 203.9 | 5399 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.7 | 161.1 | 476 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.8 | 158.6 | 132.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.9 | 238.9 | 117.8 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 77 | 122.7 | 115 | 116 | 108 | 74.6 | 118.5 | 110.8 | 49 | -4.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 45.2 | 64.8 | 111.5 | 96 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 1.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67 | 116.7 | 109.4 | 95 | 108 | 64.2 | 112.4 | 105.1 | 51 | -4.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 554.2 | 885.3 | 105.4 | 140 | 840 | 501.2 | 801.2 | 95.4 | 82 | -10 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 154 | 18.3
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 309.6 | 103.2 | 1772 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.8 | 209.3 | 103.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 335.2 | 496 | 101.9 | 49 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 335.2 | 496 | 101.9 | 50 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 108 | 22.9
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -7.1 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 19.8 | 18.2
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 434.9 | 723.3 | 99.8 | 124 | 717 | 386.2 | 643 | 88 | 44 | -11.8 | 2012 | 2018 | 6 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 138.6 | 20.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 462.1 | 838.2 | 99.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -9.5 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 145.5 | 17.3
OXFDGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303.7 | 315.1 | 97 | 567 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.5 | 90.2 | 96.1 | 24 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.5 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1052.8 | 1325.7 | 95.5 | 8925 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -0.6 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83 | 105.6 | 95.2 | 455 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 347.1 | 371.4 | 95.2 | 928 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 71.8 | 155.6 | 94.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.3 | 189 | 94.5 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.6 | 188.7 | 94.4 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.7 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1650.3 | 1825.8 | 93.4 | 7950 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 1.7 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 225.2 | 13.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.6 | 391.4 | 93.2 | 2219 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.8 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 23.9 | 14.3
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 340.5 | 446.8 | 92.7 | 283 | 478 | 334.2 | 438.6 | 90.7 | 252 | -2 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 35.5 | 8.1
MCG2GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95.5 | 91.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.8 | 15.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.6 | 97.4 | 91.7 | 25 | 108 | 45.8 | 93.5 | 87.4 | 5 | -4.3 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318 | 419.2 | 91.2 | 1241 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 52.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 421.5 | 721.5 | 90.6 | 52 | 796.7 | 435 | 745 | 93.5 | 87 | 2.9 | 2016 | 2015 | -1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 51.5 | 6.5
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.5 | 182.9 | 90.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.4 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 106.8 | 180.8 | 90.4 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -4.8 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 107 | 180.9 | 90.4 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -4.7 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 237.1 | 422.8 | 90.4 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -1.9 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 469.9 | 98.3 | 248 | 478 | - | 464 | 97.1 | 232 | -1.2 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 89.5 | 18.7
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1761.8 | 92.5 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.3 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 220.7 | 11.6
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.9 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.6 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.1 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.3 | 92.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.1 | 982.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980.5 | 91.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_1200ImportDukeCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 16 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 661.8 | 1670.8 | 203.3 | 5380 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185 | 378.6 | 161.1 | 476 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.6 | 216.4 | 144.3 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.9 | 216.5 | 144.3 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.2 | 162.4 | 135.6 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.6 | 79.2 | 127.1 | 338 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -13.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.6 | 79.2 | 127.1 | 381 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -13.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.6 | 127.7 | 119.5 | 169 | 108 | 74.6 | 118.5 | 110.8 | 49 | -8.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.2 | 242.5 | 119.5 | 132 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.5 | 120.1 | 112.5 | 114 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 555.9 | 888.1 | 105.7 | 165 | 840 | 501.2 | 801.2 | 95.4 | 82 | -10.3 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 156.8 | 18.6
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.1 | 212.9 | 104.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 344.1 | 509.6 | 104.8 | 98 | 478 | 333.2 | 503.2 | 103.2 | 68 | -1.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 121.6 | 25.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 344.1 | 509.6 | 104.8 | 99 | 478 | 333.2 | 503.2 | 103.2 | 69 | -1.6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 121.6 | 25.8
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.5 | 95.5 | 101.6 | 39 | 95 | 43.5 | 86.2 | 91.6 | 5 | -10 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 436.5 | 725.9 | 100.3 | 125 | 717 | 386.2 | 643 | 88 | 44 | -12.3 | 2011 | 2018 | 7 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 141.2 | 21.1
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60.8 | 108.6 | 100.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -6.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 19.1 | 17.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60.8 | 108.6 | 100.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -6.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 19.1 | 17.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 463.6 | 840.9 | 100.1 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -9.8 | 2011 | 2017 | 6 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 148.2 | 17.6
CLIFGM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 297.4 | 99.1 | 1655 | 300 | 213.3 | 306.1 | 102 | 1886 | 2.9 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303 | 314.8 | 96.9 | 672 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.9 | 375.6 | 96.3 | 934 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.8 | 191.6 | 95.8 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.8 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.1 | 191.4 | 95.7 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.9 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1695.7 | 1860.3 | 95.7 | 8114 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 259.7 | 15.4
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49 | 101.3 | 94.8 | 36 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 440.2 | 752.9 | 94.5 | 53 | 796.7 | 435 | 745 | 93.5 | 87 | -1 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 82.9 | 10.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 150.4 | 188.8 | 94.4 | 156 | 200 | 140 | 176.3 | 88.1 | 12 | -6.3 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1018.9 | 1299 | 93.7 | 8553 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 1.2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 31.9 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.2 | 389.7 | 92.9 | 2220 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.5 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 22.2 | 14
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 339.7 | 445.8 | 92.6 | 260 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.9 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 34.5 | 8
WYLIGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 69.9 | 186.6 | 92.3 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.6 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.7 | 151.8 | 92 | 87 | 170 | 76.2 | 156 | 94.6 | 172 | 2.6 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 95.4 | 91.6 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.7 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.7 | 15.7
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 95.4 | 91.6 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.7 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.7 | 15.7
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 58.2 | 165.2 | 90.5 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.2 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.2 | 94.2 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.6 | 119.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.5 | 30
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479.1 | 100.2 | 248 | 478 | - | 464 | 97.1 | 232 | -3.1 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.7 | 20.6
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1812 | 95.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.4 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 270.9 | 14.3
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.6 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.4 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.2 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.4 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 982.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.3 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.4
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.7 | 90.3 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.2 | 13.7 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 1200ImportDukeCPLE_AEPVP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 3 | Not in original screening
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
THALGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 654.2 | 1666.6 | 202.8 | 5402 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 184.9 | 378.5 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.4 | 157.7 | 131.7 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 5.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.3 | 237.9 | 117.3 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 76.9 | 122.3 | 114.6 | 125 | 108 | 74.6 | 118.5 | 110.8 | 49 | -3.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.7 | 116.3 | 109 | 100 | 108 | 64.2 | 112.4 | 105.1 | 51 | -3.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 74 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 43.3 | 65.8 | 105.3 | 94 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 545.3 | 871.2 | 103.7 | 133 | 840 | 501.2 | 801.2 | 95.4 | 82 | -8.3 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 139.9 | 16.6
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 208.9 | 308.3 | 102.8 | 1720 | 300 | 213.3 | 306.1 | 102 | 1886 | -0.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.2 | 208.3 | 102.7 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 334 | 492.8 | 101.1 | 41 | 478 | 333.2 | 503.2 | 103.2 | 68 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 334 | 492.8 | 101.1 | 42 | 478 | 333.2 | 503.2 | 103.2 | 69 | 2.1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 104.8 | 22.1
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.7 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 18.3 | 16.8
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 454.7 | 824.9 | 98.2 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -7.9 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 132.2 | 15.7
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 426.7 | 709.9 | 97.7 | 90 | 717 | 386.2 | 643 | 88 | 44 | -9.7 | 2013 | 2018 | 5 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 125.2 | 18.5
CLI5GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.6 | 314.8 | 96.9 | 558 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 45.4 | 89.9 | 95.7 | 25 | 95 | 43.5 | 86.2 | 91.6 | 5 | -4.1 | 2014 | 2016 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.1 | 372.2 | 95.4 | 743 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 82.4 | 105.6 | 95.2 | 348 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 103.7 | 187.8 | 93.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 1.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103 | 187.5 | 93.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.8 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 70.2 | 153.9 | 93.6 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1021.2 | 1293.1 | 92.9 | 8615 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.9 | 388.3 | 92.4 | 2188 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.8 | 13.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 339.5 | 445.6 | 92.4 | 255 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.7 | 2015 | 2016 | 1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 34.3 | 7.8
OCO3GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 212 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1631 | 1802.2 | 92 | 7820 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 201.6 | 11.7
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.2 | 97 | 91.3 | 26 | 108 | 45.8 | 93.5 | 87.4 | 5 | -3.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 43.9 | 95 | 91.2 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.3 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.3 | 15.3
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 53.3 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 315.9 | 415.5 | 90.3 | 1016 | 478 | 315.6 | 414.1 | 89.8 | 696 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.1 | 182 | 90 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.9 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 62.9 | 107.5 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 5.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 10.8 | 18.4
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 468.2 | 97.9 | 248 | 478 | - | 464 | 97.1 | 232 | -0.8 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 87.8 | 18.3
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.2 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.9 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1740.1 | 91.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3.4 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 199 | 10.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.4 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.4 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 981.2
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 977.9
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_1200ImprtDukeCPLE_AEPVP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 16 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 656.3 | 1660.2 | 202 | 5338 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185 | 378.6 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 108.1 | 216.6 | 144.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 107.3 | 216.6 | 144.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -19.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 46.8 | 161.4 | 134.7 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.4 | 76.1 | 121.7 | 322 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -8.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.4 | 76.1 | 121.7 | 365 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -8.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.5 | 127.4 | 119.2 | 168 | 108 | 74.6 | 118.5 | 110.8 | 49 | -8.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 124.7 | 241.4 | 118.9 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.2 | 119.7 | 112.1 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 94.6 | 211.8 | 104.3 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 547.1 | 874.1 | 104.1 | 137 | 840 | 501.2 | 801.2 | 95.4 | 82 | -8.7 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 142.8 | 17
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 343 | 506.5 | 104.1 | 92 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118.5 | 25.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 343 | 506.5 | 104.1 | 93 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118.5 | 25.1
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.5 | 95.2 | 101.3 | 39 | 95 | 43.5 | 86.2 | 91.6 | 5 | -9.7 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 208.9 | 296.9 | 99 | 1621 | 300 | 213.3 | 306.1 | 102 | 1886 | 3 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 60 | 107.1 | 98.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.1 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 17.6 | 16.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 60 | 107.1 | 98.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.1 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 17.6 | 16.2
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 456.2 | 827.6 | 98.5 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -8.2 | 2012 | 2017 | 5 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 134.9 | 16
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 428.3 | 712.6 | 98.2 | 122 | 717 | 386.2 | 643 | 88 | 44 | -10.2 | 2012 | 2018 | 6 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 127.9 | 19
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.7 | 314.8 | 96.9 | 524 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.1 | 190.3 | 95.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.4 | 190.1 | 95.1 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.3 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 149.9 | 188.9 | 94.5 | 181 | 200 | 140 | 176.3 | 88.1 | 12 | -6.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.7 | 100.8 | 94.4 | 34 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 368.3 | 94.4 | 739 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1677.1 | 1837.5 | 94.2 | 8212 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.9 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 236.9 | 13.9
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 31.8 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 430.4 | 736.2 | 92.4 | 52 | 796.7 | 435 | 745 | 93.5 | 87 | 1.1 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 66.2 | 8.3
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 338.9 | 444.8 | 92.3 | 249 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.6 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 33.5 | 7.7
WYLIGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.7 | 92.2 | 172 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.5 | 386.6 | 92 | 2233 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.6 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 19.1 | 13.1
DAN3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 69.5 | 185.6 | 91.7 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.2 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 94.8 | 91.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.2 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.1 | 15.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 94.8 | 91.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.2 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7.1 | 15.2
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 986.8 | 1266.8 | 91.1 | 6114 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.8 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75 | 150.2 | 90.9 | 90 | 170 | 76.2 | 156 | 94.6 | 172 | 3.7 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 59.1 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.8 | 119.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.7 | 30.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 477.1 | 99.8 | 248 | 478 | - | 464 | 97.1 | 232 | -2.7 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 96.7 | 20.2
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1789.1 | 94 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.8 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 248 | 13.1
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 980.5 | 91.9 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.2 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_1200ImportDukeCPLE_AEPVP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_1200ImportDukeCPLE_AEPVP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_1200ImportDukeCPLE_AEPVP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.5 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.5 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 980.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.3 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 977.2
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.8 | 90.5 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.2 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.3 | 13.9 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 10 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665 | 1664.5 | 202.5 | 5198 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.7 | 161.1 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.4 | 136.1 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 92.9 | 186.8 | 124.6 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.6 | 246.3 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.4 | 74.7 | 119.4 | 262 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -6.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.4 | 74.7 | 119.4 | 305 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -6.1 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 80.6 | 126.2 | 118.1 | 164 | 108 | 74.6 | 118.5 | 110.8 | 49 | -7.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.8 | 118.7 | 111.2 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -6.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.6 | 213.4 | 105 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.3 | 305 | 101.7 | 1847 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 337.3 | 494.7 | 101.5 | 53 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 106.7 | 22.5
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 337.3 | 494.7 | 101.5 | 54 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 106.7 | 22.5
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 530.9 | 848.3 | 101 | 129 | 840 | 501.2 | 801.2 | 95.4 | 82 | -5.6 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 117 | 13.9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 49.5 | 94 | 100 | 36 | 95 | 43.5 | 86.2 | 91.6 | 5 | -8.4 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 59.2 | 105.7 | 97.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.8 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 16.2 | 14.9
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 59.2 | 105.7 | 97.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.8 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 16.2 | 14.9
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.1 | 314.8 | 96.9 | 382 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 442.7 | 803.3 | 95.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -5.3 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 110.6 | 13.1
LEE3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.7 | 189.6 | 94.8 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104 | 189.4 | 94.7 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 413.4 | 688 | 94.6 | 52 | 717 | 386.2 | 643 | 88 | 44 | -6.6 | 2014 | 2018 | 4 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 103.3 | 15.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 148.6 | 187.2 | 93.6 | 175 | 200 | 140 | 176.3 | 88.1 | 12 | -5.5 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 74.5 | 154.5 | 93.6 | 169 | 170 | 76.2 | 156 | 94.6 | 172 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.3 | 99.8 | 93.5 | 32 | 108 | 45.8 | 93.5 | 87.4 | 5 | -6.1 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345 | 362.4 | 92.9 | 577 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.6 | 187.5 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 337.6 | 443 | 91.8 | 242 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 31.7 | 7.2
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343 | 384.5 | 91.4 | 2195 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17 | 12.5
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1628.2 | 1792.4 | 91.3 | 7657 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 191.8 | 11
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 94.3 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.6 | 14.6
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 94.3 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.6 | 14.6
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.1 | 963.1 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.5 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | 150 | - | 140.7 | 93.8 | 88 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 68.6 | 117.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -4.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 16.5 | 28.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 471.2 | 98.6 | 248 | 478 | - | 464 | 97.1 | 232 | -1.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 90.8 | 19
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 976 | 91.5 | 910 | 1067 | - | 976.7 | 91.5 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972.6 | 91.2 | 910 | 1067 | - | 973.3 | 91.2 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1735.1 | 91.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3.7 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 194 | 10.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141 | 94 | 21 | 150 | - | 141.3 | 94.2 | 21 | 0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.6 | 92.3 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 975.4 | 91.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 976
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 972 | 91.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.1 | #N/A | 972.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.5 | 90.1 | 21 | 96 | - | 84.8 | 88.3 | 21 | -1.8 | 2017 | 2018 | 1 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13 | 13.5 | #N/A | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 13 | Not in original screening
[25 empty] | 24 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 658.9 | 1654 | 201.2 | 5766 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.9 | 161.2 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 62.9 | 91.4 | 145.9 | 703 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -32.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 62.9 | 91.4 | 145.9 | 747 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -32.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.5 | 162.4 | 135.5 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 88 | 134.1 | 125.3 | 287 | 108 | 74.6 | 118.5 | 110.8 | 49 | -14.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 124.9 | 242.1 | 119.2 | 131 | 201 | 126 | 247.2 | 120 | 172 | 0.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.4 | 123.9 | 115.9 | 139 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 57.4 | 102.2 | 108.5 | 88 | 95 | 43.5 | 86.2 | 91.6 | 5 | -16.9 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 348.8 | 514.1 | 105.5 | 124 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.1 | 26.5
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 348.8 | 514.1 | 105.5 | 125 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.1 | 26.5
THALGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95 | 212.6 | 104.7 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 156.6 | 204.3 | 102.1 | 275 | 200 | 140 | 176.3 | 88.1 | 12 | -14 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 532.3 | 850.7 | 101.3 | 129 | 840 | 501.2 | 801.2 | 95.4 | 82 | -5.9 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 119.4 | 14.2
STUDYS | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.7 | 133.7 | 99.5 | 214 | 131 | 55.2 | 98.1 | 72.9 | 43 | -26.6 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.8 | 105.1 | 98.3 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.9 | 2012 | 2018 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211 | 295 | 98.3 | 1760 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.7 | 195 | 97.5 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.5 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107 | 194.8 | 97.4 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.6 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | GUARDSOUTH | 546 | 8MCGUIRE | 836 | 8WOODLF | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.9 | 314.8 | 96.9 | 592 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.7 | 104.8 | 96.7 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.9 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.3 | 14
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.7 | 104.8 | 96.7 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.9 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.3 | 14
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 46.5 | 90.2 | 96.3 | 48 | 95 | 32.8 | 74.4 | 79.4 | 42 | -16.9 | 2013 | 2023 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 443.9 | 805.4 | 95.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -5.6 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 112.7 | 13.4
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 414.7 | 690.2 | 95 | 84 | 717 | 386.2 | 643 | 88 | 44 | -7 | 2014 | 2018 | 4 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 105.5 | 15.8
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1691 | 1844.9 | 94.4 | 8109 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.7 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 244.3 | 14.1
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 367.9 | 94.3 | 732 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.8 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 435.3 | 745 | 93.5 | 53 | 796.7 | 435 | 745 | 93.5 | 87 | 0 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 75 | 9.4
THRPGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.3 | 139.4 | 93.1 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 248.7 | 430.6 | 92.3 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.8 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.1 | 424.7 | 92.2 | 1048 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.8 | 92.2 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.5 | 152.4 | 92.2 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2.4 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.1 | 186.6 | 92.1 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.8 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.7 | 441.8 | 91.7 | 241 | 478 | 334.2 | 438.6 | 90.7 | 252 | -1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 30.5 | 7.1
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 41.7 | 97.5 | 91.6 | 31 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.9 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 88 | 109.2 | 91.4 | 607 | 119 | 72.3 | 93 | 77.8 | 192 | -13.6 | 2016 | 2024 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.8 | 382.9 | 91.1 | 2258 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.7 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.4 | 12.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.3 | 94.1 | 90.4 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.5 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.4 | 14.5
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.3 | 94.1 | 90.4 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.5 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.4 | 14.5
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 57.3 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 59.2 | 101.1 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -22.6 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.3 | 94.2 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 5 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 79.7 | 136.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -23.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 27.6 | 47.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 483.3 | 101.1 | 248 | 478 | - | 464 | 97.1 | 232 | -4 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 102.9 | 21.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 99.9 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1802.1 | 94.6 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 261 | 13.7
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.8 | 92.1 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.6 | 90.3 | 455 | 96 | - | 81.1 | 84.5 | 455 | -5.8 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 16.9 | 17.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 70.9 | 99.6 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -19.2 | 2012 | 2023 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 27.1 | 38 | 91.4 | 59.2 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.3 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 90.4 | 94.2 | 21 | 96 | - | 84.8 | 88.3 | 21 | -5.9 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 16.9 | 17.6 | #N/A | #N/A | 86.6
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.4 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 982.8
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 979.3
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.8 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SOCO
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 671.1 | 1670.8 | 203.3 | 5281 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.2 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.2 | 163.6 | 136.4 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 53.7 | 78.1 | 124.9 | 399 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -11.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 53.7 | 78.1 | 124.9 | 442 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -11.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 83.5 | 130.3 | 121.9 | 231 | 108 | 74.6 | 118.5 | 110.8 | 49 | -11.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.6 | 243.1 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 68.6 | 122.3 | 114.6 | 135 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.8 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 52.6 | 98.2 | 104.5 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -12.9 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 344.1 | 504 | 103.4 | 94 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116 | 24.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 344.1 | 504 | 103.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116 | 24.4
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 304.8 | 101.6 | 1890 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 517.9 | 827.6 | 98.5 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -3.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 96.3 | 11.4
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 50.1 | 103.5 | 96.9 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.5 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.1 | 314.8 | 96.9 | 428 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.3 | 104.2 | 96.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.4 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 14.7 | 13.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.3 | 104.2 | 96.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -2.4 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 14.7 | 13.5
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.9 | 191.8 | 95.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.9 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 153.3 | 191.6 | 95.8 | 222 | 200 | 140 | 176.3 | 88.1 | 12 | -7.7 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.2 | 191.5 | 95.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.6 | 155.1 | 94 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.6 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.8 | 364.9 | 93.6 | 653 | 390 | 344.5 | 364.5 | 93.5 | 554 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 431.9 | 783.6 | 93.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -3 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 90.9 | 10.8
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1647.2 | 1813.8 | 92.6 | 7801 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 2.5 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 213.2 | 12.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.8 | 388.2 | 92.4 | 2256 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.7 | 13.5
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 41.7 | 86.3 | 92.3 | 43 | 95 | 32.8 | 74.4 | 79.4 | 42 | -12.9 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 401.5 | 668.2 | 91.8 | 49 | 717 | 386.2 | 643 | 88 | 44 | -3.8 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 83.5 | 12.6
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.2 | 441.1 | 91.5 | 240 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.8 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.8 | 6.9
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 997.2 | 1272.4 | 91.3 | 7380 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.6 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.6 | 94.2 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.5 | 14.6
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.6 | 94.2 | 90.5 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.6 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.5 | 14.6
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.1 | 964.1 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 43 | 95.9 | 90.2 | 23 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 316.6 | 415.4 | 90.2 | 774 | 478 | 315.6 | 414.1 | 89.8 | 696 | -0.4 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70.9 | 121.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -8.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 18.8 | 32.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 478 | 100 | 248 | 478 | - | 464 | 97.1 | 232 | -2.9 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 97.6 | 20.4
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1755.6 | 92.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.6 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 214.5 | 11.3
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.9 | 91.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.5 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SOCO
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.2 | 93 | 21 | 96 | - | 84.8 | 88.3 | 21 | -4.7 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15.7 | 16.4 | #N/A | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.5 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.9
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 975.1 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.1 | #N/A | 974.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SOCO
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 12 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 13 | Not in original screening
[25 empty] | 25 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665.7 | 1661.8 | 202.2 | 5850 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 0.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.4 | 161.4 | 478 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 67.3 | 97.9 | 156.9 | 791 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -43.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 67.3 | 97.9 | 156.9 | 835 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -43.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.6 | 162.8 | 135.8 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 90.9 | 138.2 | 129.1 | 380 | 108 | 74.6 | 118.5 | 110.8 | 49 | -18.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.3 | 242.8 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 69.1 | 127.5 | 119.3 | 147 | 108 | 64.2 | 112.4 | 105.1 | 51 | -14.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 60.4 | 106.4 | 113 | 89 | 95 | 43.5 | 86.2 | 91.6 | 5 | -21.4 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 358.2 | 529.7 | 109 | 150 | 478 | 333.2 | 503.2 | 103.2 | 68 | -5.8 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 141.7 | 30
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 358.2 | 529.7 | 109 | 151 | 478 | 333.2 | 503.2 | 103.2 | 69 | -5.8 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 141.7 | 30
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.3 | 213.2 | 105 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 161.3 | 208.7 | 104.4 | 382 | 200 | 140 | 176.3 | 88.1 | 12 | -16.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 50.6 | 108.7 | 101.7 | 48 | 108 | 45.8 | 93.5 | 87.4 | 5 | -14.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 49.5 | 94.4 | 100.8 | 67 | 95 | 32.8 | 74.4 | 79.4 | 42 | -21.4 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76 | 134 | 100 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 523.2 | 836.2 | 99.5 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 104.9 | 12.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108.9 | 197.2 | 98.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -3.6 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 108.2 | 197 | 98.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -3.7 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.8 | 294.9 | 98.3 | 1844 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.2 | 315.1 | 97 | 771 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.3 | 375.4 | 96.3 | 941 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1717.6 | 1869.7 | 95.6 | 8033 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.5 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 269.1 | 15.3
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57.8 | 103.2 | 95.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.5 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 13.7 | 12.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57.8 | 103.2 | 95.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.5 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 13.7 | 12.6
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 43.5 | 101.1 | 95 | 38 | 108 | 38.7 | 85.9 | 80.7 | 1 | -14.3 | 2014 | 2022 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 442.6 | 757.2 | 95 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | -1.5 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 87.2 | 10.9
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 436.4 | 791.7 | 94.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 99 | 11.8
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 90 | 111.7 | 93.7 | 662 | 119 | 72.3 | 93 | 77.8 | 192 | -15.9 | 2015 | 2024 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 252.7 | 441.1 | 93.7 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.2 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 321 | 428.3 | 93.2 | 1165 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3.4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.7 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 406.3 | 676.3 | 93 | 51 | 717 | 386.2 | 643 | 88 | 44 | -5 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 91.6 | 13.8
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 168 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 80.6 | 153 | 92.6 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187 | 92.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 166 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 77.1 | 88.4 | 92.1 | 494 | 96 | 69 | 80.4 | 83.8 | 350 | -8.3 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 19.2 | 20
OCO3GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343.5 | 384.3 | 91.4 | 2267 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 16.8 | 12.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335.3 | 440 | 91.4 | 239 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.7 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 28.7 | 6.8
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 494.9 | 823.8 | 90.8 | 47 | 889 | 486.6 | 810.2 | 89 | 44 | -1.8 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 68.7 | 9.2
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.8 | 94 | 90.3 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.4 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.3 | 14.4
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.8 | 94 | 90.3 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.4 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.3 | 14.4
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 117.5 | 153.9 | 90.2 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -5.1 | 2017 | 2020 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 322.5 | 422.3 | 90.2 | 671 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.5 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 63.6 | 108.7 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -30.2 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.3 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 82 | 140.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -27.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 29.9 | 51
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 490.1 | 102.5 | 256 | 478 | - | 464 | 97.1 | 232 | -5.4 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 109.7 | 22.9
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100.1 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1800.6 | 94.6 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 259.5 | 13.7
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.3 | 93.1 | 455 | 96 | - | 81.1 | 84.5 | 455 | -8.6 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 19.6 | 20.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.5 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 986 | 92.4 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.9 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.6 | 92.1 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SOCO | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SOCO\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SOCO Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SOCO | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SOCO
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 73.2 | 102.8 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -22.4 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 29.4 | 41.2 | 97.9 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.1 | 97 | 21 | 96 | - | 84.8 | 88.3 | 21 | -8.7 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 19.6 | 20.4 | 88.4 | #N/A | 89.3
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.4 | 94.9 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88.1
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.4 | 92.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.3 | 986
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980 | 91.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 982.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 292.6 | 90 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.1 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_TVA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 669.1 | 1668.5 | 203 | 5278 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.3 | 378.9 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.2 | 163.5 | 136.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.4 | 76.2 | 121.8 | 325 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -8.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.4 | 76.2 | 121.8 | 368 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -8.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 82 | 128.2 | 120 | 213 | 108 | 74.6 | 118.5 | 110.8 | 49 | -9.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 246.6 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 67.7 | 120.5 | 112.9 | 128 | 108 | 64.2 | 112.4 | 105.1 | 51 | -7.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 342 | 501.5 | 102.9 | 90 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.5 | 23.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 342 | 501.5 | 102.9 | 91 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.3 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.5 | 23.9
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51 | 96.1 | 102.2 | 41 | 95 | 43.5 | 86.2 | 91.6 | 5 | -10.6 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.9 | 304.9 | 101.6 | 1890 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 522.8 | 835.4 | 99.5 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.1 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 104.1 | 12.4
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 59.4 | 107.4 | 99.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.4 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 17.9 | 16.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 59.4 | 107.4 | 99.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -5.4 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 17.9 | 16.5
ALL4GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 301.4 | 315.3 | 97 | 387 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105.4 | 190.9 | 95.4 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.7 | 190.7 | 95.3 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49.3 | 101.7 | 95.2 | 37 | 108 | 45.8 | 93.5 | 87.4 | 5 | -7.8 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GTFLGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 150.9 | 189.2 | 94.6 | 173 | 200 | 140 | 176.3 | 88.1 | 12 | -6.5 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 435.9 | 791 | 94.2 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -3.9 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 98.3 | 11.7
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.2 | 155 | 93.9 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.7 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 364.5 | 93.4 | 632 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 27.8 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 406 | 675.6 | 92.8 | 49 | 717 | 386.2 | 643 | 88 | 44 | -4.8 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 90.9 | 13.6
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1642.6 | 1809.1 | 92.3 | 7829 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 2.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 208.5 | 12
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.1 | 387.4 | 92.2 | 2242 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 19.9 | 13.3
STUDYL | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.8 | 441.9 | 91.6 | 240 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.9 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 30.6 | 7
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 994.9 | 1270.2 | 91.1 | 7308 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | 3.8 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.4 | 94.7 | 91 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.1 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7 | 15.1
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.4 | 94.7 | 91 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -2.1 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 7 | 15.1
JOC1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 963.4 | 963.4 | 90.3 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.1 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.7 | 93.8 | 88 | 150 | - | 140.7 | 93.8 | 88 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.7 | 119.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -6.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.6 | 30
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 475.9 | 99.6 | 248 | 478 | - | 464 | 97.1 | 232 | -2.5 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.5 | 20
ALL4GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1750.6 | 91.9 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.9 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 209.5 | 11
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 977.2 | 91.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.8 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from TVA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.7 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.7
ALL5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.1 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 977.2
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 974.7 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.4 | #N/A | 973.8
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.3 | 90.9 | 21 | 96 | - | 84.8 | 88.3 | 21 | -2.6 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 13.8 | 14.3 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_TVA
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 12 | Not in original screening
[25 empty] | 22 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 663.1 | 1658.9 | 201.8 | 5843 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.4 | 379.1 | 161.3 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 66 | 96 | 153.8 | 739 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -40.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 66 | 96 | 153.8 | 783 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -40.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.6 | 162.7 | 135.8 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 89.4 | 136.1 | 127.2 | 346 | 108 | 74.6 | 118.5 | 110.8 | 49 | -16.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.3 | 242.7 | 119.5 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 68.3 | 125.7 | 117.6 | 144 | 108 | 64.2 | 112.4 | 105.1 | 51 | -12.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 58.8 | 104.2 | 110.7 | 85 | 95 | 43.5 | 86.2 | 91.6 | 5 | -19.1 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 353.8 | 519.8 | 106.9 | 141 | 478 | 333.2 | 503.2 | 103.2 | 68 | -3.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 131.8 | 27.9
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 353.8 | 519.8 | 106.9 | 142 | 478 | 333.2 | 503.2 | 103.2 | 69 | -3.7 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 131.8 | 27.9
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.2 | 212.9 | 104.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 159 | 206.3 | 103.2 | 338 | 200 | 140 | 176.3 | 88.1 | 12 | -15.1 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 49.8 | 106.9 | 100 | 45 | 108 | 45.8 | 93.5 | 87.4 | 5 | -12.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.9 | 133.9 | 99.9 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -27 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 524.1 | 837.5 | 99.7 | 127 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.3 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 106.2 | 12.6
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 47.9 | 92.3 | 98.5 | 50 | 95 | 32.8 | 74.4 | 79.4 | 42 | -19.1 | 2012 | 2023 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.6 | 295 | 98.3 | 1810 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.7 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108.4 | 196.3 | 98.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -3.2 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.7 | 196.1 | 98 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -3.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.8 | 105.1 | 97 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.2 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.6 | 14.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.8 | 105.1 | 97 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.2 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.6 | 14.3
DAN3GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.1 | 315.2 | 97 | 731 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 373.1 | 95.7 | 871 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1704.2 | 1859.9 | 95.4 | 8115 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 259.3 | 15.1
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 440.9 | 754.5 | 94.7 | 54 | 796.7 | 435 | 745 | 93.5 | 87 | -1.2 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 84.5 | 10.6
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 437.1 | 793 | 94.4 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4.1 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 100.3 | 11.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 42.6 | 99.3 | 93.3 | 34 | 108 | 38.7 | 85.9 | 80.7 | 1 | -12.6 | 2015 | 2022 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 407.2 | 677.6 | 93.2 | 54 | 717 | 386.2 | 643 | 88 | 44 | -5.2 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 92.9 | 14
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 251.3 | 439 | 93.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -4.7 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 34.5 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 89.2 | 110.8 | 92.8 | 612 | 119 | 72.3 | 93 | 77.8 | 192 | -15 | 2015 | 2024 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 320.2 | 426.9 | 92.8 | 1160 | 478 | 315.6 | 414.1 | 89.8 | 696 | -3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 169 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.9 | 152.8 | 92.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 2.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 186.9 | 92.3 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.6 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.7 | 92.2 | 160 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.8 | 385.7 | 91.8 | 2255 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.4 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 18.2 | 12.9
RIV7GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 335.7 | 440.5 | 91.5 | 239 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.8 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.2 | 6.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44.6 | 94.5 | 90.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.8 | 14.9
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44.6 | 94.5 | 90.8 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.9 | 2016 | 2017 | 1 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.8 | 14.9
FISHGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 492.3 | 819.5 | 90.3 | 47 | 889 | 486.6 | 810.2 | 89 | 44 | -1.3 | 2017 | 2017 | 0 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 64.4 | 8.7
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.8 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 75.1 | 86.5 | 90.1 | 482 | 96 | 69 | 80.4 | 83.8 | 350 | -6.3 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 17.3 | 18
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 62.4 | 106.6 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -28.1 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.1 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 80.7 | 138 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -25.4 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 28.6 | 48.9
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 488.1 | 102.1 | 256 | 478 | - | 464 | 97.1 | 232 | -5 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 107.7 | 22.5
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100.1 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1817.5 | 95.4 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 276.4 | 14.5
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985 | 92.3 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 981.6 | 92 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.4 | 91 | 455 | 96 | - | 81.1 | 84.5 | 455 | -6.5 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 17.7 | 18.4
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_TVA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_TVA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_TVA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_TVA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_TVA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 71.9 | 101 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -20.6 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 28.1 | 39.4 | 96 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 91.2 | 95 | 21 | 96 | - | 84.8 | 88.3 | 21 | -6.7 | 2014 | 2018 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 17.7 | 18.4 | 86.5 | #N/A | 87.4
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.2 | 94.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 88
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.6 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.1 | 985
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.3 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 981.6
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.6 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 677.2 | 1678.1 | 204.2 | 5337 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.7 | 379.4 | 161.4 | 509 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 60.5 | 87.9 | 140.5 | 571 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -27.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 60.5 | 87.9 | 140.5 | 615 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -27.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.7 | 136.5 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 91.4 | 141.4 | 132.3 | 363 | 108 | 74.6 | 118.5 | 110.8 | 49 | -21.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 73.4 | 132 | 123.7 | 177 | 108 | 64.2 | 112.4 | 105.1 | 51 | -18.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 243.5 | 119.9 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 61 | 109.8 | 116.8 | 85 | 95 | 43.5 | 86.2 | 91.6 | 5 | -25.2 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 55 | 113.3 | 106.2 | 59 | 108 | 45.8 | 93.5 | 87.4 | 5 | -18.8 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.6 | 213.8 | 105.3 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 50.1 | 97.9 | 104.7 | 66 | 95 | 32.8 | 74.4 | 79.4 | 42 | -25.3 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345.4 | 505 | 103.6 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 117 | 24.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345.4 | 505 | 103.6 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 117 | 24.6
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 165.9 | 204.2 | 102.1 | 641 | 200 | 140 | 176.3 | 88.1 | 12 | -14 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.4 | 304.4 | 101.5 | 1858 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 47.9 | 105.7 | 99.5 | 44 | 108 | 38.7 | 85.9 | 80.7 | 1 | -18.8 | 2012 | 2022 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.4 | 194.5 | 97.2 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.7 | 194.2 | 97.1 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.3 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRBK1 | 233 | 6BUSH RV | 42004 | 6PARR | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 81.4 | 93.1 | 97 | 693 | 96 | 69 | 80.4 | 83.8 | 350 | -13.2 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 23.9 | 24.9
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 509.9 | 815 | 97 | 124 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.6 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 83.7 | 9.9
GTFLGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.7 | 314.8 | 96.9 | 433 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.2 | 155.3 | 94.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 101.8 | 94 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.2 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.3 | 11.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 101.8 | 94 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.2 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.3 | 11.3
TUXDGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.6 | 362.9 | 93.1 | 639 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.8 | 92.8 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 346.3 | 387.6 | 92.2 | 2279 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.1 | 13.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1643.7 | 1806.1 | 92.1 | 7618 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 205.5 | 11.8
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 425.3 | 771.7 | 91.9 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.6 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 79 | 9.4
OXFDGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.5 | 438.9 | 91 | 216 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.3 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.6 | 6.4
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318.3 | 419.6 | 90.9 | 1081 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.2 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 394.2 | 656.1 | 90 | 47 | 717 | 386.2 | 643 | 88 | 44 | -2 | 2017 | 2018 | 1 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 71.4 | 10.8
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 237.8 | 423.8 | 90 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -1.5 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 57 | 97.4 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -18.9 | 2013 | 2024 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.2 | 94.1 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77.3 | 132.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -19.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 25.2 | 43
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479.3 | 100.3 | 248 | 478 | - | 464 | 97.1 | 232 | -3.2 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.9 | 20.7
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.7 | 97.6 | 455 | 96 | - | 81.1 | 84.5 | 455 | -13.1 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 24 | 25
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1751.1 | 92 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 2.8 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 210 | 11.1
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.9 | 91.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.5 | 91.5 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 97.5 | 101.6 | 21 | 96 | - | 84.8 | 88.3 | 21 | -13.3 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 24 | 25 | 93.1 | #N/A | 93.7
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 68.5 | 96.2 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -15.8 | 2013 | 2023 | 10 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 24.7 | 34.6 | 87.9 | 57 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.2 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 87.9
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 980.3 | 91.9 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 979.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976.9 | 91.6 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 976.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 14 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 14 | Not in original screening
[25 empty] | 28 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 672.9 | 1669.6 | 203.1 | 5920 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 74 | 107.6 | 172.5 | 942 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -59.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 74 | 107.6 | 172.5 | 986 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -59.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.6 | 161.5 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 99 | 149.5 | 139.7 | 666 | 108 | 74.6 | 118.5 | 110.8 | 49 | -28.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.5 | 162.8 | 135.9 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 73.9 | 137.3 | 128.6 | 170 | 108 | 64.2 | 112.4 | 105.1 | 51 | -23.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 68.9 | 118 | 125.4 | 205 | 95 | 43.5 | 86.2 | 91.6 | 5 | -33.8 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.5 | 242.9 | 119.6 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 57.9 | 106 | 113.3 | 93 | 95 | 32.8 | 74.4 | 79.4 | 42 | -33.9 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 55.5 | 118.6 | 111.1 | 82 | 108 | 45.8 | 93.5 | 87.4 | 5 | -23.7 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 174.2 | 221.5 | 110.7 | 790 | 200 | 140 | 176.3 | 88.1 | 12 | -22.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 359.5 | 530.7 | 109.2 | 150 | 478 | 333.2 | 503.2 | 103.2 | 68 | -6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.7 | 30.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 359.5 | 530.7 | 109.2 | 151 | 478 | 333.2 | 503.2 | 103.2 | 69 | -6 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.7 | 30.2
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.4 | 213.3 | 105.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 48.4 | 111 | 104.4 | 46 | 108 | 38.7 | 85.9 | 80.7 | 1 | -23.7 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 85.3 | 97.6 | 101.7 | 681 | 96 | 69 | 80.4 | 83.8 | 350 | -17.9 | 2011 | 2020 | 9 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 28.4 | 29.6
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 76.9 | 134.6 | 101 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -28.1 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 110.4 | 199.9 | 99.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -4.9 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 109.6 | 199.6 | 99.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -5 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 294.5 | 98.2 | 1847 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.8 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 515.3 | 823.6 | 98 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.6 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 92.3 | 10.9
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20723 | CAMD JCT 115 | 20734 | WATRE 115 | 1 | 20723-20734-1 | 131 | 131 | 53.2 | 124.1 | 97.4 | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2013 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 305.3 | 315.6 | 97.1 | 851 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.2 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.3 | 375.6 | 96.3 | 977 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 92.5 | 114.4 | 96.2 | 947 | 119 | 72.3 | 93 | 77.8 | 192 | -18.4 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 444.1 | 759.9 | 95.4 | 57 | 796.7 | 435 | 745 | 93.5 | 87 | -1.9 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 89.9 | 11.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1706.4 | 1858.7 | 95.2 | 8183 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.1 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 258.1 | 14.9
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 256.2 | 445.1 | 94.9 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -6.4 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 322.7 | 431.4 | 94.1 | 1165 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.3 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 35.2 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.4 | 100.8 | 93.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.7 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.3 | 10.4
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.4 | 100.8 | 93.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.7 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.3 | 10.4
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 429.7 | 779.8 | 92.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.5 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 87.1 | 10.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 172 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.2 | 153.2 | 92.8 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187.1 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.7 | 92.2 | 202 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 498.2 | 829.3 | 91.4 | 51 | 889 | 486.6 | 810.2 | 89 | 44 | -2.4 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 74.2 | 9.8
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 399 | 664.3 | 91.3 | 48 | 717 | 386.2 | 643 | 88 | 44 | -3.3 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 79.6 | 12.1
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344 | 383.6 | 91.3 | 2394 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.9 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 16.1 | 12.4
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 325.1 | 425.3 | 91 | 995 | 478 | 306.7 | 403.9 | 85.7 | 343 | -5.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 118.1 | 154.8 | 90.9 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -5.8 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.8 | 437.9 | 90.9 | 230 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.6 | 6.3
DAN3GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.6 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20524 | JACKSONV 230 | 20528 | RHEMS 230 | 1 | 20524-20528-1 | 478 | 478 | 230.9 | 417.2 | 90.2 | 86 | 478 | 208.3 | 390.9 | 83.8 | 43 | -6.4 | 2017 | 2020 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 2 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70 | 119.7 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -41.2 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.2 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | - | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 100.1 | 92.6 | 124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.6 | 91.2 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 963.2 | 90.3 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 959.9 | 90 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 88.4 | 151.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -38.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 36.3 | 62
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 491.4 | 102.8 | 260 | 478 | - | 464 | 97.1 | 232 | -5.7 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 111 | 23.2
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 97.6 | 101.6 | 455 | 96 | - | 81.1 | 84.5 | 455 | -17.1 | 2011 | 2020 | 9 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 27.9 | 29
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1796.4 | 94.3 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.5 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 255.3 | 13.4
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.4 | 93 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 988.9 | 92.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.5 | 92.4 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 352 | 90.3 | 455 | 390 | - | 345.2 | 88.5 | 455 | -1.8 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 79.8 | 112 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -31.6 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 36 | 50.4 | #N/A | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 101.4 | 105.6 | 21 | 96 | - | 84.8 | 88.3 | 21 | -17.3 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 27.9 | 29 | 97.6 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | 27.5 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.6 | 95.1 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 142 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.5 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.6 | 88.4
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.5 | 92.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.2 | 988.9
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.7 | 92.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 959.9 | 985.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
STUDYL | BADX | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 98.3 | 91 | 42 | 108 | - | 69.1 | 64 | 42 | -27 | 2016 | 2034 | 18 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 149.5 | 100.1 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.5 | 90.3 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.6 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.7 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 10 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
RIV7GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 678.7 | 1679.1 | 204.3 | 5380 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.4 | 161.5 | 511 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 61.2 | 88.9 | 142.1 | 617 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -28.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 61.2 | 88.9 | 142.1 | 661 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -28.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48 | 163.6 | 136.5 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 90.9 | 140.2 | 131.2 | 354 | 108 | 74.6 | 118.5 | 110.8 | 49 | -20.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.8 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.8 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 72.2 | 130.6 | 122.4 | 186 | 108 | 64.2 | 112.4 | 105.1 | 51 | -17.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 243.5 | 119.9 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 60.6 | 108.6 | 115.6 | 87 | 95 | 43.5 | 86.2 | 91.6 | 5 | -24 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 214 | 105.4 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 53.9 | 111.9 | 104.9 | 56 | 108 | 45.8 | 93.5 | 87.4 | 5 | -17.5 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 49.7 | 96.7 | 103.4 | 65 | 95 | 32.8 | 74.4 | 79.4 | 42 | -24 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 345.2 | 504.5 | 103.4 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.5 | 24.4
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 345.2 | 504.5 | 103.4 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.2 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.5 | 24.4
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 164.3 | 204.4 | 102.2 | 555 | 200 | 140 | 176.3 | 88.1 | 12 | -14.1 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.4 | 304.2 | 101.4 | 1857 | 300 | 213.3 | 306.1 | 102 | 1886 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 46.8 | 104.3 | 98.1 | 42 | 108 | 38.7 | 85.9 | 80.7 | 1 | -17.4 | 2012 | 2022 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 108 | 195.5 | 97.7 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107.2 | 195.3 | 97.6 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.8 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 509.4 | 814.2 | 96.9 | 124 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.5 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 82.9 | 9.8
LOOKGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 303.1 | 314.8 | 96.9 | 434 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 76.3 | 155.3 | 94.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.7 | 93.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.2 | 11.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.7 | 93.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.1 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.2 | 11.2
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 28.7 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.6 | 362.7 | 93 | 620 | 390 | 344.5 | 364.5 | 93.5 | 554 | 0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
GASTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 138 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.8 | 92.8 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THRPGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 424.8 | 770.9 | 91.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.5 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 78.2 | 9.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1640.5 | 1800.3 | 91.8 | 7655 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 3.3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 199.7 | 11.5
OCO1GM | HODGBK1LONG | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 76.5 | 88 | 91.6 | 487 | 96 | 69 | 80.4 | 83.8 | 350 | -7.8 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 18.8 | 19.5
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 344.3 | 384.8 | 91.5 | 2243 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17.3 | 12.6
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.1 | 421.1 | 91.3 | 1154 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.7 | 439.2 | 91.1 | 219 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.4 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.9 | 6.5
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 239.6 | 426.1 | 90.5 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LOOKGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FISHGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.1 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 57.6 | 98.5 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -20 | 2012 | 2024 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.4 | 94.3 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.6 | 91.2 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 77.9 | 133.1 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -20.5 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 25.8 | 44
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 479 | 100.2 | 248 | 478 | - | 464 | 97.1 | 232 | -3.1 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 98.6 | 20.6
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.8 | 92.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -8 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 19.1 | 19.9
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.2 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1747.3 | 91.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 206.2 | 10.9
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.8 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 69.1 | 97.1 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -16.7 | 2013 | 2023 | 10 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 25.3 | 35.5 | 88.9 | 57.6 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 92.5 | 96.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -8.1 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 19 | 19.8 | 88 | #N/A | 88.8
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.4 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.6 | 88
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.6 | 92 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960.2 | 981.2
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.1 | 91.7 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 977.8
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 16 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 14 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 676 | 1672.8 | 203.5 | 5918 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 74.7 | 108.6 | 174.1 | 992 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -60.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CDCKGM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 74.7 | 108.6 | 174.1 | 1036 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -60.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.9 | 379.7 | 161.6 | 514 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 98.5 | 148.2 | 138.6 | 658 | 108 | 74.6 | 118.5 | 110.8 | 49 | -27.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 47.4 | 162.8 | 135.9 | 86 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 72.8 | 135.8 | 127.2 | 170 | 108 | 64.2 | 112.4 | 105.1 | 51 | -22.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 68.4 | 116.8 | 124.1 | 202 | 95 | 43.5 | 86.2 | 91.6 | 5 | -32.5 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.4 | 242.9 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 57.5 | 104.8 | 112 | 95 | 95 | 32.8 | 74.4 | 79.4 | 42 | -32.6 | 2011 | 2023 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 172.5 | 221.7 | 110.8 | 796 | 200 | 140 | 176.3 | 88.1 | 12 | -22.7 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 54.3 | 117.2 | 109.7 | 83 | 108 | 45.8 | 93.5 | 87.4 | 5 | -22.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 359.3 | 530.3 | 109.1 | 147 | 478 | 333.2 | 503.2 | 103.2 | 68 | -5.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.3 | 30.1
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 359.3 | 530.3 | 109.1 | 148 | 478 | 333.2 | 503.2 | 103.2 | 69 | -5.9 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 142.3 | 30.1
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.4 | 213.3 | 105.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 47.2 | 109.5 | 103 | 48 | 108 | 38.7 | 85.9 | 80.7 | 1 | -22.3 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 77.2 | 134.7 | 101.1 | 215 | 131 | 55.2 | 98.1 | 72.9 | 43 | -28.2 | 2011 | 2027 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.1 | 28.1 | 100.5 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 110.9 | 200.9 | 100.4 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -5.4 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 110.2 | 200.6 | 100.3 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -5.5 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20723 | CAMD JCT 115 | 20734 | WATRE 115 | 1 | 20723-20734-1 | 131 | 131 | 54.9 | 125.4 | 98.5 | 23 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.1 | 294.3 | 98.1 | 1848 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.9 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 514.7 | 822.7 | 97.9 | 126 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.5 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 91.4 | 10.8
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 94 | 115.8 | 97.5 | 991 | 119 | 72.3 | 93 | 77.8 | 192 | -19.7 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.3 | 315.2 | 97 | 1058 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 375.6 | 96.3 | 998 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 80.4 | 91.9 | 95.7 | 672 | 96 | 69 | 80.4 | 83.8 | 350 | -11.9 | 2014 | 2020 | 6 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 22.7 | 23.6
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 258 | 447.3 | 95.4 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -6.9 | 2014 | 2018 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI3GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1703.1 | 1853.1 | 94.8 | 8128 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 0.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 252.5 | 14.5
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.5 | 432.8 | 94.5 | 1233 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.7 | 2014 | 2017 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 439.7 | 752.5 | 94.5 | 54 | 796.7 | 435 | 745 | 93.5 | 87 | -1 | 2014 | 2015 | 1 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 82.5 | 10.4
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 35.4 | 139.4 | 93.2 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.4 | 100.7 | 93 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.8 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.2 | 10.3
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.4 | 100.7 | 93 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.8 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.2 | 10.3
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 135 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 81.4 | 153.2 | 92.8 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 1.8 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 429.2 | 779 | 92.7 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.4 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 86.3 | 10.2
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.2 | 187 | 92.5 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.9 | 92.3 | 205 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.8 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 326.4 | 426.8 | 91.4 | 1420 | 478 | 306.7 | 403.9 | 85.7 | 343 | -5.7 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 553 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 118.6 | 155.4 | 91.3 | 688 | 179 | 111.9 | 147.1 | 85.1 | 344 | -6.2 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 497.9 | 828.8 | 91.3 | 50 | 889 | 486.6 | 810.2 | 89 | 44 | -2.3 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 73.7 | 9.7
MAR3GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 398.5 | 663.5 | 91.1 | 48 | 717 | 386.2 | 643 | 88 | 44 | -3.1 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 78.8 | 11.9
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 333.7 | 438 | 90.9 | 232 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.7 | 6.3
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20524 | JACKSONV 230 | 20528 | RHEMS 230 | 1 | 20524-20528-1 | 478 | 478 | 232.6 | 419.2 | 90.7 | 86 | 478 | 208.3 | 390.9 | 83.8 | 43 | -6.9 | 2016 | 2020 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342 | 380.9 | 90.6 | 2205 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -0.2 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 13.4 | 11.7
CLIFGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 80.1 | 100.3 | 90.3 | 298 | 111 | 79.4 | 79.4 | 71.5 | 130 | -18.8 | 2017 | 2028 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 56.7 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 2 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CDCKGM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 70.7 | 120.8 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -42.3 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.5 | 98.2 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | - | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 99.6 | 92.2 | 124 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2016 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.7 | 91.3 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 964.4 | 90.4 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 961.1 | 90.1 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 89.1 | 152.2 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -39.6 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 37 | 63.1
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 491.2 | 102.8 | 260 | 478 | - | 464 | 97.1 | 232 | -5.7 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 110.8 | 23.2
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 92.6 | 96.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -12 | 2013 | 2020 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 22.9 | 23.9
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1793.2 | 94.2 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 0.6 | 2015 | 2014 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 252.1 | 13.3
BUC5GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 92.9 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.7 | 92.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 986.1 | 92.4 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 351.5 | 90.1 | 455 | 390 | - | 345.2 | 88.5 | 455 | -1.6 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 80.4 | 112.9 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -32.5 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 36.6 | 51.3 | #N/A | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 96.4 | 100.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -12.1 | 2011 | 2018 | 7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 22.9 | 23.8 | 91.9 | #N/A | 92.6
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28 | 100 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.1 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.8 | 95.2 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.3 | #N/A
STUDYL | BADX | - | - | - | - | - | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20725-20731-1 | 108 | 108 | - | 102.2 | 94.6 | 42 | 108 | - | 69.1 | 64 | 42 | -30.6 | 2014 | 2034 | 20 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 148.2 | 99.6 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.2 | 92.9 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.7 | 88.3
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 987.5 | 92.6 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.4 | 989.7
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 983.5 | 92.2 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 961.1 | 986.1
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.6 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.7 | 90.4 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.2 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.8 | 90.2 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportDuke_CPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 656.1 | 1643.8 | 200 | 5704 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 2.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.4 | 379.1 | 161.3 | 506 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.3 | 226.4 | 151 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 112.5 | 226.4 | 151 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 62.3 | 90.4 | 144.3 | 668 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -31 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 62.3 | 90.4 | 144.3 | 712 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -31 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 48.1 | 163.6 | 136.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | 0.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 87 | 132.6 | 123.8 | 274 | 108 | 74.6 | 118.5 | 110.8 | 49 | -13 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 125.7 | 246.7 | 119.7 | 172 | 201 | 126 | 247.2 | 120 | 172 | 0.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.6 | 122.5 | 114.6 | 147 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 56.4 | 100.6 | 106.8 | 89 | 95 | 43.5 | 86.2 | 91.6 | 5 | -15.2 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 95.7 | 213.8 | 105.2 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20039 | SUT 3 F 230 | 20554 | 9THORG T 230 | 1 | 20039-20554-1 | 590 | 590 | 225.3 | 612.1 | 104.6 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 342.3 | 498.8 | 102.2 | 68 | 478 | 333.2 | 503.2 | 103.2 | 68 | 1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 110.8 | 23.2
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 342.3 | 498.8 | 102.2 | 69 | 478 | 333.2 | 503.2 | 103.2 | 69 | 1 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 110.8 | 23.2
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 154.8 | 202.8 | 101.4 | 280 | 200 | 140 | 176.3 | 88.1 | 12 | -13.3 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 211.3 | 301.4 | 100.5 | 1850 | 300 | 213.3 | 306.1 | 102 | 1886 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 74.1 | 131 | 98.3 | 166 | 131 | 55.2 | 98.1 | 72.9 | 43 | -25.4 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48 | 103.7 | 97 | 43 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.6 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.1 | 315.1 | 97 | 377 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107 | 193.7 | 96.9 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.9 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.3 | 193.5 | 96.8 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 506.9 | 810.3 | 96.5 | 121 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.1 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 79 | 9.4
OCO1GM | 24 | 20022 | BRUN 1 N | 20621 | BARNRD W | 5 | 20552 | E WILM 230 | 20554 | 9THORG T 230 | 1 | 20552-20554-1 | 590 | 590 | 173.1 | 560.9 | 95.9 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 45.5 | 88.7 | 94.6 | 46 | 95 | 32.8 | 74.4 | 79.4 | 42 | -15.2 | 2014 | 2023 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 57 | 101.9 | 94.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.3 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.4 | 11.4
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 57 | 101.9 | 94.1 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -0.3 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.4 | 11.4
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 77.2 | 155.1 | 93.9 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | 0.7 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 29.9 | 139.4 | 93.1 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | 0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 70.7 | 187.7 | 92.6 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 0.3 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.3 | 92.1 | 130 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | OAKBOR100CAP | 5635 | OAKBRCAP | 635 | OAKBORO | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.1 | 358.7 | 92 | 523 | 390 | 344.5 | 364.5 | 93.5 | 554 | 1.5 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 422.7 | 767.2 | 91.3 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 74.5 | 8.8
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 316.7 | 419 | 91.1 | 806 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.3 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.4 | 438.8 | 90.9 | 207 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.2 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.5 | 6.3
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 243.5 | 424.1 | 90.7 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2.2 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964 | 964 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ROCKGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 55.9 | 165.2 | 90.3 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 40.9 | 96.1 | 90.2 | 25 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1620.3 | 1772.5 | 90 | 7512 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 5.1 | 2017 | 2014 | -3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 171.9 | 9.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 58.5 | 100.1 | 172 | 58.5 | - | 45.9 | 78.5 | 48 | -21.6 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 176 | 40 | - | 36.7 | 91.8 | 176 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.3 | 90.9 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 78.8 | 134.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -22 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 26.7 | 45.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 475.7 | 99.5 | 248 | 478 | - | 464 | 97.1 | 232 | -2.4 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 95.3 | 19.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978 | 91.7 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 973.7 | 91.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1727.9 | 90.7 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 4.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 186.8 | 9.8
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 86.5 | 90.1 | 455 | 96 | - | 81.1 | 84.5 | 455 | -5.6 | 2017 | 2020 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 16.8 | 17.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600 MW Import from CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600 MW Import from CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600 MW Import from CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 70.2 | 98.6 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -18.2 | 2012 | 2023 | 11 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 26.4 | 37 | 90.4 | 58.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.7 | 94.5 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.3 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 140.8 | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 90.3 | 94 | 21 | 96 | - | 84.8 | 88.3 | 21 | -5.7 | 2015 | 2018 | 3 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 16.8 | 17.4 | #N/A | #N/A | 86.5
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.4 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.3 | 87.8
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 978.9 | 91.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 978
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.7 | 91.7 | 42 | 40 | - | 36.7 | 91.8 | 42 | 0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 975.6 | 91.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964 | #N/A | 973.7
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.5 | 90.1 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.3 | #N/A | #N/A
Populate Summary Worksheet

## Roxboro_600ImportDuke_CPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 10 | Not in original screening
[25 empty] | 21 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 1057.9 | 1884.8 | 229.3 | 5969 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -26.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.5 | 379.2 | 161.4 | 509 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | -26.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 64 | 93 | 148.3 | 668 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -35 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 64 | 93 | 148.3 | 712 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -35 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 49.9 | 168.1 | 140.3 | 129 | 119 | 48.4 | 164.1 | 136.8 | 129 | -3.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 88.1 | 133.7 | 124.9 | 300 | 108 | 74.6 | 118.5 | 110.8 | 49 | -14.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 127.7 | 248 | 122.1 | 301 | 201 | 126 | 247.2 | 120 | 172 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 66.7 | 123.2 | 115.3 | 149 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 57.5 | 101.8 | 108.1 | 92 | 95 | 43.5 | 86.2 | 91.6 | 5 | -16.5 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 97.6 | 218.4 | 107.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | -2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 346.4 | 506 | 103.7 | 95 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118 | 24.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 346.4 | 506 | 103.7 | 96 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 118 | 24.7
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 156 | 205.4 | 102.7 | 279 | 200 | 140 | 176.3 | 88.1 | 12 | -14.6 | 2011 | 2018 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20052 | CAPE F F 115 | 20882 | CF1&2DUM13.0 | 1 | 20052-20882-1 | 28 | 28 | 28.2 | 28.2 | 100.9 | 130 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 75.6 | 133.7 | 99.3 | 212 | 131 | 55.2 | 98.1 | 72.9 | 43 | -26.4 | 2012 | 2027 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.1 | 295.1 | 98.4 | 1732 | 300 | 213.3 | 306.1 | 102 | 1886 | 3.6 | 2012 | 2011 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 48.1 | 104.4 | 97.7 | 51 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.3 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 95.9 | 116.9 | 97.5 | 1199 | 119 | 72.3 | 93 | 77.8 | 192 | -19.7 | 2013 | 2024 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 300.8 | 314.8 | 96.9 | 492 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 507.3 | 810.8 | 96.5 | 122 | 840 | 501.2 | 801.2 | 95.4 | 82 | -1.1 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 79.5 | 9.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.3 | 192.5 | 96.3 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -1.3 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 105.6 | 192.3 | 96.2 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.4 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 46.7 | 89.9 | 95.9 | 50 | 95 | 32.8 | 74.4 | 79.4 | 42 | -16.5 | 2014 | 2023 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 72.5 | 192.2 | 95 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | -2.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 363 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20001 | BLEWETT 115 | 20004 | TIL 1-4H 115 | 1 | 20001-20004-1 | 118 | 118 | 80.2 | 116.3 | 94.5 | 414 | 118 | 60 | 95 | 77.4 | 81 | -17.1 | 2014 | 2024 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.9 | 101.6 | 93.8 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 12.1 | 11.1
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 33.4 | 139.4 | 93.3 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 79.3 | 153.6 | 93.1 | 130 | 170 | 76.2 | 156 | 94.6 | 172 | 1.5 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 173 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.1 | 322.9 | 92.3 | 173 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 247.8 | 434.6 | 92.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 343.3 | 359.6 | 92.2 | 560 | 390 | 344.5 | 364.5 | 93.5 | 554 | 1.3 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 318.5 | 422.2 | 92 | 1073 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.2 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.3 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 423 | 767.8 | 91.4 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -1.1 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 75.1 | 8.9
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1639 | 1783.1 | 91 | 7906 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | 4.1 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 182.5 | 10.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 40.9 | 96.8 | 90.9 | 28 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.2 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.1 | 438.4 | 90.8 | 206 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.1 | 6.2
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.3 | 964.3 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 57.3 | 165.2 | 90.4 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 2 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1041.6 | 126.7 | 176 | 822 | - | 646.7 | 78.7 | 176 | -48 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60.2 | 102.9 | 176 | 58.5 | - | 45.9 | 78.5 | 48 | -24.4 | 2011 | 2024 | 13 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 27.6 | 98.4 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141 | 94 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.2 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86 | 90.5 | 176 | 95 | - | 86.3 | 90.8 | 176 | 0.3 | 2017 | 2016 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 2 | Not in original screening
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 80.4 | 137.5 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -24.9 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 28.3 | 48.4
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1089.9 | 132.6 | 910 | 822 | - | 667.9 | 81.3 | 910 | -51.3 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 480.1 | 100.4 | 248 | 478 | - | 464 | 97.1 | 232 | -3.3 | 2011 | 2013 | 2 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 99.7 | 20.8
BEL1GM | BEL2 | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.3 | 910 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.5 | 92.1 | 910 | 95 | - | 87.7 | 92.3 | 910 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981 | 91.9 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1748 | 91.8 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | 3 | 2016 | 2014 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 206.9 | 10.9
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 977.5 | 91.6 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 87.2 | 90.8 | 455 | 96 | - | 81.1 | 84.5 | 455 | -6.3 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 17.5 | 18.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - Roxboro_600Import_CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Roxboro_600Import_CPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Roxboro_600Import_CPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Roxboro_600Import_CPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Roxboro_600Import_CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 1067.3 | 129.8 | 42 | 822 | - | 662.5 | 80.6 | 42 | -49.2 | 2011 | 2022 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 71.9 | 100.9 | 42 | 71.2 | - | 57.3 | 80.4 | 42 | -20.5 | 2011 | 2023 | 12 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | - | 43.8 | 61.6 | 28.1 | 39.3 | 93 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20052 | CAPE F F | 20882 | CF1&2DUM | 1 | 20052-20882-1 | 28 | 28 | - | 28.1 | 100.2 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 28.2 | #N/A | #N/A
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 91 | 94.8 | 21 | 96 | - | 84.8 | 88.3 | 21 | -6.5 | 2014 | 2018 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 17.5 | 18.2 | #N/A | #N/A | 87.2
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.9 | 94.6 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.5 | 92.1 | 42 | 95 | - | 87.7 | 92.3 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86 | 87.5
BUC5GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 91.9 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 979.4 | 91.8 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 981
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 976 | 91.5 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.3 | #N/A | 977.5
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 315.5 | 90.1 | 21 | 350 | - | 315.8 | 90.2 | 21 | 0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 5 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 5 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BUC5GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 662.7 | 1677 | 204 | 5213 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.2 | 378.7 | 161.2 | 474 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.1 | 159.3 | 133.2 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.3 | 239.7 | 118.2 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 71.1 | 114.9 | 107.6 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 331.2 | 504.8 | 103.7 | 62 | 478 | 333.2 | 503.2 | 103.2 | 68 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.8 | 24.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 331.2 | 504.8 | 103.7 | 63 | 478 | 333.2 | 503.2 | 103.2 | 69 | -0.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 116.8 | 24.7
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 212.8 | 310.7 | 103.6 | 1846 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.2 | 210.1 | 103.6 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.5 | 110.5 | 103.5 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 1.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1112.7 | 1393.7 | 100.7 | 9015 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -5.8 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 525.2 | 839.3 | 99.9 | 118 | 840 | 501.2 | 801.2 | 95.4 | 82 | -4.5 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 108 | 12.8
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 40.7 | 58.3 | 98.9 | 52 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 14.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 40.7 | 58.3 | 98.9 | 65 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 14.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1712.6 | 1896.2 | 97.2 | 7863 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -2.1 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 295.6 | 16.9
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58.8 | 105 | 96.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.1 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 15.5 | 14.2
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58.8 | 105 | 96.9 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -3.1 | 2013 | 2015 | 2 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 15.5 | 14.2
OXFDGM | CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 304.5 | 314.9 | 96.9 | 596 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 448 | 767.1 | 96.3 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -2.8 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 97.1 | 12.2
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.8 | 375.5 | 96.3 | 835 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 73 | 157 | 95.6 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 68 | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83.6 | 105.6 | 95.1 | 433 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.6 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 438 | 794.7 | 94.6 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -4.3 | 2014 | 2017 | 3 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 102 | 12.1
TURNGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 104.4 | 189.1 | 94.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 0.4 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.7 | 188.9 | 94.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.3 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.9 | 139.4 | 93.7 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 408.2 | 679.4 | 93.3 | 82 | 717 | 386.2 | 643 | 88 | 44 | -5.3 | 2015 | 2018 | 3 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 94.7 | 14.1
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323.1 | 92.3 | 216 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.2 | 387.8 | 92.2 | 2170 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.8 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.3 | 13.3
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 319.4 | 421.7 | 91.9 | 1252 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 337.1 | 442.4 | 91.6 | 296 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.9 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 31.1 | 7
THTCGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 153.8 | 91.5 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 153.7 | 91.5 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DRBNGM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 108 | 182.6 | 91.3 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -5.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 107.7 | 182.3 | 91.2 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -5.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 239.7 | 425.9 | 91.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -2.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.9 | 183.7 | 90.9 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 51 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 278.9 | 412.7 | 90.7 | 45 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 1.4 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -8.1 | -0.7
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 432.7 | 760.2 | 90.5 | 44 | 840 | 420.2 | 738.3 | 87.9 | 44 | -2.6 | 2017 | 2018 | 1 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 96.2 | 11.4
BUZDGM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 1 | 164-190-1 | 108.2 | 108.2 | 44 | 93.9 | 90.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.2 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.2 | 14.2
CLI5GM | SINGLE 836 | 20800 | ASHEVIL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100 | 190 | PISGAH 100 | 2 | 164-190-2 | 108.2 | 108.2 | 44 | 93.9 | 90.1 | 130 | 108.2 | 44.1 | 92.6 | 88.9 | 130 | -1.2 | 2017 | 2017 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 44.7 | 87.7 | 75.9 | 6.2 | 14.2
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.8 | 94.5 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 961.6 | 90.1 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.6 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60 | 102.6 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 10 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 7.9 | 13.5
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 462.6 | 96.8 | 232 | 478 | - | 464 | 97.1 | 232 | 0.3 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 82.2 | 17.2
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1830.3 | 96.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -1.3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 289.2 | 15.2
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.6 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 983.5 | 92.2 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 980.3 | 91.9 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_AEP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_AEP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88 | 92.6 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 87.9
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 984.4 | 92.3 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 961.6 | 983.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 981.2 | 92 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.7 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 980.3
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323.1 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_VP
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
DAN3GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 657.6 | 1668.7 | 203 | 5294 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.3 | 378.8 | 161.2 | 487 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 44.7 | 158.4 | 132.4 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 4.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 122.8 | 238.7 | 117.7 | 129 | 201 | 126 | 247.2 | 120 | 172 | 2.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 70.9 | 114.6 | 107.3 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 3.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 210.8 | 309.5 | 103.2 | 1728 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 92.7 | 209.1 | 103.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 2.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 64.2 | 109.9 | 102.9 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 329.9 | 501.3 | 102.8 | 61 | 478 | 333.2 | 503.2 | 103.2 | 68 | 0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.3 | 23.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 329.9 | 501.3 | 102.8 | 62 | 478 | 333.2 | 503.2 | 103.2 | 69 | 0.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 113.3 | 23.8
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 40.9 | 58.6 | 99.3 | 49 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 14 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 40.9 | 58.6 | 99.3 | 65 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 14 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 515.9 | 824.6 | 98.2 | 86 | 840 | 501.2 | 801.2 | 95.4 | 82 | -2.8 | 2012 | 2014 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 93.3 | 11.1
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1081 | 1361.6 | 98.1 | 8912 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -3.2 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 302.9 | 314.8 | 96.9 | 552 | 325 | 301.2 | 314.8 | 96.9 | 423 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1692.7 | 1872.3 | 95.7 | 7938 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -0.6 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 271.7 | 15.4
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 58 | 103.5 | 95.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.8 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 14 | 12.9
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 58 | 103.5 | 95.6 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -1.8 | 2014 | 2015 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 14 | 12.9
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 83 | 105.6 | 95.2 | 370 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 345.5 | 370.3 | 94.9 | 710 | 390 | 344.5 | 364.5 | 93.5 | 554 | -1.4 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 71.8 | 155.4 | 94.5 | 129 | 170 | 76.2 | 156 | 94.6 | 172 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 438 | 750.2 | 94.2 | 87 | 796.7 | 435 | 745 | 93.5 | 87 | -0.7 | 2015 | 2015 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 80.2 | 10.1
TUXDGM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 103.7 | 187.9 | 94 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | 1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RDHSGM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 103.1 | 187.7 | 93.9 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | 0.9 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.7 | 139.4 | 93.6 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.4 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 430.3 | 780.8 | 93 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -2.7 | 2015 | 2017 | 2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 88.1 | 10.5
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 322.9 | 92.3 | 212 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 281.9 | 417.1 | 91.7 | 46 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.4 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.7 | 0.3
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.6 | 384.7 | 91.4 | 2153 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 17.2 | 12.5
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 336.1 | 441.1 | 91.3 | 273 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.6 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 29.8 | 6.7
BEL1GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 399.7 | 665.3 | 91.2 | 49 | 717 | 386.2 | 643 | 88 | 44 | -3.2 | 2016 | 2018 | 2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 80.6 | 12
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 317.2 | 417.9 | 90.9 | 1190 | 478 | 315.6 | 414.1 | 89.8 | 696 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 51.9 | 165.3 | 90.7 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.4 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 107.2 | 181.1 | 90.6 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -4.9 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 107 | 181 | 90.5 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -4.9 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 67.5 | 182.7 | 90.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 2.5 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.6 | 94.4 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.4 | 91 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.5 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 60.2 | 102.9 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 9.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 8.1 | 13.8
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 460.8 | 96.4 | 232 | 478 | - | 464 | 97.1 | 232 | 0.7 | 2013 | 2013 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 80.4 | 16.8
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1810 | 95 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -0.2 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 268.9 | 14.1
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.8 | 92.5 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 981.9 | 92 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 978.6 | 91.7 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_VP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_VP\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_VP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_VP | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_VP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.5 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 141.6 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.9 | 92.5 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.4 | 87.8
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 982.5 | 92.1 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960.2 | 981.9
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.8 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 979.2 | 91.8 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | 978.6
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 322.9 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_SCEG
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 13 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 22 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
MCG2GM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 671.3 | 1685.3 | 205 | 5445 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.7 | 379.4 | 161.5 | 513 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.1 | 159.7 | 133.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.6 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.6 | 130 | 121.7 | 58 | 108 | 74.6 | 118.5 | 110.8 | 49 | -10.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 51.4 | 74.7 | 119.5 | 347 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -6.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 51.4 | 74.7 | 119.5 | 390 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -6.2 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.6 | 240.2 | 118.6 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 71.3 | 123.6 | 115.8 | 135 | 108 | 64.2 | 112.4 | 105.1 | 51 | -10.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 339.4 | 514.3 | 105.7 | 85 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.3 | 26.7
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 339.4 | 514.3 | 105.7 | 86 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.5 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 126.3 | 26.7
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 51 | 98.3 | 104.6 | 43 | 95 | 43.5 | 86.2 | 91.6 | 5 | -13 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.4 | 210.6 | 103.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.8 | 310.1 | 103.4 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1106.4 | 1385.8 | 100.5 | 9054 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -5.6 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 52.8 | 104.9 | 98.3 | 44 | 108 | 45.8 | 93.5 | 87.4 | 5 | -10.9 | 2012 | 2018 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1728.3 | 1909.8 | 98.1 | 7734 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -3 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 309.2 | 17.8
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 454.2 | 777.5 | 97.6 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -4.1 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 107.5 | 13.5
TUXDGM | SINGLE 54 | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.2 | 315.8 | 97.2 | 1290 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.3 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.2 | 194.2 | 97.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.1 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106.5 | 194 | 97 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.2 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 21 | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346.2 | 375.6 | 96.3 | 1071 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.1 | 157.8 | 96.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 504.2 | 805.9 | 95.9 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.5 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 74.6 | 8.8
RDHSGM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84.2 | 105.6 | 95.2 | 799 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.1 | 428.3 | 93.8 | 1357 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 23.7 | 139.4 | 93.7 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 247.3 | 435.5 | 93.6 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.1 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.6 | 101.1 | 93.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.5 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.6 | 10.6
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.6 | 101.1 | 93.3 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.5 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.6 | 10.6
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 345.6 | 391 | 93 | 2162 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.6 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 23.5 | 14.1
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 131 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 40.3 | 86.4 | 92.5 | 52 | 95 | 32.8 | 74.4 | 79.4 | 42 | -13.1 | 2015 | 2023 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | BUSHRIVERB | 242 | BUSH RIV | 2610 | BUSH R 1 | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 77.5 | 88.6 | 92.3 | 505 | 96 | 69 | 80.4 | 83.8 | 350 | -8.5 | 2016 | 2020 | 4 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 19.4 | 20.2
TUXDGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.3 | 323 | 92.3 | 308 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 108.9 | 184.1 | 92.1 | 75 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.5 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 109 | 184.2 | 92.1 | 79 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.4 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 153.7 | 183.9 | 92 | 111 | 200 | 140 | 176.3 | 88.1 | 12 | -3.9 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 438.7 | 770.8 | 91.8 | 47 | 840 | 420.2 | 738.3 | 87.9 | 44 | -3.9 | 2016 | 2018 | 2 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 106.8 | 12.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 45.8 | 97.3 | 91.6 | 37 | 108 | 38.7 | 85.9 | 80.7 | 1 | -10.9 | 2016 | 2022 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68.1 | 184.1 | 91.2 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.7 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420.5 | 763.1 | 90.8 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.5 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 70.4 | 8.3
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 50.4 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334 | 438.2 | 90.8 | 263 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 26.9 | 6.2
ALL5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 320 | 419.9 | 90.1 | 614 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.4 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.3 | 94.9 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.7 | 91.3 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 965.2 | 90.5 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 962.1 | 90.2 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 68.6 | 117.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -4.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 16.5 | 28.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 470.9 | 98.5 | 232 | 478 | - | 464 | 97.1 | 232 | -1.4 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 90.5 | 18.9
BEL1GM | BEL2 | - | - | - | - | - | 431 | ENGR6TAP | 576 | CONLY TB | 1 | 431-576-1 | 126.4 | 126.4 | - | 124 | 98.1 | 455 | 126.4 | - | 122.5 | 96.9 | 455 | -1.2 | 2012 | 2013 | 1 |  | 126.4 | 139.4 | 126.4 | HOPEWELL B | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 103.4 | 81.8 | 20.6 | 16.3
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1848.7 | 97.1 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -2.3 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 307.6 | 16.2
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 89.7 | 93.5 | 455 | 96 | - | 81.1 | 84.5 | 455 | -9 | 2015 | 2020 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 20 | 20.9
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 92.9 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 988.3 | 92.6 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.2 | 92.3 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCEG | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCEG\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCEG Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCEG | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_SCEG
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 93.5 | 97.4 | 21 | 96 | - | 84.8 | 88.3 | 21 | -9.1 | 2013 | 2018 | 5 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 20 | 20.8 | 88.6 | #N/A | 89.7
ALL4GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.8 | 95.2 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.3 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.2 | 92.9 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.7 | 88.3
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 987.7 | 92.6 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 965.2 | 988.3
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 984.6 | 92.3 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 962.1 | 985.2
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.2 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.2 | 90.2 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.8 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_SCPSA
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 11 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 9 | Not in original screening
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 676.9 | 1684.7 | 205 | 5404 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -2.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.8 | 379.5 | 161.5 | 515 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45 | 159.6 | 133.6 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 3.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.6 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 52.1 | 75.6 | 121.1 | 398 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | -7.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 52.1 | 75.6 | 121.1 | 441 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | -7.8 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 81.2 | 128.8 | 120.6 | 55 | 108 | 74.6 | 118.5 | 110.8 | 49 | -9.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.6 | 240.2 | 118.6 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | MONROEWH | 380 | LANCASTR | 654 | ROUGHEDG | &1 | 10392 | RED R BL 100 | 10381 | LAN R BL 100 | 1 | 10381-10392-1 | 70.8 | 70.8 | 40.6 | 82.4 | 117.4 | 84 | 70.8 | 38.8 | 80.9 | 114.9 | 71 | -2.5 | 2011 | 2011 | 0 |  | 58.2 | 70.8 | 58.2 | MONROE BL | 100 kV Line | 71.1852 | 78.1132 | 71.1852 | 70.8 | 22.6 | 61.9 | 87.3 | 20.5 | 30.1
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 70.1 | 122.1 | 114.5 | 124 | 108 | 64.2 | 112.4 | 105.1 | 51 | -9.4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 339.1 | 513.8 | 105.6 | 86 | 478 | 333.2 | 503.2 | 103.2 | 68 | -2.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 125.8 | 26.6
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 339.1 | 513.8 | 105.6 | 87 | 478 | 333.2 | 503.2 | 103.2 | 69 | -2.4 | 2011 | 2011 | 0 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 125.8 | 26.6
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.3 | 210.5 | 103.9 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 50.6 | 97.1 | 103.4 | 45 | 95 | 43.5 | 86.2 | 91.6 | 5 | -11.8 | 2011 | 2016 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 213.9 | 309.9 | 103.3 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1090.4 | 1370 | 99.3 | 8826 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -4.4 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1725 | 1904.2 | 97.7 | 7758 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -2.6 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 303.6 | 17.4
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 107.8 | 195.2 | 97.6 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -2.6 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 107 | 194.9 | 97.5 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -2.7 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 452.4 | 774.6 | 97.2 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -3.7 | 2013 | 2015 | 2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 104.6 | 13.1
THALGM | SINGLE 54 | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.4 | 315.4 | 97.1 | 1402 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.2 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 51.7 | 103.4 | 96.9 | 44 | 108 | 45.8 | 93.5 | 87.4 | 5 | -9.5 | 2013 | 2018 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 346 | 375.6 | 96.3 | 996 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75.2 | 157.8 | 96.1 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.5 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 503.6 | 805 | 95.8 | 83 | 840 | 501.2 | 801.2 | 95.4 | 82 | -0.4 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 73.7 | 8.7
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84.4 | 105.6 | 95.2 | 868 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.7 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 323.9 | 429.8 | 94.2 | 1365 | 478 | 315.6 | 414.1 | 89.8 | 696 | -4.4 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 249 | 437.6 | 94.1 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -5.6 | 2015 | 2018 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 23.9 | 139.4 | 93.8 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56.5 | 100.9 | 93.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.6 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 11.4 | 10.5
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56.5 | 100.9 | 93.2 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 0.6 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 11.4 | 10.5
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 343.5 | 388.2 | 92.3 | 2180 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -1.9 | 2016 | 2017 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 20.7 | 13.4
WYLIGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.3 | 323 | 92.3 | 270 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 152.1 | 184.2 | 92.1 | 100 | 200 | 140 | 176.3 | 88.1 | 12 | -4 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 108.9 | 183.9 | 92 | 80 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
DAN3GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 108.6 | 183.7 | 91.9 | 79 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.3 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 437 | 767.7 | 91.4 | 47 | 840 | 420.2 | 738.3 | 87.9 | 44 | -3.5 | 2016 | 2018 | 2 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 103.7 | 12.3
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 39.9 | 85.3 | 91.2 | 48 | 95 | 32.8 | 74.4 | 79.4 | 42 | -11.8 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68 | 184 | 91.2 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.7 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 50.6 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 334.2 | 438.5 | 90.8 | 264 | 478 | 334.2 | 438.6 | 90.7 | 252 | -0.1 | 2016 | 2016 | 0 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 27.2 | 6.2
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 420 | 762.2 | 90.7 | 44 | 840 | 418 | 758.7 | 90.3 | 44 | -0.4 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 69.5 | 8.2
BEL1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 321.3 | 421.5 | 90.5 | 791 | 478 | 306.7 | 403.9 | 85.7 | 343 | -4.8 | 2017 | 2019 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 44.6 | 95.9 | 90.2 | 13 | 108 | 38.7 | 85.9 | 80.7 | 1 | -9.5 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
99ISGM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.5 | 95 | 88 | 150 | - | 140.7 | 93.8 | 88 | -1.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.8 | 91.4 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.6 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 966.4 | 90.6 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -1.1 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 963.3 | 90.3 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 69.2 | 118.3 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | -5.7 | 2011 | 2011 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 17.1 | 29.2
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 470.3 | 98.4 | 232 | 478 | - | 464 | 97.1 | 232 | -1.3 | 2012 | 2013 | 1 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 89.9 | 18.8
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1844.8 | 96.9 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -2.1 | 2013 | 2014 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 303.7 | 16
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.4 | 93.1 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.8 | 92.8 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 986.6 | 92.5 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_SCPSA | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_SCPSA\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_SCPSA Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_SCPSA | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_SCPSA
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 143.1 | 95.4 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1.2 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | 142.5 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.3 | 93 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.8 | 88.4
ALL4GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 989.1 | 92.7 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 966.4 | 989.8
ALL4GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 985.8 | 92.4 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -1.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 963.3 | 986.6
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 88.5 | 92.2 | 21 | 96 | - | 84.8 | 88.3 | 21 | -3.9 | 2016 | 2018 | 2 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 15 | 15.6 | #N/A | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293.4 | 90.3 | 42 | 325 | - | 290.2 | 89.3 | 42 | -1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.4 | #N/A | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.2 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
Populate Summary Worksheet

## 600ImportCPLE_Duke
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 12 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 3 | Not in original screening
[25 empty] | 15 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
TUXDGM | SINGLE 38 | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 665.7 | 1679.8 | 204.4 | 5364 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | -1.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | SINGLE 843 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.6 | 379.2 | 161.4 | 548 | 235 | 185.6 | 379.1 | 161.3 | 542 | -0.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 45.4 | 160.1 | 133.9 | 43 | 119 | 48.4 | 164.1 | 136.8 | 129 | 2.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.7 | 186.7 | 124.5 | 43 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 400 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93.1 | 186.7 | 124.5 | 43 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 123.7 | 240.5 | 118.7 | 129 | 201 | 126 | 247.2 | 120 | 172 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -10.5 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 633 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 68.8 | 112 | 104.9 | 48 | 108 | 74.6 | 118.5 | 110.8 | 49 | 5.9 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 93.6 | 210.9 | 104.1 | 43 | 201 | 96 | 214.3 | 105.4 | 43 | 1.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 214.6 | 311.1 | 103.7 | 1807 | 300 | 213.3 | 306.1 | 102 | 1886 | -1.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -6.8 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 371 | 21.6
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 474 | 811.3 | 101.8 | 88 | 796.7 | 435 | 745 | 93.5 | 87 | -8.3 | 2011 | 2015 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 141.3 | 17.7
WATRGM | SINGLE 635 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 63.5 | 107.9 | 101.1 | 46 | 108 | 64.2 | 112.4 | 105.1 | 51 | 4 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 174 | 20122 | REGNCYPK | 20211 | APEX | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 307.8 | 315.2 | 97 | 679 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 75 | 158.4 | 96.5 | 172 | 170 | 76.2 | 156 | 94.6 | 172 | -1.9 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BRDGGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 344.9 | 375.5 | 96.3 | 873 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.8 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 457.8 | 804.1 | 95.7 | 80 | 840 | 420.2 | 738.3 | 87.9 | 44 | -7.8 | 2014 | 2018 | 4 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 140.1 | 16.6
CLI5GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 68 | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 84 | 105.6 | 95.1 | 707 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.6 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 105 | 190.2 | 95.1 | 43 | 200 | 104.9 | 189.9 | 95 | 43 | -0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 443 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 104.3 | 190 | 95 | 43 | 200 | 104.1 | 189.5 | 94.8 | 43 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 498.3 | 796.6 | 94.8 | 78 | 840 | 501.2 | 801.2 | 95.4 | 82 | 0.6 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 65.3 | 7.7
MCG2GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 22.1 | 139.4 | 93.8 | 43 | 158 | 27.5 | 139.4 | 93.2 | 43 | -0.6 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 287.6 | 425.5 | 93.6 | 52 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | -1.5 | 2015 | 2016 | 1 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | 4.7 | 2.2
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 38.5 | 55.1 | 93.6 | 42 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 19.7 | 2015 | 2011 | -4 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 684 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 38.5 | 55.1 | 93.6 | 48 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 19.7 | 2015 | 2011 | -4 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 375 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.6 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 22.6 | 14.1
OCO1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 841 | 6BOBWH B 230 | 1 | 714-841-1 | 478 | 478 | 359.8 | 449 | 92.9 | 376 | 478 | 328.3 | 416.2 | 85.7 | 126 | -7.2 | 2015 | 2019 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 64.1 | 14.5
OCO3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 842 | 6BOBWH W 230 | 2 | 714-842-2 | 478 | 478 | 360 | 449 | 92.9 | 419 | 478 | 328.3 | 416.2 | 85.7 | 162 | -7.2 | 2015 | 2019 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 64.1 | 14.5
BRDGGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 131 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 291.8 | 453 | 92.8 | 39 | 478 | 333.2 | 503.2 | 103.2 | 68 | 10.4 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 65 | 13.8
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 291.8 | 453 | 92.8 | 40 | 478 | 333.2 | 503.2 | 103.2 | 69 | 10.4 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 65 | 13.8
BEL1GM | SINGLE 472 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 321.1 | 424.7 | 92.7 | 1264 | 478 | 315.6 | 414.1 | 89.8 | 696 | -2.9 | 2015 | 2017 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1.4 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 10.6 | 9.7
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 1.4 | 2015 | 2015 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 10.6 | 9.7
BEL1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 109.3 | 184.6 | 92.3 | 43 | 200 | 101.4 | 171.3 | 85.7 | 43 | -6.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTKGM | SINGLE 43 | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 315.2 | 323 | 92.3 | 257 | 350 | 315.2 | 322.9 | 92.3 | 130 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 397 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 109.1 | 184.5 | 92.2 | 43 | 200 | 101.2 | 171.2 | 85.6 | 43 | -6.6 | 2016 | 2019 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 529 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 242.9 | 430 | 92.2 | 86 | 478 | 232.6 | 417.1 | 88.5 | 86 | -3.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.4 | 91.9 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 270.3 | 398.8 | 91.5 | 167 | 437 | 249.4 | 367.6 | 83.9 | 85 | -7.6 | 2016 | 2020 | 4 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 676 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 270.3 | 398.8 | 91.5 | 211 | 437 | 248.6 | 366.8 | 83.9 | 128 | -7.6 | 2016 | 2020 | 4 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 48.9 | 19.3
OCO3GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 68.3 | 184.5 | 91.4 | 43 | 201 | 71 | 188.2 | 92.9 | 43 | 1.5 | 2016 | 2015 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 1 | 7-106-1 | 478 | 478 | 193.9 | 448.6 | 91.3 | 5 | 478 | 187.8 | 430.9 | 87.6 | 2 | -3.7 | 2016 | 2018 | 2 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 2 | 7-106-2 | 478 | 478 | 193.9 | 448.6 | 91.3 | 5 | 478 | 187.8 | 430.9 | 87.6 | 2 | -3.7 | 2016 | 2018 | 2 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230 | 540 | 6MCGUIRE 230 | 1 | 537-540-1 | 318.6 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | 318.6 | 162.7 | 283.2 | 86.9 | 44 | -4.3 | 2016 | 2019 | 3 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 57.1 | 18.4
WYLIGM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 49.4 | 165.3 | 90.8 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -0.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 332.2 | 435.9 | 90.3 | 233 | 478 | 334.2 | 438.6 | 90.7 | 252 | 0.4 | 2017 | 2016 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 24.6 | 5.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142 | 94.7 | 88 | 150 | - | 140.7 | 93.8 | 88 | -0.9 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 176 | 40 | - | 36.7 | 91.8 | 176 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 86.5 | 91.1 | 176 | 95 | - | 86.3 | 90.8 | 176 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1726.3 | 90.7 | 176 | 1904.3 | - | 1623 | 85.2 | 176 | -5.5 | 2016 | 2020 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1369 | 71.9 | 357.3 | 18.8
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 963.2 | 90.3 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -0.8 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 960.2 | 90 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -0.7 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1909.2 | 100.3 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -5.5 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 368.1 | 19.4
CAT1GM | CAT2 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 58.1 | 99.4 | 910 | 58.5 | - | 65.9 | 112.6 | 910 | 13.2 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 52.1 | 89.1 | 6 | 10.3
BEL1GM | BEL2 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 910 | 95 | - | 87.7 | 92.3 | 910 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.6 | 92.4 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -0.9 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.5 | 92.1 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -0.9 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - 600ImportCPLE_Duke | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\600ImportCPLE_Duke\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening 600ImportCPLE_Duke Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - 600ImportCPLE_Duke
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.5 | 95 | 21 | 150 | - | 141.3 | 94.2 | 21 | -0.8 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | 142 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.7 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.4 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 86.5 | 88.1
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.7 | 92.4 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -0.8 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 963.2 | 985.6
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.6 | 92.1 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -0.8 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 960.2 | 982.5
ALL4GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 92.1 | 42 | 40 | - | 36.7 | 91.8 | 42 | -0.3 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 36.9 | #N/A
ALL4GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.1 | 90.3 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293 | 90.2 | 42 | 325 | - | 290.2 | 89.3 | 42 | -0.9 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.2 | #N/A | #N/A
Populate Summary Worksheet

## PEC TRM BR1 Down
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 15 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1357.9 | 1628.1 | 119.3 | 50 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -24.4 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 64.5 | 116.6 | 107.6 | 1 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -13.8 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 27.1 | 24.9
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 64.5 | 116.6 | 107.6 | 1 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -13.8 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 27.1 | 24.9
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 481.4 | 822.7 | 103.3 | 3 | 796.7 | 435 | 745 | 93.5 | 87 | -9.8 | 2011 | 2015 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 152.7 | 19.2
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1761.8 | 1980.3 | 102.4 | 73 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -7.3 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 379.7 | 22.1
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 465 | 815.3 | 97.1 | 2 | 840 | 420.2 | 738.3 | 87.9 | 44 | -9.2 | 2013 | 2018 | 5 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 151.3 | 18
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 1 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 309.7 | 455.8 | 94.6 | 12 | 437 | 248.6 | 366.8 | 83.9 | 128 | -10.7 | 2014 | 2025 | 11 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 105.9 | 22.4
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 223.1 | 378.1 | 93.7 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 491.4 | 787.4 | 93.7 | 2 | 840 | 501.2 | 801.2 | 95.4 | 82 | 1.7 | 2015 | 2014 | -1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 56.1 | 6.6
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 222.6 | 377.4 | 93.5 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500 | 850 | 8PL GRDN 500 | 1 | 849-850-1 | 1385.6 | 1385.6 | 946.4 | 1270 | 90.7 | 3 | 1385.6 | 837 | 1174.5 | 82.7 | 44 | -8 | 2016 | 2021 | 5 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 248.7 | 20
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 27 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 3 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
[12 empty] | -- | 129.9 | 129.9 | - | 133.4 | 102.7 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1874.1 | 98.4 | 42 | 1904.3 | - | 1804.3 | 94.8 | 910 | -3.6 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 333 | 17.5
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1313.4 | 97.3 | 42 | 1350 | - | 996.1 | 73.8 | 910 | -23.5 | 2013 | 2027 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.5 | 93.7 | 1 | 150 | - | 141.3 | 94.2 | 21 | 0.5 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.9 | 92.2 | 2 | 40 | - | 36.7 | 91.8 | 42 | -0.4 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Populate Summary Worksheet

## PEC TRM HR Down
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1336.9 | 1606.3 | 118.3 | 52 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -23.4 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 64.4 | 116.4 | 107.5 | 1 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -13.7 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 26.9 | 24.8
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 64.4 | 116.4 | 107.5 | 1 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | -13.7 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 26.9 | 24.8
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 493.4 | 843.2 | 105.8 | 3 | 796.7 | 435 | 745 | 93.5 | 87 | -12.3 | 2011 | 2015 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 173.2 | 21.7
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1785.6 | 1993.6 | 103.8 | 71 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -8.7 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 393 | 23.5
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 476.6 | 835.6 | 99.5 | 2 | 840 | 420.2 | 738.3 | 87.9 | 44 | -11.6 | 2012 | 2018 | 6 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 171.6 | 20.4
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.8 | 142.8 | 95.2 | 1 | 150 | 142.9 | 142.9 | 95.2 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 310.7 | 457.3 | 95 | 13 | 437 | 248.6 | 366.8 | 83.9 | 128 | -11.1 | 2014 | 2025 | 11 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 107.4 | 22.8
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 494.3 | 792.2 | 94.3 | 2 | 840 | 501.2 | 801.2 | 95.4 | 82 | 1.1 | 2014 | 2014 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 60.9 | 7.2
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 219.6 | 372.3 | 92.7 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500 | 850 | 8PL GRDN 500 | 1 | 849-850-1 | 1385.6 | 1385.6 | 970 | 1290.6 | 92.6 | 9 | 1385.6 | 837 | 1174.5 | 82.7 | 44 | -9.9 | 2015 | 2021 | 6 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 269.3 | 21.9
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 219.2 | 371.6 | 92.6 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230 | 540 | 6MCGUIRE 230 | 1 | 537-540-1 | 318.6 | 318.6 | 183.7 | 293.1 | 90.4 | 2 | 318.6 | 162.7 | 283.2 | 86.9 | 44 | -3.5 | 2017 | 2019 | 2 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 54.6 | 17.6
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 27 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 3 | Not in original screening
[25 empty] | 30 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1904.3 | 100 | 42 | 1904.3 | - | 1804.3 | 94.8 | 910 | -5.2 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 363.2 | 19.1
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1295.5 | 96 | 42 | 1350 | - | 996.1 | 73.8 | 910 | -22.2 | 2014 | 2027 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Harris Down
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
Populate Summary Worksheet

## PEC TRM BR1 Down 600ImCPLE_Duke
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 15 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 10 | Not in original screening
[25 empty] | 25 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1446.9 | 1694.5 | 126 | 50 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | -20.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 526.8 | 900.4 | 113 | 4 | 796.7 | 474 | 811.3 | 101.8 | 88 | -11.2 | 2011 | 2011 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 230.4 | 28.9
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 64.2 | 116 | 107.1 | 1 | 108.3 | 56 | 100.1 | 92.4 | 43 | -14.7 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 26.5 | 24.4
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 64.2 | 116 | 107.1 | 1 | 108.3 | 56 | 100.1 | 92.4 | 43 | -14.7 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 26.5 | 24.4
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 508.8 | 892.4 | 106.2 | 3 | 840 | 457.8 | 804.1 | 95.7 | 80 | -10.5 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 228.4 | 27.1
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 248.5 | 411.6 | 103.8 | 2 | 398 | 180.9 | 315.2 | 77.6 | 123 | -26.2 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 248 | 410.8 | 103.6 | 2 | 398 | 180.3 | 314.6 | 77.5 | 117 | -26.1 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1706.8 | 1931.6 | 101.1 | 69 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | 0.8 | 2011 | 2011 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 331 | 20.8
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 329.9 | 485.8 | 100.9 | 27 | 437 | 270.3 | 398.8 | 91.5 | 211 | -9.4 | 2011 | 2021 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 135.9 | 28.7
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 1 | 844-848-1 | 478 | 478 | 262.9 | 433.7 | 96 | 2 | 478 | 223.9 | 382.2 | 82 | 44 | -14 | 2014 | 2022 | 8 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 2 | 844-848-2 | 478 | 478 | 262.9 | 433.7 | 96 | 2 | 478 | 223.8 | 382.2 | 82 | 44 | -14 | 2014 | 2022 | 8 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 482 | 482 | 329.9 | 450.8 | 94.8 | 26 | 437 | 270.3 | 398.8 | 91.5 | 167 | -3.3 | 2014 | 2021 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 304.9 | 383.1 | 94.1 | 11 | 423 | 272.9 | 351.7 | 84.4 | 607 | -9.7 | 2015 | 2020 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500 | 850 | 8PL GRDN 500 | 1 | 849-850-1 | 1385.6 | 1385.6 | 1035.6 | 1293.7 | 93.1 | 40 | 1385.6 | 883 | 1244.2 | 88.8 | 174 | -4.3 | 2015 | 2017 | 2 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 272.4 | 22.4
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 841 | 6BOBWH B 230 | 1 | 714-841-1 | 478 | 478 | 347.7 | 446.1 | 92.8 | 16 | 478 | 359.8 | 449 | 92.9 | 376 | 0.1 | 2015 | 2015 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 61.2 | 14.4
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 842 | 6BOBWH W 230 | 2 | 714-842-2 | 478 | 478 | 347.7 | 446.1 | 92.8 | 17 | 478 | 360 | 449 | 92.9 | 419 | 0.1 | 2015 | 2015 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 61.2 | 14.4
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 100.6 | 100.6 | 90.6 | 2 | 111 | 84 | 105.6 | 95.1 | 707 | 4.5 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 293.3 | 293.3 | 90.2 | 1 | 325 | 307.8 | 315.2 | 97 | 679 | 6.8 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1413.5 | 104.7 | 42 | 1350 | - | 1123.1 | 83.2 | 910 | -21.5 | 2011 | 2021 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1823.2 | 95.7 | 42 | 1904.3 | - | 1909.2 | 100.3 | 910 | 4.6 | 2014 | 2011 | -3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 282.1 | 14.8
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 600 MW Export to CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1260 | 93.3 | 2 | 1350 | - | 966.8 | 71.6 | 42 | -21.7 | 2015 | 2028 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1694.5 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.1 | 92.8 | 2 | 40 | - | 36.8 | 92.1 | 42 | -0.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Populate Summary Worksheet

## PEC TRM HR Down 600ImCPLE_Duke
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 18 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 11 | Not in original screening
[25 empty] | 29 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1426.5 | 1667.2 | 125.2 | 48 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | -19.8 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 538.5 | 920.5 | 115.5 | 5 | 796.7 | 474 | 811.3 | 101.8 | 88 | -13.7 | 2011 | 2011 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 250.5 | 31.4
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 520.1 | 912.3 | 108.6 | 3 | 840 | 457.8 | 804.1 | 95.7 | 80 | -12.9 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 248.3 | 29.5
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 64.1 | 115.8 | 106.9 | 1 | 108.3 | 56 | 100.1 | 92.4 | 43 | -14.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 26.3 | 24.2
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 64.1 | 115.8 | 106.9 | 1 | 108.3 | 56 | 100.1 | 92.4 | 43 | -14.5 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 26.3 | 24.2
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 244.1 | 405.1 | 103.2 | 2 | 398 | 180.9 | 315.2 | 77.6 | 123 | -25.6 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 243.6 | 404.3 | 103 | 2 | 398 | 180.3 | 314.6 | 77.5 | 117 | -25.5 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1730.3 | 1940.3 | 102.6 | 66 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | -0.7 | 2011 | 2011 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 339.7 | 22.3
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 330.3 | 487.3 | 101.3 | 29 | 437 | 270.3 | 398.8 | 91.5 | 211 | -9.8 | 2011 | 2021 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 137.4 | 29.1
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 1 | 844-848-1 | 478 | 478 | 278 | 441.2 | 99.9 | 2 | 478 | 223.9 | 382.2 | 82 | 44 | -17.9 | 2012 | 2022 | 10 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 2 | 844-848-2 | 478 | 478 | 278 | 441.2 | 99.9 | 3 | 478 | 223.8 | 382.2 | 82 | 44 | -17.9 | 2012 | 2022 | 10 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 306.9 | 384.2 | 95.3 | 11 | 423 | 272.9 | 351.7 | 84.4 | 607 | -10.9 | 2014 | 2020 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230 | 20124 | METHOD 230 | 1 | 20073-20124-1 | 637 | 637 | 390 | 588.1 | 95.3 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500 | 850 | 8PL GRDN 500 | 1 | 849-850-1 | 1385.6 | 1385.6 | 1058.7 | 1313.8 | 95.2 | 42 | 1385.6 | 883 | 1244.2 | 88.8 | 174 | -6.4 | 2014 | 2017 | 3 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 292.5 | 24.5
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 482 | 482 | 330.3 | 448 | 94.7 | 28 | 437 | 270.3 | 398.8 | 91.5 | 167 | -3.2 | 2014 | 2021 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 841 | 6BOBWH B 230 | 1 | 714-841-1 | 478 | 478 | 350 | 450.5 | 94.4 | 21 | 478 | 359.8 | 449 | 92.9 | 376 | -1.5 | 2014 | 2015 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 65.6 | 16
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 842 | 6BOBWH W 230 | 2 | 714-842-2 | 478 | 478 | 350 | 450.5 | 94.4 | 22 | 478 | 360 | 449 | 92.9 | 419 | -1.5 | 2014 | 2015 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 65.6 | 16
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230 | 540 | 6MCGUIRE 230 | 1 | 537-540-1 | 318.6 | 318.6 | 189 | 293.5 | 90.7 | 3 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | 0.5 | 2016 | 2016 | 0 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 55 | 17.9
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 100.4 | 100.4 | 90.4 | 2 | 111 | 84 | 105.6 | 95.1 | 707 | 4.7 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 292.5 | 292.5 | 90 | 1 | 325 | 307.8 | 315.2 | 97 | 679 | 7 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 478 | 478 | 348.4 | 408.9 | 89.9 | 42 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 3.1 | 2017 | 2020 | 3 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 41.4 | 11
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 6 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1396.3 | 103.4 | 42 | 1350 | - | 1123.1 | 83.2 | 910 | -20.2 | 2011 | 2021 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1854.3 | 97.4 | 42 | 1904.3 | - | 1909.2 | 100.3 | 910 | 2.9 | 2013 | 2011 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 313.2 | 16.5
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 600 DUKExportCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Harris Down 600 MW Export to CPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.2 | 93.1 | 2 | 40 | - | 36.8 | 92.1 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1242.3 | 92 | 2 | 1350 | - | 966.8 | 71.6 | 42 | -20.4 | 2016 | 2028 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1667.2 | #N/A | #N/A
Populate Summary Worksheet

## PEC TRM BR1 Down 1200 AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 14 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1381.7 | 1630.3 | 120.6 | 50 | 1350 | 1052.8 | 1325.7 | 95.5 | 8925 | -25.1 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 69.5 | 125.6 | 116 | 3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | -15.1 | 2011 | 2011 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 36.1 | 33.3
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 69.5 | 125.6 | 116 | 3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | -15.1 | 2011 | 2011 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 36.1 | 33.3
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 541.7 | 865.9 | 103.1 | 4 | 840 | 554.2 | 885.3 | 105.4 | 140 | 2.3 | 2011 | 2011 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 134.6 | 16
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 465.4 | 796.3 | 99.9 | 2 | 796.7 | 421.5 | 721.5 | 90.6 | 52 | -9.3 | 2012 | 2016 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 126.3 | 15.8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1651.8 | 1872 | 97.7 | 73 | 1904.3 | 1650.3 | 1825.8 | 93.4 | 7950 | -4.3 | 2013 | 2015 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 271.4 | 17.4
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 424.4 | 706 | 97.6 | 3 | 717 | 434.9 | 723.3 | 99.8 | 124 | 2.2 | 2013 | 2012 | -1 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 121.3 | 18.4
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 451.8 | 819.9 | 97.6 | 1 | 840 | 462.1 | 838.2 | 99.8 | 44 | 2.2 | 2013 | 2012 | -1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 127.2 | 15.1
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 315.3 | 465.2 | 96.9 | 21 | 437 | 257.5 | 379.9 | 86.8 | 169 | -10.1 | 2013 | 2024 | 11 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 115.3 | 24.7
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 227.7 | 385.2 | 96.6 | 1 | 398 | 166.5 | 285.6 | 70.2 | 4 | -26.4 | 2013 | 2029 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 227.3 | 384.5 | 96.4 | 1 | 398 | 165.4 | 285.2 | 70.1 | 3 | -26.3 | 2013 | 2029 | 16 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 305.9 | 383.4 | 94 | 11 | 423 | 274.3 | 347.5 | 84.5 | 699 | -9.5 | 2015 | 2020 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 449.5 | 789.1 | 93.9 | 2 | 840 | 407.1 | 715.1 | 85.1 | 44 | -8.8 | 2015 | 2020 | 5 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 125.1 | 14.8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 482 | 482 | 315.3 | 431.7 | 90.9 | 20 | 437 | 257.5 | 379.9 | 86.8 | 126 | -4.1 | 2016 | 2024 | 8 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 100.6 | 100.6 | 90.6 | 2 | 111 | 83 | 105.6 | 95.2 | 455 | 4.6 | 2016 | 2014 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 293.3 | 293.3 | 90.2 | 1 | 325 | 303.7 | 315.1 | 97 | 567 | 6.8 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1348.2 | 99.9 | 42 | 1350 | - | 1024 | 75.9 | 910 | -24 | 2012 | 2025 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1782.2 | 93.6 | 42 | 1904.3 | - | 1761.8 | 92.5 | 910 | -1.1 | 2015 | 2015 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 241.1 | 12.7
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
Populate Summary Worksheet

## PEC TRM HR Down 1200 AEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 14 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 69.4 | 125.5 | 115.8 | 3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | -14.9 | 2011 | 2011 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 36 | 33.1
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 69.4 | 125.5 | 115.8 | 3 | 108.3 | 61.2 | 109.3 | 100.9 | 43 | -14.9 | 2011 | 2011 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 36 | 33.1
| GUARDSOUTH | 546 | 8MCGUIRE | 836 | 8WOODLF | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1361.6 | 1539.8 | 113.1 | 48 | 1350 | 1052.8 | 1325.7 | 95.5 | 8925 | -17.6 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 544.7 | 870.6 | 103.6 | 3 | 840 | 554.2 | 885.3 | 105.4 | 140 | 1.8 | 2011 | 2011 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 139.3 | 16.5
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 477.3 | 816.7 | 102.5 | 2 | 796.7 | 421.5 | 721.5 | 90.6 | 52 | -11.9 | 2011 | 2016 | 5 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 146.7 | 18.4
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1675.4 | 1882.1 | 99.2 | 73 | 1904.3 | 1650.3 | 1825.8 | 93.4 | 7950 | -5.8 | 2012 | 2015 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 281.5 | 18.9
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 427 | 710.4 | 98.4 | 2 | 717 | 434.9 | 723.3 | 99.8 | 124 | 1.4 | 2012 | 2012 | 0 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 125.7 | 19.2
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 454.2 | 824.2 | 98.1 | 1 | 840 | 462.1 | 838.2 | 99.8 | 44 | 1.7 | 2012 | 2012 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 131.5 | 15.6
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 316.2 | 466.7 | 97.3 | 20 | 437 | 257.5 | 379.9 | 86.8 | 169 | -10.5 | 2013 | 2024 | 11 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 116.8 | 25.1
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 461 | 809.4 | 96.4 | 2 | 840 | 407.1 | 715.1 | 85.1 | 44 | -11.3 | 2013 | 2020 | 7 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 145.4 | 17.3
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 223.7 | 378.7 | 95.8 | 1 | 398 | 166.5 | 285.6 | 70.2 | 4 | -25.6 | 2014 | 2029 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 223.3 | 378 | 95.6 | 1 | 398 | 165.4 | 285.2 | 70.1 | 3 | -25.5 | 2014 | 2029 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 307.8 | 384.1 | 95.1 | 11 | 423 | 274.3 | 347.5 | 84.5 | 699 | -10.6 | 2014 | 2020 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 482 | 482 | 316.2 | 429.4 | 90.8 | 19 | 437 | 257.5 | 379.9 | 86.8 | 126 | -4 | 2016 | 2024 | 8 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 100.3 | 100.3 | 90.4 | 3 | 111 | 83 | 105.6 | 95.2 | 455 | 4.8 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 478 | 478 | 351.8 | 409.8 | 90.1 | 40 | 436.9 | 346.6 | 391.4 | 93.2 | 2219 | 3.1 | 2017 | 2020 | 3 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 42.3 | 11.2
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 292.5 | 292.5 | 90 | 1 | 325 | 303.7 | 315.1 | 97 | 567 | 7 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1330.6 | 98.6 | 42 | 1350 | - | 1024 | 75.9 | 910 | -22.7 | 2012 | 2025 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1812.4 | 95.2 | 42 | 1904.3 | - | 1761.8 | 92.5 | 910 | -2.7 | 2014 | 2015 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 271.3 | 14.3
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK AEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK AEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
Populate Summary Worksheet

## PEC TRM BR1 Down 1200 VPAEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 16 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1351.1 | 1602.8 | 117.9 | 50 | 1350 | 1021.2 | 1293.1 | 92.9 | 8615 | -25 | 2011 | 2015 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 68.6 | 124 | 114.5 | 1 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | -15 | 2011 | 2012 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 34.5 | 31.8
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 68.6 | 124 | 114.5 | 1 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | -15 | 2011 | 2012 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 34.5 | 31.8
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 532.7 | 851.5 | 101.4 | 4 | 840 | 545.3 | 871.2 | 103.7 | 133 | 2.3 | 2011 | 2011 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 120.2 | 14.3
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 455.8 | 780.1 | 97.9 | 2 | 796.7 | 411.5 | 704.6 | 88.4 | 49 | -9.5 | 2013 | 2018 | 5 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 110.1 | 13.8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1632.9 | 1852.6 | 96.1 | 73 | 1904.3 | 1631 | 1802.2 | 92 | 7820 | -4.1 | 2014 | 2016 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 252 | 15.8
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 444.2 | 806.3 | 96 | 1 | 840 | 454.7 | 824.9 | 98.2 | 44 | 2.2 | 2014 | 2012 | -2 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 113.6 | 13.5
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 416 | 692.2 | 95.5 | 3 | 717 | 426.7 | 709.9 | 97.7 | 90 | 2.2 | 2014 | 2013 | -1 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 107.5 | 16.3
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 310.1 | 457.5 | 95.2 | 16 | 437 | 253 | 373.3 | 85.3 | 131 | -9.9 | 2014 | 2024 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 107.6 | 23
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 222.1 | 376.5 | 93.9 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 221.7 | 375.8 | 93.7 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 302.9 | 379.7 | 92.6 | 9 | 423 | 272.8 | 350.5 | 83.9 | 613 | -8.7 | 2015 | 2020 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 440.2 | 773.1 | 92 | 1 | 840 | 397.5 | 698.3 | 83.1 | 44 | -8.9 | 2016 | 2021 | 5 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 109.1 | 12.9
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 293.3 | 293.3 | 90.2 | 1 | 325 | 301.6 | 314.8 | 96.9 | 558 | 6.7 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 100 | 100 | 90 | 3 | 111 | 82.4 | 105.6 | 95.2 | 348 | 5.2 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1314.7 | 97.4 | 42 | 1350 | - | 992.5 | 73.5 | 910 | -23.9 | 2013 | 2027 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1758.4 | 92.3 | 42 | 1904.3 | - | 1740.1 | 91.4 | 910 | -0.9 | 2016 | 2016 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 217.3 | 11.4
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Br1 Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Brunswick 1 Down 1200 PECDUK VPAEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
Populate Summary Worksheet

## PEC TRM HR Down 1200 VPAEP
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 13 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 7 | Not in original screening
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1331 | 1577.7 | 116.9 | 51 | 1350 | 1021.2 | 1293.1 | 92.9 | 8615 | -24 | 2011 | 2015 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 68.5 | 123.8 | 114.4 | 1 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | -14.9 | 2011 | 2012 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 34.3 | 31.7
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 68.5 | 123.8 | 114.4 | 1 | 108.3 | 60.4 | 107.8 | 99.5 | 43 | -14.9 | 2011 | 2012 | 1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 34.3 | 31.7
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 535.6 | 856.2 | 101.9 | 4 | 840 | 545.3 | 871.2 | 103.7 | 133 | 1.8 | 2011 | 2011 | 0 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 124.9 | 14.8
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 467.8 | 800.6 | 100.5 | 2 | 796.7 | 411.5 | 704.6 | 88.4 | 49 | -12.1 | 2011 | 2018 | 7 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 130.6 | 16.4
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1656.7 | 1865.8 | 97.5 | 71 | 1904.3 | 1631 | 1802.2 | 92 | 7820 | -5.5 | 2013 | 2016 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 265.2 | 17.2
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 446.7 | 810.7 | 96.5 | 1 | 840 | 454.7 | 824.9 | 98.2 | 44 | 1.7 | 2013 | 2012 | -1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 118 | 14
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 418.7 | 696.7 | 96.3 | 3 | 717 | 426.7 | 709.9 | 97.7 | 90 | 1.4 | 2013 | 2013 | 0 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 112 | 17.1
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 482 | 482 | 311.1 | 459 | 95.6 | 18 | 437 | 253 | 373.3 | 85.3 | 131 | -10.3 | 2014 | 2024 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 109.1 | 23.4
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.2 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 451.8 | 793.5 | 94.5 | 2 | 840 | 397.5 | 698.3 | 83.1 | 44 | -11.4 | 2014 | 2021 | 7 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 129.5 | 15.4
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 304.8 | 380.7 | 93.7 | 12 | 423 | 272.8 | 350.5 | 83.9 | 613 | -9.8 | 2015 | 2020 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 219.1 | 370.7 | 93 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 218.7 | 370 | 92.8 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE5 | 845 | 6E.DURHM | 20063 | E12-RDMT | 1 | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 89.8 | 100.5 | 90.5 | 16 | 111 | 82.4 | 105.6 | 95.2 | 348 | 4.7 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 292.5 | 292.5 | 90 | 1 | 325 | 301.6 | 314.8 | 96.9 | 558 | 6.9 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1297 | 96.1 | 42 | 1350 | - | 992.5 | 73.5 | 910 | -22.6 | 2014 | 2027 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1789.3 | 94 | 42 | 1904.3 | - | 1740.1 | 91.4 | 910 | -2.6 | 2015 | 2016 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 248.2 | 13.1
2 | % Yearly Load Growth |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening PEC TRM Har Dn 1200 PECDUK VPAEP Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP | [5 empty] | 2011 Summer Screening - 1200ImportDukeCPLE_AEPVP | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - PEC TRM Harris Down 1200 PECDUK VPAEP
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
Populate Summary Worksheet

## Duke 1200 to CPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - Duke1200MWtoCPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Duke1200MWtoCPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Duke1200MWtoCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 29 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 5 | Not in original screening
[25 empty] | 34 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Duke1200MWtoCPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
OXFDGM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20024 | ROX 1-4F 230 | 20870 | ROX #2 24.0 | 1 | 20024-20870-1 | 822 | 822 | 670.3 | 1403.8 | 170.8 | 5536 | 822 | 667.8 | 1667.7 | 202.9 | 5261 | 32.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 844 | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800 | ASHEVIL 115 | 20852 | ASHVL #220.0 | 1 | 20800-20852-1 | 235 | 235 | 185.4 | 377.6 | 160.7 | 536 | 235 | 185.6 | 379.1 | 161.3 | 542 | 0.6 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20285 | SEY JOHN 115 | 20287 | GOLDS SW 115 | 1 | 20285-20287-1 | 119 | 119 | 41.8 | 153.8 | 131.1 | 215 | 119 | 48.4 | 164.1 | 136.8 | 129 | 5.7 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 402 | 20389 | P2-FAY E | 20369 | FAY E | 2 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 1 | 20369-20389-1 | 150 | 150 | 93.6 | 186.7 | 124.5 | 173 | 150 | 93.7 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 401 | 20389 | P2-FAY E | 20369 | FAY E | 1 | 20369 | FAY E 69.0 | 20389 | P2-FAY E 230 | 2 | 20369-20389-2 | 150 | 150 | 93 | 186.7 | 124.5 | 173 | 150 | 93.1 | 186.8 | 124.5 | 43 | 0 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20261 | LEE 115 | 20284 | WEIL 115 | 1 | 20261-20284-1 | 201 | 201 | 120.3 | 234.5 | 117.8 | 947 | 201 | 126 | 247.2 | 120 | 172 | 2.2 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500 | 20377 | RICHMOND 500 | 1 | 337-20377-1 | 1350 | 1350 | 1256.2 | 1526.2 | 111.5 | 9164 | 1350 | 1037.5 | 1320.5 | 94.9 | 8129 | -16.6 | 2011 | 2014 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 6 | 847-849-6 | 796.7 | 796.7 | 502.9 | 860.9 | 108.1 | 3283 | 796.7 | 435 | 745 | 93.5 | 87 | -14.6 | 2011 | 2015 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 190.9 | 24
BEL1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500 | 850 | 8PL GRDN 500 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1824.3 | 2019.1 | 105.5 | 7646 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7732 | -10.4 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 418.5 | 25.2
OCO1GM | 34 | 20089 | HENDERSN | 20105 | FRANKLIN | 5 | 20182 | FALLS 230 | 20185 | FALLS 115 | 1 | 20182-20185-1 | 300 | 300 | 215.4 | 315.9 | 105.3 | 2794 | 300 | 213.3 | 306.1 | 102 | 1886 | -3.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20284 | WEIL 115 | 1 | 20239-20284-1 | 201 | 201 | 90 | 204.8 | 102.9 | 351 | 201 | 96 | 214.3 | 105.4 | 43 | 2.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230 | 849 | 8PARKWOD 500 | 5 | 847-849-5 | 840 | 840 | 485.7 | 853.2 | 101.6 | 3170 | 840 | 420.2 | 738.3 | 87.9 | 44 | -13.7 | 2011 | 2018 | 7 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 189.2 | 22.5
BEL1GM | SINGLE 399 | 20387 | P1-FAY 0 | 20392 | FAY | 2 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 1 | 20387-20392-1 | 200 | 200 | 117.3 | 198 | 99 | 1202 | 200 | 101.4 | 171.3 | 85.7 | 43 | -13.3 | 2012 | 2019 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 398 | 20387 | P1-FAY 0 | 20392 | FAY | 1 | 20387 | P1-FAY 0 230 | 20392 | FAY 115 | 2 | 20387-20392-2 | 200 | 200 | 117.1 | 197.9 | 98.9 | 1197 | 200 | 101.2 | 171.2 | 85.6 | 43 | -13.3 | 2012 | 2019 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20185 | FALLS 115 | 1 | 20111-20185-1 | 170 | 170 | 73.6 | 160.6 | 98.7 | 768 | 170 | 76.2 | 156 | 94.6 | 172 | -4.1 | 2012 | 2014 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 530 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20465 | NEW BERN 230 | 20471 | CCWDCG T 230 | 1 | 20465-20471-1 | 478 | 478 | 259.2 | 445.3 | 98.5 | 2721 | 478 | 232.6 | 417.1 | 88.5 | 86 | -10 | 2012 | 2018 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 473 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20519 | M-TARAWA 230 | 20524 | JACKSONV 230 | 1 | 20519-20524-1 | 478 | 478 | 332.4 | 443 | 97.9 | 2384 | 478 | 315.6 | 414.1 | 89.8 | 696 | -8.1 | 2013 | 2017 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 678 | 542 | 6OAKBORO | 538 | 6HARRISB | 2 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 1 | 538-542-1 | 437 | 437 | 289.5 | 427.2 | 97.6 | 3884 | 437 | 249.4 | 367.6 | 83.9 | 85 | -13.7 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 677 | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230 | 542 | 6OAKBORO 230 | 2 | 538-542-2 | 437 | 437 | 289.5 | 427.2 | 97.6 | 3928 | 437 | 248.6 | 366.8 | 83.9 | 128 | -13.7 | 2013 | 2020 | 7 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 77.3 | 25.4
CLIFGM | SINGLE 418 | 20398 | M-FBWOOD | 20338 | E15-BRDW | 1 | 20378 | RICHMOND 230 | 20976 | RICH EMC13.8 | 1 | 20378-20976-1 | 325 | 325 | 309.7 | 315.8 | 97.2 | 505 | 325 | 301.2 | 314.8 | 96.9 | 423 | -0.3 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 634 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20725 | CAMDEN 115 | 20731 | I-DUP CA 115 | 1 | 20725-20731-1 | 108 | 108 | 61.1 | 103.1 | 96.5 | 56 | 108 | 74.6 | 118.5 | 110.8 | 49 | 14.3 | 2013 | 2011 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20985 | ANSON 230 | 20986 | LILESEMC13.8 | 1 | 20985-20986-1 | 390 | 390 | 348.1 | 376 | 96.4 | 1647 | 390 | 344.5 | 364.5 | 93.5 | 554 | -2.9 | 2013 | 2015 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 445 | 20421 | LAURINBG | 20424 | LAURINBG | 2 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 1 | 20421-20424-1 | 200 | 200 | 106.7 | 192.7 | 96.4 | 523 | 200 | 104.9 | 189.9 | 95 | 43 | -1.4 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 444 | 20421 | LAURINBG | 20424 | LAURINBG | 1 | 20421 | LAURINBG 115 | 20424 | LAURINBG 230 | 2 | 20421-20424-2 | 200 | 200 | 106 | 192.5 | 96.2 | 458 | 200 | 104.1 | 189.5 | 94.8 | 43 | -1.4 | 2013 | 2014 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230 | 20616 | BARNARD 115 | 1 | 20615-20616-1 | 150 | 150 | 143 | 143 | 95.4 | 87 | 150 | 142.9 | 142.9 | 95.2 | 87 | -0.2 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20875 | LEE #1 13.8 | 1 | 20030-20875-1 | 111 | 111 | 105.6 | 105.6 | 95.1 | 136 | 111 | 79.4 | 79.4 | 71.5 | 130 | -23.6 | 2014 | 2028 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 841 | 6BOBWH B 230 | 1 | 714-841-1 | 478 | 478 | 365.8 | 457.8 | 95.1 | 1378 | 478 | 328.3 | 416.2 | 85.7 | 126 | -9.4 | 2014 | 2019 | 5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 72.9 | 16.7
OCO1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230 | 842 | 6BOBWH W 230 | 2 | 714-842-2 | 478 | 478 | 365.8 | 457.8 | 95.1 | 1422 | 478 | 328.3 | 416.2 | 85.7 | 162 | -9.4 | 2014 | 2019 | 5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 72.9 | 16.7
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20545 | CASTLE H 115 | 1 | 20544-20545-1 | 179 | 179 | 118.8 | 157.7 | 95 | 1069 | 179 | 111.9 | 147.1 | 85.1 | 344 | -9.9 | 2014 | 2020 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 230 | 20185 | FALLS | 20145 | NEUSE | 1 | 20155 | CHSTNT H 115 | 20163 | MILBURNE 115 | 1 | 20155-20163-1 | 158 | 158 | 18.3 | 139.3 | 94.9 | 172 | 158 | 27.5 | 139.4 | 93.2 | 43 | -1.7 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 636 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20725 | CAMDEN 115 | 1 | 20716-20725-1 | 108 | 108 | 61.8 | 101.3 | 94.8 | 346 | 108 | 64.2 | 112.4 | 105.1 | 51 | 10.3 | 2014 | 2011 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 1 | 443-540-1 | 478 | 478 | 290.6 | 457.6 | 93.5 | 241 | 478 | 333.2 | 503.2 | 103.2 | 68 | 9.7 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 69.6 | 14.5
MAR3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230 | 540 | 6MCGUIRE 230 | 2 | 443-540-2 | 478 | 478 | 290.6 | 457.6 | 93.5 | 277 | 478 | 333.2 | 503.2 | 103.2 | 69 | 9.7 | 2015 | 2011 | -4 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | 69.6 | 14.5
BEL1GM | SINGLE 530 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20524 | JACKSONV 230 | 20528 | RHEMS 230 | 1 | 20524-20528-1 | 478 | 478 | 233.7 | 422.8 | 93.4 | 1787 | 478 | 208.3 | 390.9 | 83.8 | 43 | -9.6 | 2015 | 2020 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
JOC1GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20564 | SCOTT T 230 | 1 | 20550-20564-1 | 478 | 478 | 329.8 | 438.6 | 93.4 | 3203 | 478 | 306.7 | 403.9 | 85.7 | 343 | -7.7 | 2015 | 2019 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230 | 541 | 6MORN ST 230 | 1 | 333-541-1 | 436.9 | 436.9 | 340.3 | 393.4 | 93.1 | 2353 | 436.9 | 338.7 | 380.8 | 90.4 | 2085 | -2.7 | 2015 | 2017 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 25.9 | 14.2
BEL1GM | PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500 | 850 | 8PL GRDN 500 | 1 | 849-850-1 | 1385.6 | 1385.6 | 940.3 | 1289.5 | 92.8 | 6566 | 1385.6 | 837 | 1174.5 | 82.7 | 44 | -10.1 | 2015 | 2021 | 6 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 268.2 | 22.1
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20885 | WSP #3 13.8 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 130 | 95 | 88.1 | 88.1 | 92.8 | 130 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20041 | CF 5-6 F 230 | 20053 | CAPE 5&6 115 | 1 | 20041-20053-1 | 350 | 350 | 317.9 | 323.2 | 92.4 | 435 | 350 | 315.2 | 322.9 | 92.3 | 130 | -0.1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 265 | 20222 | ROCKY MT | 20221 | PA-RMT | 2 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 1 | 20221-20222-1 | 168 | 168 | 76.6 | 154.5 | 92 | 43 | 168 | 76.6 | 153.8 | 91.5 | 43 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 264 | 20222 | ROCKY MT | 20221 | PA-RMT | 1 | 20221 | PA-RMT 69.0 | 20222 | ROCKY MT 230 | 2 | 20221-20222-2 | 168 | 168 | 76.6 | 154.5 | 92 | 43 | 168 | 76.6 | 153.7 | 91.5 | 43 | -0.5 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 2 | 712-719-2 | 840 | 840 | 483.1 | 772.4 | 92 | 1495 | 840 | 501.2 | 801.2 | 95.4 | 82 | 3.4 | 2016 | 2014 | -2 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | 41.1 | 4.9
BEL1GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20163 | MILBURNE 115 | 20168 | YONKERS 115 | 1 | 20163-20168-1 | 190 | 190 | 43.9 | 165.3 | 91.9 | 172 | 190 | 55.1 | 165.2 | 90.3 | 172 | -1.6 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 2 | 236-265-2 | 452.5 | 452.5 | 282 | 417.5 | 91.3 | 1480 | 452.5 | 283.3 | 419.2 | 92.1 | 49 | 0.8 | 2016 | 2016 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -3.3 | -0.1
BEL1GM | STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230 | 445 | 6STAMEY 230 | 2 | 443-445-2 | 889 | 889 | 497.1 | 827.8 | 90.9 | 1784 | 889 | 486.6 | 810.2 | 89 | 44 | -1.9 | 2016 | 2017 | 1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 72.7 | 9.3
BEL1GM | SINGLE 366 | 20348 | RKH | 20361 | WEST END | 1 | 20348 | RKH 230 | 20638 | WDSB T 230 | 1 | 20348-20638-1 | 539 | 539 | 316.2 | 493.3 | 90.5 | 2192 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230 | 20862 | BRUN #1 24.0 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 1067 | 963.3 | 963.3 | 90.3 | 130 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20544 | HOLLY RG 115 | 20546 | E9-TOPSL 115 | 1 | 20544-20546-1 | 179 | 179 | 111.1 | 149.3 | 90.2 | 1069 | 179 | 104.2 | 139.3 | 80.6 | 258 | -9.6 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 1 | 7-106-1 | 478 | 478 | 186.1 | 443.8 | 90.1 | 45 | 478 | 187.8 | 430.9 | 87.6 | 2 | -2.5 | 2017 | 2018 | 1 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | KATOMA | 8 | 8OCONEE | 5004 | 8KATRTRT | 1 | 7 | 6OCONEE 230 | 106 | 6JOCASSE 230 | 2 | 7-106-2 | 478 | 478 | 186.1 | 443.8 | 90.1 | 46 | 478 | 187.8 | 430.9 | 87.6 | 2 | -2.5 | 2017 | 2018 | 1 |  | 459.7 | 477.96 | 477.96 | JOCASSEE | 230 kV Line | 765.2496 | 851.6937 | 765.2496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20020 | BRUN 2 N 230 | 20863 | BRUN #2 24.0 | 1 | 20020-20863-1 | 1067 | 1067 | 959.5 | 959.5 | 89.9 | 130 | 1067 | 959.5 | 959.5 | 89.9 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | 6 | 20030 | LEE 1-3F | 20281 | BELFAST | 5 | 20239 | GOLD C T 115 | 20285 | SEY JOHN 115 | 1 | 20239-20285-1 | 201 | 201 | 64.9 | 178.6 | 89.9 | 129 | 201 | 71 | 188.2 | 92.9 | 43 | 3 | 2017 | 2015 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20350 | PH SH 1B 230 | 20985 | ANSON 230 | 1 | 20350-20985-1 | 398 | 398 | 214.9 | 362.3 | 89.9 | 2592 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20097 | CG-ROX 230 | 1 | 20066-20097-1 | 423 | 423 | 287.3 | 366.2 | 89.8 | 3698 | 423 | 256.4 | 333 | 79.3 | 230 | -10.5 | 2017 | 2023 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20349 | PH SH 2W 230 | 20985 | ANSON 230 | 1 | 20349-20985-1 | 398 | 398 | 214.5 | 361.6 | 89.7 | 2689 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2017 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 227 | 20185 | FALLS | 20111 | E18-WK F | 1 | 20089 | HENDERSN 115 | 20105 | FRANKLIN 115 | 1 | 20089-20105-1 | 201 | 201 | 122.7 | 165.2 | 89.4 | 1960 | 201 | 113.9 | 157.6 | 84.5 | 54 | -4.9 | 2017 | 2020 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20106 | WAKEFORE 115 | 20107 | E18-WEMC69.0 | 1 | 20106-20107-1 | 40 | 40 | 35.7 | 35.7 | 89.3 | 87 | 40 | 35.7 | 35.7 | 89.3 | 87 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 212 | 20163 | MILBURNE | 20168 | YONKERS | 1 | 20137 | METHOD 115 | 20150 | I-NCSU S 115 | 1 | 20137-20150-1 | 190 | 190 | 122.7 | 165 | 89.3 | 2093 | 190 | 110.9 | 164.1 | 87.8 | 92 | -1.5 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20556 | TOPSL T 230 | 20564 | SCOTT T 230 | 1 | 20556-20564-1 | 478 | 478 | 308.4 | 415.8 | 89.2 | 3189 | 478 | 285.4 | 381.6 | 81.4 | 215 | -7.8 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 179 | 20124 | METHOD | 20137 | METHOD | 1 | 20124 | METHOD 230 | 20137 | METHOD 115 | 2 | 20124-20137-2 | 300 | 300 | 172.7 | 266.8 | 88.9 | 2734 | 300 | 158.1 | 244.4 | 81.5 | 43 | -7.4 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 2W | 20800 | ASHEVIL | 20762 | ENKA SW | 5 | 20793 | BILTMORE 115 | 20806 | OTEEN 115 | 1 | 20793-20806-1 | 279 | 279 | 83.6 | 245.6 | 88.9 | 86 | 279 | 74.8 | 227.4 | 82.2 | 86 | -6.7 | 2017 | 2021 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 180 | 20124 | METHOD | 20137 | METHOD | 2 | 20124 | METHOD 230 | 20137 | METHOD 115 | 1 | 20124-20137-1 | 300 | 300 | 172.3 | 266.5 | 88.8 | 2704 | 300 | 157.7 | 244.1 | 81.4 | 43 | -7.4 | 2017 | 2022 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 1 | 844-848-1 | 478 | 478 | 244.6 | 406.5 | 88.6 | 2061 | 478 | 188.4 | 334.1 | 71.2 | 3 | -17.4 | 2018 | 2029 | 11 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230 | 848 | 6PL GRDN 230 | 2 | 844-848-2 | 478 | 478 | 244.6 | 406.5 | 88.6 | 2105 | 478 | 188.4 | 334.1 | 71.2 | 3 | -17.4 | 2018 | 2029 | 11 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20876 | LEE #2 13.8 | 1 | 20030-20876-1 | 106 | 106 | 93.8 | 93.8 | 88.5 | 130 | 106 | 76.4 | 81.4 | 76.8 | 131 | -11.7 | 2018 | 2025 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 2 | 443-544-2 | 478 | 478 | 326.8 | 429.1 | 88.4 | 1640 | 478 | 334.2 | 438.6 | 90.7 | 252 | 2.3 | 2018 | 2016 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 17.8 | 3.8
BEL1GM | SINGLE 256 | 20205 | CLINTON | 20255 | CLINTON | 1 | 20265 | E15-STED 115 | 20401 | VANDER 115 | 1 | 20265-20401-1 | 163 | 163 | 118.6 | 139.2 | 88.2 | 1939 | 163 | 90.8 | 115.6 | 71.7 | 86 | -16.5 | 2018 | 2028 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 329 | 20309 | BISCOE W | 20332 | ASHEB | 1 | 20303 | SEAGROVE 115 | 20304 | E14-ULAH 115 | 1 | 20303-20304-1 | 148 | 148 | 69.5 | 128.8 | 88 | 391 | 148 | 63.6 | 118.6 | 80.2 | 43 | -7.8 | 2018 | 2023 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 523 | 20515 | WALLACE | 20517 | WALLACE | 1 | 20513 | BURGAW C 115 | 20533 | ID/OCC T 115 | 1 | 20513-20533-1 | 120 | 120 | 62.5 | 104.3 | 87.4 | 527 | 120 | 54.7 | 93.7 | 77.6 | 49 | -9.8 | 2018 | 2024 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 120 | 20054 | DURHAM | 20183 | WAKE | 1 | 20024 | ROX 1-4F 230 | 20872 | ROX #4 24.0 | 1 | 20024-20872-1 | 883 | 883 | 749.3 | 771.1 | 87.3 | 4765 | 883 | 719 | 769.7 | 87.2 | 2677 | -0.1 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230 | 540 | 6MCGUIRE 230 | 1 | 537-540-1 | 318.6 | 318.6 | 162.3 | 285 | 87.2 | 2102 | 318.6 | 162.7 | 283.2 | 86.9 | 44 | -0.3 | 2018 | 2019 | 1 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 46.5 | 14.4
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230 | 719 | 8ANTIOCH 500 | 1 | 712-719-1 | 840 | 840 | 402.9 | 731.5 | 87.1 | 146 | 840 | 418 | 758.7 | 90.3 | 44 | 3.2 | 2018 | 2017 | -1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | 38.8 | 4.6
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 837 | 6ROWANG 230 | 840 | 6ROWANT 230 | 1 | 837-840-1 | 1110 | 1110 | 976.9 | 976.9 | 86.9 | 175 | 1110 | 977.5 | 977.5 | 86 | 37 | -0.9 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 362 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20004 | TIL 1-4H 115 | 20302 | E14-TROY 115 | 1 | 20004-20302-1 | 269 | 269 | 149.2 | 234.6 | 86.6 | 2126 | 269 | 117.3 | 201.3 | 74.2 | 82 | -12.4 | 2019 | 2027 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20883 | WSP #1 13.8 | 1 | 20047-20883-1 | 62 | 62 | 53.7 | 53.7 | 86.6 | 130 | 62 | 53.7 | 53.7 | 86.6 | 130 | 0 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NANTGM | BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115 | 20884 | WSP #2 13.8 | 1 | 20047-20884-1 | 62 | 62 | 53.7 | 53.7 | 86.6 | 130 | 62 | 53.7 | 53.7 | 86.6 | 130 | 0 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 1 | 101-3164-1 | 108.3 | 108.3 | 52.5 | 93.7 | 86.5 | 517 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 7.3 | 2019 | 2015 | -4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 4.2 | 3.8
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115 | 3164 | HORSESH2 100 | 2 | 101-3164-2 | 108.3 | 108.3 | 52.5 | 93.7 | 86.5 | 517 | 108.3 | 56.8 | 101.5 | 93.8 | 43 | 7.3 | 2019 | 2015 | -4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 4.2 | 3.8
BEL1GM | SINGLE 808 | 20762 | ENKA SW | 20800 | ASHEVIL | 1 | 20767 | BENT CRK 115 | 20799 | AVERYCRK 115 | 1 | 20767-20799-1 | 264 | 264 | 151.9 | 228.4 | 86.5 | 1686 | 264 | 143.1 | 215 | 81.4 | 86 | -5.1 | 2019 | 2022 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 808 | 20762 | ENKA SW | 20800 | ASHEVIL | 1 | 20799 | AVERYCRK 115 | 20800 | ASHEVIL 115 | 1 | 20799-20800-1 | 264 | 264 | 152.3 | 229.5 | 86.5 | 1680 | 264 | 143.6 | 216 | 81.4 | 86 | -5.1 | 2019 | 2022 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 453 | 20428 | BISCOE W | 20294 | BISCOSUB | 1 | 20290 | I-OLVRRB 115 | 20312 | ASHEB E 115 | 1 | 20290-20312-1 | 138 | 138 | 16.5 | 116.6 | 86.4 | 43 | 138 | 19.6 | 116.6 | 85.3 | 43 | -1.1 | 2019 | 2020 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 10 | 20163 | MILBURNE | 20170 | CLAYTON | 5 | 20137 | METHOD 115 | 20153 | TRYON HL 115 | 1 | 20137-20153-1 | 108 | 108 | 64 | 88.9 | 86.3 | 1288 | 108 | 57.1 | 88.9 | 85.1 | 106 | -1.2 | 2019 | 2020 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 523 | 20515 | WALLACE | 20517 | WALLACE | 1 | 20533 | ID/OCC T 115 | 20545 | CASTLE H 115 | 1 | 20533-20545-1 | 131 | 131 | 71.5 | 113.1 | 86.3 | 535 | 131 | 63.6 | 103.1 | 77.8 | 86 | -8.5 | 2019 | 2024 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 20018 | ROB 2 N 230 | 20864 | ROB #2 22.0 | 1 | 20018-20864-1 | 878 | 878 | 734.4 | 756.9 | 86.2 | 1015 | 878 | 728.2 | 736.1 | 83.8 | 174 | -2.4 | 2019 | 2020 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TUXDGM | SINGLE 120 | 20054 | DURHAM | 20183 | WAKE | 1 | 20024 | ROX 1-4F 230 | 20871 | ROX #3 24.0 | 1 | 20024-20871-1 | 883 | 883 | 747.3 | 759.9 | 86.1 | 5193 | 883 | 717.6 | 759.2 | 86 | 2758 | -0.1 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 339 | 20331 | ASHEB | 20332 | ASHEB | 1 | 20331 | ASHEB 115 | 20332 | ASHEB 230 | 2 | 20331-20332-2 | 200 | 200 | 99.6 | 172.2 | 86.1 | 301 | 200 | 101 | 174.6 | 87.3 | 86 | 1.2 | 2019 | 2018 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
TURNGM | SINGLE 34 | 20020 | BRUN 2 N | 20515 | WALLACE | 1 | 20039 | SUT 3 F 230 | 20520 | I-KOSA 230 | 1 | 20039-20520-1 | 478 | 478 | 310.1 | 404.8 | 86 | 2499 | 478 | 281.5 | 368.5 | 76.7 | 133 | -9.3 | 2019 | 2025 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | WOODLAWN5 | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230 | 545 | 6WOODLWN 230 | 2 | 331-545-2 | 717 | 717 | 400.3 | 605.5 | 85.6 | 2204 | 717 | 413.6 | 625.2 | 88.9 | 174 | 3.3 | 2019 | 2017 | -2 |  | 717 | 717 | 717 | STEELBERRY | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 394.5 | 597 | 84.4 | 8.5 | 1.2
BUC5GM | SINGLE 340 | 20331 | ASHEB | 20332 | ASHEB | 2 | 20331 | ASHEB 115 | 20332 | ASHEB 230 | 1 | 20331-20332-1 | 200 | 200 | 99.1 | 170.8 | 85.4 | 301 | 200 | 100.4 | 174.3 | 87.2 | 86 | 1.8 | 2019 | 2018 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 395 | 20387 | P1-FAY 0 | 20389 | P2-FAY E | 1 | 20387 | P1-FAY 0 230 | 20388 | P3-FAYRR 230 | 1 | 20387-20388-1 | 637 | 637 | 387.5 | 536.9 | 85.4 | 4355 | 637 | 377 | 508.4 | 79.7 | 123 | -5.7 | 2019 | 2023 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 55 | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024 | ROX 1-4F 230 | 20869 | ROX #1 22.0 | 1 | 20024-20869-1 | 483 | 483 | 403.2 | 411.9 | 85.3 | 2425 | 483 | 389 | 411.4 | 85.2 | 1796 | -0.1 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115 | 20877 | LEE #3 18.0 | 1 | 20030-20877-1 | 333 | 333 | 284 | 284 | 85.3 | 130 | 333 | 253.3 | 269.4 | 80.9 | 760 | -4.4 | 2020 | 2022 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20540 | GEI&SW T 230 | 20556 | TOPSL T 230 | 1 | 20540-20556-1 | 478 | 478 | 284 | 386.4 | 85.3 | 2796 | 478 | 261.9 | 355.3 | 77.6 | 167 | -7.7 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 840 | 20800 | ASHEVIL | 20799 | AVERYCRK | 1 | 20762 | ENKA SW 115 | 20800 | ASHEVIL 115 | 1 | 20762-20800-1 | 264 | 264 | 144.5 | 224.5 | 85.3 | 1581 | 264 | 135.7 | 211.2 | 80.2 | 129 | -5.1 | 2020 | 2023 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 654 | 337 | 8NEWPORT | 5003 | 8ASBRTRT | 1 | 337 | 8NEWPORT 500 | 546 | 8MCGUIRE 500 | 1 | 337-546-1 | 1249.6 | 1249.6 | 764.7 | 1108.1 | 85.2 | 400 | 1249.6 | 669.6 | 997.1 | 76.2 | 1 | -9 | 2020 | 2025 | 5 |  | 1249.638 | 1725.072 | 1346.63 | WOODCHUCK | 500 kV Line | 2851.738 | 2851.738 | 2851.738 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 212 | 20163 | MILBURNE | 20168 | YONKERS | 1 | 20148 | RALEIGH 115 | 20150 | I-NCSU S 115 | 1 | 20148-20150-1 | 159 | 159 | 88.1 | 130.2 | 85.2 | 1787 | 159 | 76.4 | 128.6 | 83.1 | 43 | -2.1 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 538 | 6HARRISB 230 | 540 | 6MCGUIRE 230 | 4 | 538-540-4 | 490.8 | 490.8 | 369.2 | 416.8 | 85.1 | 2458 | 490.8 | 359.3 | 398.6 | 81.6 | 832 | -3.5 | 2020 | 2022 | 2 |  | 490.8 | 563.7 | 540.2 | MECKLENBURG WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 563.7 | 333.5 | 415.6 | 73.7 | 1.2 | 11.4
OCO1GM | SINGLE 234 | 20190 | WAKE | 20191 | WENDELL | 1 | 20070 | PERSON 230 | 20079 | OXF S T 230 | 1 | 20070-20079-1 | 539 | 539 | 385.1 | 448.9 | 85 | 4472 | 539 | 354.9 | 413.8 | 77.7 | 543 | -7.3 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV6GM | SINGLE 415 | 20392 | FAY | 20402 | E15-VAND | 1 | 20392 | FAY 115 | 20401 | VANDER 115 | 1 | 20392-20401-1 | 163 | 163 | 69.3 | 138.3 | 84.8 | 86 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2020 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20619 | MASONBOR 230 | 20621 | BARNRD W 230 | 1 | 20619-20621-1 | 637 | 637 | 397.3 | 539.9 | 84.7 | 1979 | 637 | 386.2 | 515.8 | 82 | 258 | -2.7 | 2020 | 2022 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230 | 716 | 6MITCH R 230 | 2 | 712-716-2 | 717 | 717 | 369.9 | 615.6 | 84.6 | 176 | 717 | 386.2 | 643 | 88 | 44 | 3.4 | 2020 | 2018 | -2 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | 30.9 | 5.4
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20015 | MAYO 1F 500 | 20873 | MAYO #1 20.0 | 1 | 20015-20873-1 | 917 | 917 | 775.7 | 775.7 | 84.6 | 308 | 917 | 775.7 | 775.7 | 84.6 | 350 | 0 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20354 | I-ROCKY 230 | 20524 | JACKSONV 230 | 1 | 20354-20524-1 | 478 | 478 | 311.8 | 371.1 | 84.3 | 1551 | 478 | 293.9 | 379.1 | 82.9 | 364 | -1.4 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230 | 20157 | HOMESTED 230 | 1 | 20066-20157-1 | 423 | 423 | 264.3 | 343.4 | 84.2 | 3730 | 423 | 233.6 | 310.3 | 73.9 | 216 | -10.3 | 2020 | 2027 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20200 | ZEBULON 230 | 20203 | BAILEY T 230 | 1 | 20200-20203-1 | 637 | 637 | 389.1 | 516.6 | 84.2 | 5057 | 637 | 356.3 | 476.5 | 75.9 | 129 | -8.3 | 2020 | 2025 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | RIPPB | 335 | 6RIPP | 336 | 6SHELBY | 1 | 335 | 6RIPP 230 | 336 | 6SHELBY 230 | 2 | 335-336-2 | 736.6 | 736.6 | 364.9 | 619 | 83.8 | 54 | 736.6 | 368.4 | 624.5 | 85.1 | 1 | 1.3 | 2020 | 2020 | 0 |  | 736.6 | 736.6 | 736.6 | RIPP | 230 kV Line | 320.2468 | 320.2468 | 320.2468 | 736.6 | 345.7 | 587.2 | 80.2 | 31.8 | 3.6
MCG2GM | SINGLE 362 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20302 | E14-TROY 115 | 20683 | BURNETTE 115 | 1 | 20302-20683-1 | 269 | 269 | 139.3 | 221.6 | 83.7 | 1414 | 269 | 108.8 | 190.4 | 71.4 | 38 | -12.3 | 2020 | 2029 | 9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 9 | 20415 | RAEFORD | 20356 | ROCKFISH | 5 | 20047 | WSP BUS 115 | 20406 | ST PAULS 115 | 1 | 20047-20406-1 | 119 | 119 | 75 | 99 | 83.6 | 1290 | 119 | 72.3 | 93 | 77.8 | 192 | -5.8 | 2021 | 2024 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 453 | 20428 | BISCOE W | 20294 | BISCOSUB | 1 | 20312 | ASHEB E 115 | 20331 | ASHEB 115 | 1 | 20312-20331-1 | 201 | 201 | 90.5 | 165.2 | 83.3 | 215 | 201 | 94.6 | 165.3 | 82.3 | 86 | -1 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 104 | 20047 | WSP BUS | 115 | ROB #1 | 1 | 20632 | MARION 115 | 20654 | DILLON T 115 | 1 | 20632-20654-1 | 97 | 97 | 52.9 | 80.7 | 83.3 | 728 | 97 | 49.9 | 80.7 | 82.7 | 43 | -0.6 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 72 | 20035 | SUT 1-2F | 20545 | CASTLE H | 1 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 2 | 20035-20545-2 | 131 | 131 | 62.3 | 107.6 | 83.2 | 879 | 131 | 55.2 | 98.1 | 72.9 | 43 | -10.3 | 2021 | 2027 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 36 | 20182 | FALLS | 20024 | ROX 1-4F | 5 | 20078 | WD VALLY 230 | 20117 | DURHAM 230 | 1 | 20078-20117-1 | 541 | 541 | 276.5 | 439.8 | 83.1 | 2368 | 541 | 229.7 | 377.7 | 70.1 | 1 | -13 | 2021 | 2029 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230 | 443 | 6MARSHAL 230 | 1 | 443-713-1 | 478 | 478 | 283.8 | 408 | 82.9 | 2086 | 478 | 294.5 | 414.5 | 84.5 | 71 | 1.6 | 2021 | 2020 | -1 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 45.7 | 9.8
BUZDGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230 | 443 | 6MARSHAL 230 | 2 | 443-713-2 | 478 | 478 | 283.9 | 408.1 | 82.9 | 2129 | 478 | 294.5 | 414.5 | 84.5 | 71 | 1.6 | 2021 | 2020 | -1 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 45.8 | 9.8
OCO3GM | BASE CASE | 0 |  | 0 |  |  | 714 | 6BELEWS 230 | 827 | 6ERNEST1 230 | 1 | 714-827-1 | 576 | 576 | 494.8 | 494.8 | 82.9 | 24 | 576 | 495.8 | 495.8 | 82.8 | 3 | -0.1 | 2021 | 2021 | 0 |  | 576 | 621.4 | 576 | JACOBS | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | 576 | 494.6 | 494.6 | 81.7 | 0.2 | 1.2
BEL1GM | SINGLE 204 | 20162 | MILBURNE | 20163 | MILBURNE | 2 | 20162 | MILBURNE 230 | 20163 | MILBURNE 115 | 1 | 20162-20163-1 | 300 | 300 | 187.1 | 248.2 | 82.7 | 2804 | 300 | 193.2 | 256.1 | 85.4 | 638 | 2.7 | 2021 | 2019 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20329 | RAMSEUR 69.0 | 20330 | I-RAMTEX69.0 | 1 | 20329-20330-1 | 19 | 19 | 15.6 | 15.6 | 82.7 | 87 | 19 | 15.6 | 15.6 | 81.8 | 87 | -0.9 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | SINGLE 145 | 20070 | PERSON | 20079 | OXF S T | 1 | 20035 | SUT 1-2F 115 | 20867 | SUT #2 13.8 | 1 | 20035-20867-1 | 142 | 142 | 108.1 | 117.3 | 82.6 | 908 | 142 | 106 | 106 | 74.7 | 130 | -7.9 | 2021 | 2026 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20009 | HARRIS1N 230 | 20865 | HARRIS#122.0 | 1 | 20009-20865-1 | 1120 | 1120 | 922 | 922 | 82.3 | 134 | 1120 | 913.8 | 922.4 | 82.4 | 1187 | 0.1 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 24 | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20024 | ROX 1-4F 230 | 20070 | PERSON 230 | 2 | 20024-20070-2 | 797 | 797 | 410.5 | 639.6 | 82.2 | 2521 | 797 | 355.6 | 589.8 | 73.3 | 43 | -8.9 | 2021 | 2027 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 394 | 20387 | P1-FAY 0 | 20388 | P3-FAYRR | 1 | 20387 | P1-FAY 0 230 | 20389 | P2-FAY E 230 | 1 | 20387-20389-1 | 637 | 637 | 277.1 | 513 | 82.2 | 114 | 637 | 243.3 | 474.7 | 74.6 | 43 | -7.6 | 2021 | 2026 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 592 | 20632 | MARION | 20654 | DILLON T | 1 | 20047 | WSP BUS 115 | 20447 | E10-HOGS 115 | 1 | 20047-20447-1 | 97 | 97 | 29.8 | 79.6 | 82 | 43 | 97 | 32.8 | 80.9 | 83.7 | 43 | 1.7 | 2022 | 2020 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20237 | E9-W ONS 230 | 20515 | WALLACE 230 | 1 | 20237-20515-1 | 478 | 478 | 241.7 | 357.5 | 81.7 | 2070 | 478 | 236.7 | 346.1 | 75.4 | 80 | -6.3 | 2022 | 2026 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 366 | 20348 | RKH | 20361 | WEST END | 1 | 20360 | ELLERBE 230 | 20638 | WDSB T 230 | 1 | 20360-20638-1 | 507 | 507 | 241.7 | 415.3 | 81.7 | 297 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230 | 105 | 6SHADYTW 230 | 2 | 4-105-2 | 478 | 478 | 303.2 | 389.2 | 81.5 | 1793 | 478 | 315.5 | 404.7 | 85.3 | 179 | 3.8 | 2022 | 2020 | -2 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 300.9 | 384.5 | 80.7 | 4.7 | 0.8
BEL1GM | SINGLE 61 | 20030 | LEE 1-3F | 20261 | LEE | 1 | 20030 | LEE 1-3F 115 | 20261 | LEE 115 | 2 | 20030-20261-2 | 239 | 239 | 106.1 | 197.4 | 81.5 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 26 | 20182 | FALLS | 20162 | MILBURNE | 5 | 20145 | NEUSE 115 | 20185 | FALLS 115 | 1 | 20145-20185-1 | 201 | 201 | 122.7 | 156.7 | 81.3 | 1885 | 201 | 111.8 | 139.6 | 71.3 | 49 | -10 | 2022 | 2029 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115 | 20851 | ASHVL #118.0 | 1 | 20800-20851-1 | 235 | 235 | 190.5 | 190.5 | 81.1 | 130 | 235 | 191.6 | 191.6 | 81.6 | 130 | 0.5 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 62 | 20030 | LEE 1-3F | 20261 | LEE | 2 | 20030 | LEE 1-3F 115 | 20261 | LEE 115 | 1 | 20030-20261-1 | 239 | 239 | 96.7 | 196.3 | 81 | 86 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 473 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20499 | E2-MAYVL 230 | 20527 | SWANSBOR 230 | 1 | 20499-20527-1 | 478 | 478 | 258.1 | 367.4 | 80.8 | 2202 | 478 | 236.5 | 333 | 72.5 | 74 | -8.3 | 2022 | 2028 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | DUTCHOVERB | 543 | 6RIVRBEN | 441 | 6LINCOLN | 1 | 441 | 6LINCOLN 230 | 543 | 6RIVRBEN 230 | 2 | 441-543-2 | 597.5 | 597.5 | 288.9 | 490.4 | 80.6 | 88 | 597.5 | 279.4 | 473.4 | 77.9 | 37 | -2.7 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 597.5 | 285.3 | 500.9 | 82.2 | -10.5 | -1.6
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20191 | WENDELL 230 | 20200 | ZEBULON 230 | 1 | 20191-20200-1 | 797 | 797 | 483.6 | 621.5 | 80.6 | 5276 | 797 | 457.7 | 586.7 | 74.3 | 129 | -6.3 | 2022 | 2027 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 843 | 20800 | ASHEVIL | 20804 | SKYLAND | 1 | 20762 | ENKA SW 115 | 20791 | WEST ASH 115 | 1 | 20762-20791-1 | 239 | 239 | 94.7 | 191.7 | 80.6 | 288 | 239 | 88.9 | 182.6 | 76.7 | 43 | -3.9 | 2022 | 2025 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 547 | 20545 | CASTLE H | 20533 | ID/OCC T | 1 | 20515 | WALLACE 230 | 20517 | WALLACE 115 | 1 | 20515-20517-1 | 150 | 150 | 64.2 | 120.7 | 80.5 | 343 | 150 | 59 | 111 | 74 | 43 | -6.5 | 2022 | 2027 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | PINOCAW | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 2 | 539 | 6LAKEWOD 230 | 543 | 6RIVRBEN 230 | 1 | 539-543-1 | 796.7 | 796.7 | 371.6 | 648.5 | 80.4 | 156 | 796.7 | 383.1 | 668.2 | 83.4 | 45 | 3 | 2023 | 2021 | -2 |  | 735 | 796.7 | 735 | PINOCA BLACK | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 340.3 | 594.8 | 74.1 | 53.7 | 6.3
RIV7GM | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230 | 543 | 6RIVRBEN 230 | 2 | 539-543-2 | 796.7 | 796.7 | 371.6 | 648.5 | 80.4 | 156 | 796.7 | 383.1 | 668.2 | 83.4 | 45 | 3 | 2023 | 2021 | -2 |  | 735 | 796.7 | 735 | PINOCA WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 340.3 | 594.8 | 74.1 | 53.7 | 6.3
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20203 | BAILEY T 230 | 20228 | WILSON 230 | 1 | 20203-20228-1 | 637 | 637 | 364.2 | 492.7 | 80.3 | 4922 | 637 | 332.3 | 452.5 | 72.1 | 86 | -8.2 | 2023 | 2028 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 33 | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20044 | ROB 1 F 115 | 20874 | ROB #1 18.0 | 1 | 20044-20874-1 | 244 | 244 | 174.6 | 195.2 | 80 | 173 | 244 | 174.3 | 174.3 | 71.4 | 130 | -8.6 | 2023 | 2029 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20039 | SUT 3 F 230 | 20868 | SUT #3 24.0 | 1 | 20039-20868-1 | 533 | 533 | 424 | 424 | 79.5 | 130 | 533 | 423.5 | 423.5 | 79.5 | 130 | 0 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
LEE3GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 105 | 6SHADYTW 230 | 109 | 6SHADY G 230 | 2 | 105-109-2 | 478 | 478 | 234.9 | 376.8 | 79.4 | 148 | 478 | 242.3 | 388.3 | 82.5 | 44 | 3.1 | 2023 | 2021 | -2 |  | 477.96 | 477.96 | 477.96 | SHADY GROVE | 230 kV Line | 859.9297 | 1008.8939 | 859.9297 | 478 | 214.7 | 346.1 | 73.3 | 30.7 | 6.1
MCG2GM | 3 | 20137 | METHOD | 20153 | TRYON HL | 5 | 20163 | MILBURNE 115 | 20174 | I-PERSTP 115 | 1 | 20163-20174-1 | 119 | 119 | 24.1 | 89.3 | 79.3 | 86 | 119 | 32 | 88.6 | 77.5 | 86 | -1.8 | 2023 | 2024 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20237 | E9-W ONS 230 | 20521 | CATHRNLK 230 | 1 | 20237-20521-1 | 478 | 478 | 230.2 | 343.9 | 79.3 | 1760 | 478 | 225 | 332.9 | 73.1 | 43 | -6.2 | 2023 | 2027 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 362 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20301 | TROY 115 | 20683 | BURNETTE 115 | 1 | 20301-20683-1 | 269 | 269 | 127.9 | 208.6 | 79.3 | 511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | 2W | 20800 | ASHEVIL | 20762 | ENKA SW | 5 | 20791 | WEST ASH 115 | 20793 | BILTMORE 115 | 1 | 20791-20793-1 | 279 | 279 | 58.6 | 218.9 | 79.2 | 86 | 279 | 50.1 | 200.6 | 72.6 | 38 | -6.6 | 2023 | 2028 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 329 | 20309 | BISCOE W | 20332 | ASHEB | 1 | 20290 | I-OLVRRB 115 | 20304 | E14-ULAH 115 | 1 | 20290-20304-1 | 138 | 138 | 49.4 | 107.5 | 79 | 43 | 138 | 44.1 | 97.8 | 71 | 39 | -8 | 2023 | 2029 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 78 | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035 | SUT 1-2F 115 | 20866 | SUT #1 13.8 | 1 | 20035-20866-1 | 142 | 142 | 100.4 | 112 | 78.9 | 988 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 158 | 20089 | HENDERSN | 20105 | FRANKLIN | 1 | 20111 | E18-WK F 115 | 20113 | WF T NC1 115 | 1 | 20111-20113-1 | 170 | 170 | 40.9 | 127.4 | 78.8 | 172 | 170 | 43.6 | 122.8 | 74.9 | 86 | -3.9 | 2024 | 2026 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 845 | 6E.DURHM 230 | 20076 | LEESVILL 230 | 1 | 845-20076-1 | 745 | 745 | 411.1 | 575.1 | 78.5 | 6497 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 234 | 20190 | WAKE | 20191 | WENDELL | 1 | 20079 | OXF S T 230 | 20085 | OXFORD N 230 | 1 | 20079-20085-1 | 539 | 539 | 349.4 | 412.5 | 78.4 | 4470 | 539 | 319.4 | 377.7 | 71.1 | 66 | -7.3 | 2024 | 2029 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 189 | 20137 | METHOD | 20150 | I-NCSU S | 1 | 20149 | MORDECAI 115 | 20168 | YONKERS 115 | 1 | 20149-20168-1 | 190 | 190 | 20.2 | 138.8 | 78.4 | 172 | 190 | 31.1 | 138.8 | 77 | 43 | -1.4 | 2024 | 2025 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20524 | JACKSONV 230 | 20540 | GEI&SW T 230 | 1 | 20524-20540-1 | 478 | 478 | 251.7 | 354.7 | 78.3 | 2510 | 478 | 228.8 | 323.8 | 70.7 | 40 | -7.6 | 2024 | 2029 | 5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115 | 20858 | ASHVCT#118.0 | 1 | 20800-20858-1 | 200 | 200 | 156.5 | 156.5 | 78.3 | 130 | 200 | 156.5 | 156.5 | 78.3 | 130 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115 | 20859 | ASHVCT#218.0 | 1 | 20800-20859-1 | 200 | 200 | 156.5 | 156.5 | 78.3 | 130 | 200 | 156.5 | 156.5 | 78.3 | 130 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20977 | RICH CC118.0 | 1 | 20378-20977-1 | 660 | 660 | 516 | 516 | 78.2 | 95 | 660 | 502.9 | 516 | 78.2 | 730 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 203 | 20162 | MILBURNE | 20163 | MILBURNE | 1 | 20162 | MILBURNE 230 | 20163 | MILBURNE 115 | 2 | 20162-20163-2 | 300 | 300 | 179.5 | 234.2 | 78.1 | 2492 | 300 | 184.6 | 241.2 | 80.4 | 129 | 2.3 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 524 | 20515 | WALLACE | 20551 | E4-BEVRG | 1 | 20280 | BEULAVIL 115 | 20517 | WALLACE 115 | 1 | 20280-20517-1 | 78 | 78 | 44.3 | 60.3 | 78 | 599 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 638 | 20730 | CAMDEN | 43010 | 6LUGOFF | 1 | 20723 | CAMD JCT 115 | 20726 | CAMCTYDB 115 | 1 | 20723-20726-1 | 108 | 108 | 26.5 | 78.6 | 78 | 129 | 108 | 24.8 | 82.3 | 82.2 | 45 | 4.2 | 2024 | 2021 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20053 | CAPE 5&6 115 | 20878 | CAPE #5 13.8 | 1 | 20053-20878-1 | 200 | 200 | 146.4 | 155.9 | 77.9 | 1039 | 200 | 144.2 | 155.4 | 77.7 | 173 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20971 | RICH CT118.0 | 1 | 20378-20971-1 | 220 | 220 | 170.5 | 170.5 | 77.5 | 87 | 220 | 165.1 | 170.5 | 77.5 | 113 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20972 | RICH CT218.0 | 1 | 20378-20972-1 | 220 | 220 | 170.5 | 170.5 | 77.5 | 130 | 220 | 165 | 170.5 | 77.5 | 156 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20973 | RICH CT318.0 | 1 | 20378-20973-1 | 220 | 220 | 170.5 | 170.5 | 77.5 | 130 | 220 | 165.5 | 170.5 | 77.5 | 156 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20974 | RICH CT418.0 | 1 | 20378-20974-1 | 220 | 220 | 170.5 | 170.5 | 77.5 | 87 | 220 | 165.2 | 170.5 | 77.5 | 113 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MTISGM | BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230 | 20975 | RICH CT518.0 | 1 | 20378-20975-1 | 220 | 220 | 170.5 | 170.5 | 77.5 | 87 | 220 | 165.4 | 170.5 | 77.5 | 113 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 638 | 20730 | CAMDEN | 43010 | 6LUGOFF | 1 | 20732 | ELGIN T 115 | 20734 | WATRE 115 | 1 | 20732-20734-1 | 95 | 95 | 24.1 | 71.4 | 77.5 | 130 | 95 | 32.8 | 74.4 | 79.4 | 42 | 1.9 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 808 | 20762 | ENKA SW | 20800 | ASHEVIL | 1 | 20762 | ENKA SW 115 | 20767 | BENT CRK 115 | 1 | 20762-20767-1 | 264 | 264 | 127.8 | 204.3 | 77.4 | 894 | 264 | 119 | 190.9 | 72.3 | 39 | -5.1 | 2024 | 2028 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 377 | 20377 | RICHMOND | 20391 | CUMBERLD | 1 | 20348 | RKH 230 | 20355 | HAMLET 230 | 1 | 20348-20355-1 | 507 | 507 | 275.7 | 395.8 | 77.2 | 2675 | 507 | 252 | 363.7 | 70.4 | 29 | -6.8 | 2025 | 2029 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 17 | 20009 | HARRIS1N | 20204 | DUNCAN | 1 | 20052 | CAPE F F 115 | 20220 | LILINGTN 115 | 1 | 20052-20220-1 | 86 | 86 | 42.1 | 64.2 | 77.1 | 660 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 422 | 20401 | VANDER | 20265 | E15-STED | 1 | 20205 | CLINTON 230 | 20255 | CLINTON 115 | 1 | 20205-20255-1 | 200 | 200 | 70.5 | 154.1 | 77.1 | 43 | 200 | 81.3 | 146.5 | 73.3 | 43 | -3.8 | 2025 | 2027 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 636 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20716 | CAMCTY02 115 | 20729 | STEEPLE 115 | 1 | 20716-20729-1 | 108 | 108 | 43.4 | 82.4 | 77.1 | 89 | 108 | 45.8 | 93.5 | 87.4 | 5 | 10.3 | 2025 | 2018 | -7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 366 | 20348 | RKH | 20361 | WEST END | 1 | 20360 | ELLERBE 230 | 20361 | WEST END 230 | 1 | 20360-20361-1 | 507 | 507 | 216.7 | 391 | 76.9 | 46 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | SINGLE 34 | 20020 | BRUN 2 N | 20515 | WALLACE | 1 | 20520 | I-KOSA 230 | 20534 | I-PRXR W 230 | 1 | 20520-20534-1 | 478 | 478 | 266.3 | 361.2 | 76.8 | 2259 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 22 | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230 | 20097 | CG-ROX 230 | 1 | 20070-20097-1 | 423 | 423 | 239.8 | 326.1 | 76.7 | 4176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20053 | CAPE 5&6 115 | 20879 | CAPE #6 18.0 | 1 | 20053-20879-1 | 233 | 233 | 178.4 | 178.4 | 76.6 | 130 | 233 | 174.5 | 174.5 | 74.9 | 130 | -1.7 | 2025 | 2026 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | SINGLE 368 | 20348 | RKH | 20378 | RICHMOND | 2 | 20348 | RKH 230 | 20378 | RICHMOND 230 | 1 | 20348-20378-1 | 1014 | 1014 | 444.9 | 789 | 76.3 | 165 | 1014 | 436.1 | 772.5 | 74.6 | 43 | -1.7 | 2025 | 2026 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | 3 | 20137 | METHOD | 20153 | TRYON HL | 5 | 20152 | GARNER 115 | 20174 | I-PERSTP 115 | 1 | 20152-20174-1 | 119 | 119 | 20.7 | 85.3 | 76.2 | 86 | 119 | 28.4 | 85.4 | 75.1 | 86 | -1.1 | 2025 | 2026 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 530 | 20524 | JACKSONV | 20519 | M-TARAWA | 1 | 20471 | CCWDCG T 230 | 20528 | RHEMS 230 | 1 | 20471-20528-1 | 557 | 557 | 216.3 | 400.3 | 76.2 | 86 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | SINGLE 377 | 20377 | RICHMOND | 20391 | CUMBERLD | 1 | 20378 | RICHMOND 230 | 20415 | RAEFORD 230 | 1 | 20378-20415-1 | 797 | 797 | 427.2 | 593.4 | 76.1 | 3530 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | BASE CASE | 0 |  | 0 |  |  | 112 | 8BAD CRK 500 | 113 | 8JOCASSE 500 | 1 | 112-113-1 | 1732 | 1732 | 1396.6 | 1396.6 | 75.8 | 129 | 1732 | 1396.6 | 1396.6 | 75.8 | 84 | 0 | 2025 | 2025 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | 1397.7 | 1397.7 | 73 | -1.1 | 2.8
BEL1GM | SINGLE 256 | 20205 | CLINTON | 20255 | CLINTON | 1 | 20260 | ROSEBORO 115 | 20265 | E15-STED 115 | 1 | 20260-20265-1 | 163 | 163 | 100.6 | 119.6 | 75.7 | 1934 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 538 | 6HARRISB 230 | 540 | 6MCGUIRE 230 | 1 | 538-540-1 | 490.8 | 490.8 | 327.9 | 370.1 | 75.6 | 2210 | 490.8 | 319.1 | 354 | 72.4 | 41 | -3.2 | 2026 | 2028 | 2 |  | 490.8 | 563.7 | 540.2 | CRAIGHEAD BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20086 | E12-HYCO 115 | 20093 | CONCORD 115 | 1 | 20086-20093-1 | 236 | 236 | 115.2 | 179.8 | 75.5 | 609 | 236 | 110.7 | 170.2 | 71.3 | 43 | -4.2 | 2026 | 2029 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI5GM | 2W | 20800 | ASHEVIL | 20762 | ENKA SW | 5 | 209 | 3MILLSRV 115 | 20800 | ASHEVIL 115 | 1 | 209-20800-1 | 207 | 207 | 122.9 | 157.4 | 75.3 | 1345 | 207 | 132.6 | 164.6 | 79.4 | 98 | 4.1 | 2026 | 2023 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 634 | 20725 | CAMDEN | 20716 | CAMCTY02 | 1 | 20731 | I-DUP CA 115 | 20732 | ELGIN T 115 | 1 | 20731-20732-1 | 95 | 95 | 29.8 | 70.7 | 75.2 | 121 | 95 | 43.5 | 86.2 | 91.6 | 5 | 16.4 | 2026 | 2016 | -10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230 | 20124 | METHOD 230 | 1 | 20073-20124-1 | 637 | 637 | 305.8 | 470.2 | 75.1 | 1505 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OXFDGM | SINGLE 34 | 20020 | BRUN 2 N | 20515 | WALLACE | 1 | 20515 | WALLACE 230 | 20516 | I-BASF 230 | 1 | 20515-20516-1 | 478 | 478 | 252.8 | 344.9 | 75 | 2009 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | KIMBRELLB | 331 | 6ALLEN | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230 | 544 | 6WINECOF 230 | 1 | 443-544-1 | 478 | 478 | 321.8 | 364.3 | 74.9 | 1596 | 478 | 325.4 | 368.9 | 76.3 | 208 | 1.4 | 2026 | 2025 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 342.8 | 70 | 21.5 | 4.9
OCO3GM | SINGLE 216 | 20177 | SELMA | 20192 | SELMA | 1 | 20163 | MILBURNE 115 | 20170 | CLAYTON 115 | 1 | 20163-20170-1 | 201 | 201 | 83.8 | 144.3 | 74.8 | 257 | 201 | 53.7 | 132.2 | 70.7 | 43 | -4.1 | 2026 | 2029 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20619 | MASONBOR 230 | 20626 | WRIGHTVL 230 | 1 | 20619-20626-1 | 637 | 637 | 334.9 | 476.1 | 74.8 | 1737 | 637 | 323.9 | 456.1 | 72.4 | 128 | -2.4 | 2026 | 2028 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 37 | 20020 | BRUN 2 N | 20615 | BARNARD | 1 | 20020 | BRUN 2 N 230 | 20515 | WALLACE 230 | 1 | 20020-20515-1 | 478 | 478 | 250.3 | 352.4 | 74.7 | 2008 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 234 | 20190 | WAKE | 20191 | WENDELL | 1 | 20163 | MILBURNE 115 | 20164 | KNIGHTDL 115 | 1 | 20163-20164-1 | 271 | 271 | 70.3 | 191 | 74.5 | 86 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 221 | 20182 | FALLS | 20185 | FALLS | 1 | 20162 | MILBURNE 230 | 20182 | FALLS 230 | 1 | 20162-20182-1 | 423 | 423 | 211.4 | 312.1 | 74.4 | 2880 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 653 | 337 | 8NEWPORT | 546 | 8MCGUIRE | 1 | 8 | 8OCONEE 500 | 5004 | 8KATRTRT 500 | 1 | 8-5004-1 | 1666.2 | 1666.2 | 1178.2 | 1304.8 | 74.2 | 506 | 1666.2 | 1125.7 | 1234.1 | 70.2 | 1 | -4 | 2027 | 2029 | 2 |  | 1666.184 | 2218.692 | 1790.888 | KATOMA | 500 kV Line | 995.9 | 1101.552 | 995.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 653 | 337 | 8NEWPORT | 546 | 8MCGUIRE | 1 | 113 | 8JOCASSE 500 | 5004 | 8KATRTRT 500 | 1 | 113-5004-1 | 1666.2 | 1666.2 | 1178.2 | 1304.8 | 74.2 | 502 | 1666.2 | 1125.7 | 1234.1 | 70.2 | 1 | -4 | 2027 | 2029 | 2 |  | 1666.184 | 2218.692 | 1790.888 | KATOMA | 500 kV Line | 995.9 | 1101.552 | 995.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | HODGBK1SHORT | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115 | 22 | CLARK HL 100 | 4 | 1-22-4 | 96 | 96 | 59.7 | 71.1 | 74.1 | 638 | 96 | 69 | 80.4 | 83.8 | 350 | 9.7 | 2027 | 2020 | -7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | 1.9 | 2
OCO3GM | SINGLE 362 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20301 | TROY 115 | 20428 | BISCOE W 115 | 1 | 20301-20428-1 | 269 | 269 | 114.4 | 194.7 | 74.1 | 257 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20521 | CATHRNLK 230 | 20524 | JACKSONV 230 | 1 | 20521-20524-1 | 478 | 478 | 205.7 | 318.8 | 73.7 | 398 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 96 | 20044 | ROB 1 F | 20721 | BETHNE T | 1 | 20725 | CAMDEN 115 | 20730 | CAMDEN 230 | 1 | 20725-20730-1 | 200 | 200 | 123.6 | 147 | 73.5 | 277 | 200 | 140 | 176.3 | 88.1 | 12 | 14.6 | 2027 | 2018 | -9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL5GM | PEACOCKB | 332 | 6CATAWBA | 334 | 6PEACOCK | 1 | 332 | 6CATAWBA 230 | 334 | 6PEACOCK 230 | 2 | 332-334-2 | 655.2 | 655.2 | 289.6 | 475.3 | 73.4 | 711 | 655.2 | 305.5 | 501 | 77.8 | 45 | 4.4 | 2027 | 2024 | -3 |  | 553.637 | 655.2035 | 553.637 | PEACOCK | 230 kV Line | 1151.8836 | 1436.2698 | 1151.8836 | 655.2 | 290.6 | 476.9 | 73.8 | -1.6 | -0.4
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20086 | E12-HYCO 115 | 20092 | ROXBORO 115 | 1 | 20086-20092-1 | 237 | 237 | 109.7 | 173 | 73.3 | 361 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 335 | 20312 | ASHEB E | 20331 | ASHEB | 1 | 20319 | ASHEB N 115 | 20331 | ASHEB 115 | 1 | 20319-20331-1 | 201 | 201 | 68.3 | 146.8 | 73.3 | 86 | 201 | 70.4 | 150.9 | 74.7 | 43 | 1.4 | 2027 | 2026 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 234 | 20190 | WAKE | 20191 | WENDELL | 1 | 20084 | I-NOVO 115 | 20105 | FRANKLIN 115 | 1 | 20084-20105-1 | 201 | 201 | 99.9 | 138.3 | 73.2 | 923 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 382 | 20378 | RICHMOND | 20415 | RAEFORD | 1 | 20047 | WSP BUS 115 | 20432 | PA-LMB#2 115 | 1 | 20047-20432-1 | 133 | 133 | 61.3 | 95.1 | 73.1 | 644 | 133 | 65.5 | 95.8 | 72.8 | 86 | -0.3 | 2027 | 2028 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 6 | 20004 | TIL 1-4H | 20302 | E14-TROY | 1 | 20347 | ABRDN RD 230 | 20348 | RKH 230 | 1 | 20347-20348-1 | 539 | 539 | 336.3 | 398.9 | 73.1 | 3765 | 539 | 329.7 | 415.7 | 75.6 | 164 | 2.5 | 2027 | 2026 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20550 | CSTL HYN 230 | 20622 | OGDEN 230 | 1 | 20550-20622-1 | 478 | 478 | 212.1 | 347.6 | 73 | 285 | 478 | 201 | 338.5 | 71.3 | 43 | -1.7 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | BASE CASE | 0 |  | 0 |  |  | 20001 | BLEWETT 115 | 20894 | BLEWDUM 4.40 | 1 | 20001-20894-1 | 33 | 33 | 24.1 | 24.1 | 72.9 | 130 | 33 | 24.1 | 24.1 | 72.9 | 130 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 473 | 20465 | NEW BERN | 20471 | CCWDCG T | 1 | 20484 | HAVELOCK 230 | 20499 | E2-MAYVL 230 | 1 | 20484-20499-1 | 478 | 478 | 224.2 | 332.4 | 72.9 | 955 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | KIMBRELLB | 331 | 6ALLEN | 544 | 6WINECOF | 1 | 331 | 6ALLEN 230 | 544 | 6WINECOF 230 | 2 | 331-544-2 | 473.3 | 473.3 | 277.8 | 348 | 72.8 | 1801 | 473.3 | 284.6 | 356.3 | 74.7 | 12 | 1.9 | 2028 | 2026 | -2 |  | 458.1 | 473.3 | 458.1 | KIMBRELL | 230 kV Line | 458.114 | 473.2517 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | 30 | 20124 | METHOD | 20119 | PRISON F | 5 | 20091 | BRIERCK 230 | 20117 | DURHAM 230 | 1 | 20091-20117-1 | 539 | 539 | 242 | 387 | 72.7 | 714 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 548 | 20545 | CASTLE H | 20544 | HOLLY RG | 1 | 20530 | JACKSNVL 115 | 20535 | NORTHWDS 115 | 1 | 20530-20535-1 | 221 | 221 | 87.1 | 151.6 | 72.7 | 129 | 221 | 90.6 | 160.5 | 74 | 86 | 1.3 | 2028 | 2027 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | 36 | 20182 | FALLS | 20024 | ROX 1-4F | 5 | 20077 | SIX FORK 230 | 20078 | WD VALLY 230 | 1 | 20077-20078-1 | 541 | 541 | 220.5 | 382.5 | 72.6 | 261 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 316 | 20261 | LEE | 20284 | WEIL | 1 | 20030 | LEE 1-3F 115 | 20283 | NEW HOPE 115 | 1 | 20030-20283-1 | 201 | 201 | 96.6 | 146.9 | 72.2 | 563 | 201 | 101.1 | 153.4 | 74.4 | 43 | 2.2 | 2028 | 2026 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 841 | 6BOBWH B 230 | 848 | 6PL GRDN 230 | 1 | 841-848-1 | 478 | 478 | 163.8 | 341.8 | 72.1 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 842 | 6BOBWH W 230 | 848 | 6PL GRDN 230 | 2 | 842-848-2 | 478 | 478 | 163.3 | 341.6 | 72.1 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 848 | 6PL GRDN 230 | 850 | 8PL GRDN 500 | 5 | 848-850-5 | 1680 | 1680 | 589.5 | 1210.2 | 72 | 263 | 1680 | 885.4 | 1398.3 | 83.2 | 43 | 11.2 | 2028 | 2021 | -7 |  | 1680 | 1680 | 1680 | PLEASANT GARDEN TIE 05 | 500/230 kV Transformer | 1680 | 1680 | 1680 | 1680 | 725.6 | 1187.3 | 70.7 | 22.9 | 1.3
MCG2GM | SINGLE 540 | 20530 | JACKSNVL | 20535 | NORTHWDS | 1 | 20504 | E9-N JAX 115 | 20530 | JACKSNVL 115 | 1 | 20504-20530-1 | 220 | 220 | 71.8 | 154.4 | 72 | 172 | 220 | 74.2 | 159.5 | 73.1 | 43 | 1.1 | 2028 | 2027 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 239 | 20192 | SELMA | 20251 | LEE | 1 | 20177 | SELMA 115 | 20192 | SELMA 230 | 1 | 20177-20192-1 | 300 | 300 | 150.5 | 215.6 | 71.9 | 852 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 422 | 20401 | VANDER | 20265 | E15-STED | 1 | 20255 | CLINTON 115 | 20257 | E15-CLNT 115 | 1 | 20255-20257-1 | 163 | 163 | 15.1 | 112 | 71.8 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 377 | 20377 | RICHMOND | 20391 | CUMBERLD | 1 | 20355 | HAMLET 230 | 20387 | P1-FAY 0 230 | 1 | 20355-20387-1 | 507 | 507 | 242.5 | 356.7 | 71.8 | 879 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 102 | 20047 | WSP BUS | 115 | ROB #1 | 1 | 20411 | RAEFORD 115 | 20425 | RED SP T 115 | 1 | 20411-20425-1 | 133 | 133 | 29.9 | 91.5 | 71.8 | 176 | 133 | 26.1 | 91.4 | 70.9 | 43 | -0.9 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | SINGLE 377 | 20377 | RICHMOND | 20391 | CUMBERLD | 1 | 20314 | E3-CTRCH 230 | 20361 | WEST END 230 | 1 | 20314-20361-1 | 507 | 507 | 265.1 | 362.1 | 71.3 | 3496 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | BASE CASE | 0 |  | 0 |  |  | 20369 | FAY E 69.0 | 20948 | FAYPWC9 13.8 | 1 | 20369-20948-1 | 94 | 94 | 66.9 | 66.9 | 71.2 | 130 | 94 | 66.9 | 66.9 | 71.2 | 130 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WYLIGM | SINGLE 503 | 20497 | MR WILDW | 20498 | MR WILDW | 1 | 20484 | HAVELOCK 230 | 20485 | HAVELOCK 115 | 1 | 20484-20485-1 | 200 | 200 | 80.6 | 142.5 | 71.2 | 129 | 200 | 79.7 | 141.5 | 70.8 | 86 | -0.4 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
THTCGM | SINGLE 494 | 20484 | HAVELOCK | 20497 | MR WILDW | 1 | 20484 | HAVELOCK 230 | 20485 | HAVELOCK 115 | 2 | 20484-20485-2 | 200 | 200 | 80.6 | 142.4 | 71.2 | 129 | 200 | 79.7 | 141.5 | 70.8 | 86 | -0.4 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 805 | 20762 | ENKA SW | 20761 | I-SE CNT | 1 | 20790 | VANDERBT 115 | 20791 | WEST ASH 115 | 1 | 20790-20791-1 | 123 | 123 | 56.4 | 87.7 | 71.2 | 456 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115 | 20890 | TILL #3 13.8 | 1 | 20004-20890-1 | 31 | 31 | 22.1 | 22.1 | 71.1 | 130 | 31 | 22 | 22 | 71 | 130 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115 | 20891 | TILL #4 13.8 | 1 | 20004-20891-1 | 31 | 31 | 22.1 | 22.1 | 71.1 | 130 | 31 | 22 | 22 | 71 | 130 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230 | 20076 | LEESVILL 230 | 1 | 20073-20076-1 | 745 | 745 | 356.6 | 520.8 | 71.1 | 1360 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLIFGM | 20 | 20070 | PERSON | 20068 | RXBOWMAN | 5 | 20090 | E12-ROX 115 | 20092 | ROXBORO 115 | 1 | 20090-20092-1 | 190 | 190 | 71.1 | 134.1 | 71.1 | 172 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 653 | 337 | 8NEWPORT | 546 | 8MCGUIRE | 1 | 332 | 6CATAWBA 230 | 333 | 6NEWPORT 230 | 3 | 332-333-3 | 459.7 | 459.7 | 276.6 | 329.6 | 71 | 933 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | 459.7 | 617.5 | 495.6 | ALLISON CRK | 230 kV Line | 556.9 | 617.4 | 556.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO3GM | SINGLE 653 | 337 | 8NEWPORT | 546 | 8MCGUIRE | 1 | 332 | 6CATAWBA 230 | 333 | 6NEWPORT 230 | 4 | 332-333-4 | 459.7 | 459.7 | 276.6 | 329.6 | 71 | 975 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | 459.7 | 617.5 | 495.6 | ALLISON CRK | 230 kV Line | 556.9 | 617.4 | 556.9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 329 | 20309 | BISCOE W | 20332 | ASHEB | 1 | 20294 | BISCOSUB 115 | 20428 | BISCOE W 115 | 1 | 20294-20428-1 | 239 | 239 | 108.2 | 168 | 71 | 258 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20543 | E9-FOLKS 115 | 20546 | E9-TOPSL 115 | 1 | 20543-20546-1 | 185 | 185 | 83.7 | 121.4 | 71 | 590 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 561 | 20568 | DELCO | 20563 | LELANIND | 1 | 20035 | SUT 1-2F 115 | 20560 | IND OOB5 115 | 1 | 20035-20560-1 | 159 | 159 | 55.7 | 114.1 | 70.9 | 43 | 159 | 57.8 | 114.9 | 71.5 | 43 | 0.6 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 382 | 20378 | RICHMOND | 20415 | RAEFORD | 1 | 20419 | WAGRAMSW 115 | 20421 | LAURINBG 115 | 1 | 20419-20421-1 | 201 | 201 | 81.2 | 139 | 70.9 | 75 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 40 | 20022 | BRUN 1 N | 20354 | I-ROCKY | 1 | 20622 | OGDEN 230 | 20626 | WRIGHTVL 230 | 1 | 20622-20626-1 | 557 | 557 | 255.8 | 393.5 | 70.9 | 288 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
RIV7GM | SINGLE 414 | 20392 | FAY | 20401 | VANDER | 1 | 20392 | FAY 115 | 20402 | E15-VAND 115 | 1 | 20392-20402-1 | 201 | 201 | 82.9 | 142.3 | 70.8 | 43 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | JOCASSE_XFMR | 113 | 8JOCASSE | 106 | 6JOCASSE | 1 | 236 | 6PEACH V 230 | 265 | 6RIVERVW 230 | 1 | 236-265-1 | 409 | 409 | 281.6 | 293.9 | 70.7 | 1436 | 409 | 283.3 | 295.4 | 71.4 | 5 | 0.7 | 2029 | 2029 | 0 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 409 | 277.8 | 289.4 | 70.6 | 4.5 | 0.1
CLI5GM | DACUSB | 7 | 6OCONEE | 107 | 6N GRNVL | 1 | 7 | 6OCONEE 230 | 107 | 6N GRNVL 230 | 2 | 7-107-2 | 478 | 478 | 289.6 | 337.6 | 70.6 | 981 | 478 | 300.4 | 350 | 73.7 | 26 | 3.1 | 2029 | 2027 | -2 |  | 459.7 | 477.96 | 477.96 | DACUS | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 286.7 | 334.3 | 70.1 | 3.3 | 0.5
CLI5GM | SADLERB | 826 | 6ERNEST2 | 718 | 6SADLER | 1 | 718 | 6SADLER 230 | 826 | 6ERNEST2 230 | 2 | 718-826-2 | 717 | 717 | 292.8 | 516.8 | 70.6 | 52 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | 576 | 717 | 576 | SADLER | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 554 | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20022 | BRUN 1 N 230 | 20354 | I-ROCKY 230 | 1 | 20022-20354-1 | 590 | 590 | 323.5 | 383.1 | 70.5 | 1537 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 73 | 20035 | SUT 1-2F | 20545 | CASTLE H | 2 | 20035 | SUT 1-2F 115 | 20545 | CASTLE H 115 | 1 | 20035-20545-1 | 159 | 159 | 69 | 111.3 | 70.4 | 231 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BAD1GM | SINGLE 471 | 20465 | NEW BERN | 20466 | NEW BERN | 1 | 20465 | NEW BERN 230 | 20466 | NEW BERN 115 | 2 | 20465-20466-2 | 200 | 200 | 82.4 | 140.7 | 70.4 | 86 | 200 | 83.7 | 143.2 | 71.6 | 43 | 1.2 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OXFDGM | GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 331 | 6ALLEN 230 | 544 | 6WINECOF 230 | 1 | 331-544-1 | 473.3 | 473.3 | 265.3 | 334.9 | 70.3 | 1757 | 473.3 | 284.6 | 350.9 | 73.9 | 4 | 3.6 | 2029 | 2027 | -2 |  | 458.1 | 473.3 | 458.1 | KIMBRELL | 230 kV Line | 458.114 | 473.2517 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | SINGLE 592 | 20632 | MARION | 20654 | DILLON T | 1 | 20447 | E10-HOGS 115 | 20448 | FAIRMONT 115 | 1 | 20447-20448-1 | 97 | 97 | 19 | 68 | 70.3 | 43 | 97 | 21 | 67.8 | 71.1 | 43 | 0.8 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 636 | 20725 | CAMDEN | 20731 | I-DUP CA | 1 | 20724 | CAMCTY01 115 | 20729 | STEEPLE 115 | 1 | 20724-20729-1 | 108 | 108 | 36.4 | 74.9 | 70.3 | 10 | 108 | 38.7 | 85.9 | 80.7 | 1 | 10.4 | 2029 | 2022 | -7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 686 | 416 | WATEREE | 375 | GT FALL1 | 2 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 1 | 375-416-1 | 58.5 | 58.5 | 29.4 | 42 | 70.2 | 136 | 58.5 | 46.6 | 70.9 | 113.3 | 161 | 43.1 | 2029 | 2011 | -18 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 685 | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100 | 416 | WATEREE 100 | 2 | 375-416-2 | 58.5 | 58.5 | 29.4 | 42 | 70.2 | 145 | 58.5 | 46.6 | 70.9 | 113.3 | 204 | 43.1 | 2029 | 2011 | -18 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | SINGLE 376 | 20377 | RICHMOND | 337 | 8NEWPORT | 1 | 538 | 6HARRISB 230 | 540 | 6MCGUIRE 230 | 2 | 538-540-2 | 529.8 | 529.8 | 327.9 | 370.1 | 70 | 2035 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2030 | #N/A | #N/A |  | 529.8 | 625.8 | 553.7 | CRAIGHEAD WH | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | SINGLE 362 | 20348 | RKH | 20347 | ABRDN RD | 1 | 20001 | BLEWETT 115 | 20004 | TIL 1-4H 115 | 1 | 20001-20004-1 | 118 | 118 | 49.8 | 85.6 | 70 | 123 | 118 | 60 | 95 | 77.4 | 81 | 7.4 | 2030 | 2024 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
WATRGM | SINGLE 472 | 20465 | NEW BERN | 20466 | NEW BERN | 2 | 20465 | NEW BERN 230 | 20466 | NEW BERN 115 | 1 | 20465-20466-1 | 200 | 200 | 80.9 | 140 | 70 | 86 | 200 | 82.3 | 142.5 | 71.3 | 43 | 1.3 | 2030 | 2029 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Duke1200MWtoCPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Duke1200MWtoCPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Duke1200MWtoCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening
[25 empty] | 7 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Duke1200MWtoCPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | - | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1773.8 | 93.1 | 176 | 1904.3 | - | 1623 | 85.2 | 176 | -7.9 | 2015 | 2020 | 5 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1369 | 71.9 | 404.8 | 21.2
BEL1GM | - | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.2 | 93 | 176 | 40 | - | 36.7 | 91.8 | 176 | -1.2 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 87.2 | 91.8 | 176 | 95 | - | 86.3 | 90.8 | 176 | -1 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1235.3 | 91.5 | 176 | 1350 | - | 998.1 | 73.9 | 160 | -17.6 | 2016 | 2027 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 972.7 | 91.2 | 176 | 1067 | - | 955.1 | 89.5 | 176 | -1.7 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 295.8 | 91 | 176 | 325 | - | 286.6 | 88.2 | 176 | -2.8 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 969.3 | 90.8 | 176 | 1067 | - | 952.9 | 89.3 | 176 | -1.5 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 99.5 | 89.6 | 176 | 111 | - | 80 | 72.1 | 176 | -17.5 | 2017 | 2028 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 313.4 | 89.6 | 88 | 350 | - | 309.9 | 88.5 | 88 | -1.1 | 2017 | 2018 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 341.6 | 87.6 | 88 | 390 | - | 338.1 | 86.7 | 88 | -0.9 | 2018 | 2019 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1110 | 1110 | - | 964.3 | 86.9 | 88 | 1110 | - | 954.1 | 86 | 26 | -0.9 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 53.6 | 86.4 | 176 | 62 | - | 53 | 85.5 | 176 | -0.9 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 53.6 | 86.4 | 176 | 62 | - | 53 | 85.5 | 176 | -0.9 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 89.9 | 84.8 | 176 | 106 | - | 77 | 72.6 | 176 | -12.2 | 2020 | 2028 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714-827-1 | 576 | 576 | - | 477.2 | 82.9 | 16 | 576 | - | 477 | 82.8 | 2 | -0.1 | 2021 | 2021 | 0 |  | 576 | 621.4 | 576 | JACOBS | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | 576 | - | 470.4 | 81.7 | 6.8 | 1.2
BEL1GM | - | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 276.2 | 82.9 | 176 | 333 | - | 256.1 | 76.9 | 176 | -6 | 2021 | 2025 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 926 | 82.7 | 176 | 1120 | - | 916.7 | 81.9 | 176 | -0.8 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20329 | RAMSEUR | 20330 | I-RAMTEX | 1 | 20329-20330-1 | 19 | 19 | - | 15.7 | 82.7 | 176 | 19 | - | 15.5 | 81.8 | 176 | -0.9 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 722.7 | 82.3 | 176 | 878 | - | 720.5 | 82.1 | 176 | -0.2 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192.4 | 81.9 | 176 | 235 | - | 192.2 | 81.8 | 176 | -0.1 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 718.1 | 81.3 | 176 | 883 | - | 693.7 | 78.6 | 176 | -2.7 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 744.2 | 81.2 | 176 | 917 | - | 739.4 | 80.6 | 176 | -0.6 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 716.2 | 81.1 | 176 | 883 | - | 694.6 | 78.7 | 176 | -2.4 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 388.7 | 80.5 | 176 | 483 | - | 375.8 | 77.8 | 176 | -2.7 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 187.9 | 80 | 176 | 235 | - | 187.3 | 79.7 | 176 | -0.3 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG1GM | - | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 436.9 | 436.9 | - | 349.3 | 79.9 | 176 | 436.9 | - | 349.7 | 80 | 172 | 0.1 | 2023 | 2023 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 436.9 | - | 338.4 | 77.5 | 10.9 | 2.4
BEL1GM | - | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 422.5 | 79.3 | 176 | 533 | - | 415.1 | 77.9 | 176 | -1.4 | 2023 | 2024 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 651.2 | 79.2 | 176 | 822 | - | 646.7 | 78.7 | 176 | -0.5 | 2023 | 2024 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.1 | 77.6 | 176 | 200 | - | 154.9 | 77.5 | 176 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | - | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.1 | 77.6 | 176 | 200 | - | 154.9 | 77.5 | 176 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 112 | 8BAD CRK | 113 | 8JOCASSE | 1 | 112-113-1 | 1732 | 1732 | - | 1312.4 | 75.8 | 86 | 1732 | - | 1313.4 | 75.8 | 84 | 0 | 2025 | 2025 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1732 | - | 1305.1 | 75.4 | 7.3 | 0.4
MCG2GM | - | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 360.5 | 75.4 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | - | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 360.5 | 75.4 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20265 | E15-STED | 20401 | VANDER | 1 | 20265-20401-1 | 163 | 163 | - | 121.1 | 74.3 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035-20867-1 | 142 | 142 | - | 104.7 | 73.7 | 176 | 142 | - | 103.8 | 73.1 | 176 | -0.6 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20053 | CAPE 5&6 | 20879 | CAPE #6 | 1 | 20053-20879-1 | 233 | 233 | - | 171.7 | 73.7 | 176 | 233 | - | 169.8 | 72.9 | 176 | -0.8 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20001 | BLEWETT | 20894 | BLEWDUM | 1 | 20001-20894-1 | 33 | 33 | - | 24.2 | 73.4 | 176 | 33 | - | 24.1 | 73.1 | 176 | -0.3 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | - | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 22.7 | 73.4 | 176 | 31 | - | 22.7 | 73.3 | 176 | -0.1 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | - | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 22.7 | 73.4 | 176 | 31 | - | 22.7 | 73.3 | 176 | -0.1 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BDCKGM | - | - | - | - | - | - | 20182 | FALLS | 20185 | FALLS | 1 | 20182-20185-1 | 300 | 300 | - | 218.8 | 72.9 | 88 | 300 | - | 214.7 | 71.6 | 88 | -1.3 | 2027 | 2028 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20977 | RICH CC1 | 1 | 20378-20977-1 | 660 | 660 | - | 480 | 72.7 | 176 | 660 | - | 469.7 | 71.2 | 176 | -1.5 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20519 | M-TARAWA | 20524 | JACKSONV | 1 | 20519-20524-1 | 478 | 478 | - | 347.7 | 72.7 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BDCKGM | - | - | - | - | - | - | 20070 | PERSON | 20079 | OXF S T | 1 | 20070-20079-1 | 539 | 539 | - | 388.4 | 72.1 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20971 | RICH CT1 | 1 | 20378-20971-1 | 220 | 220 | - | 158.6 | 72.1 | 176 | 220 | - | 154.8 | 70.4 | 168 | -1.7 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20972 | RICH CT2 | 1 | 20378-20972-1 | 220 | 220 | - | 158.6 | 72.1 | 176 | 220 | - | 154.8 | 70.4 | 168 | -1.7 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20973 | RICH CT3 | 1 | 20378-20973-1 | 220 | 220 | - | 158.6 | 72.1 | 176 | 220 | - | 154.8 | 70.4 | 168 | -1.7 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20974 | RICH CT4 | 1 | 20378-20974-1 | 220 | 220 | - | 158.6 | 72.1 | 176 | 220 | - | 154.8 | 70.4 | 168 | -1.7 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20378 | RICHMOND | 20975 | RICH CT5 | 1 | 20378-20975-1 | 220 | 220 | - | 158.6 | 72.1 | 176 | 220 | - | 154.8 | 70.4 | 168 | -1.7 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20369 | FAY E | 20948 | FAYPWC9 | 1 | 20369-20948-1 | 94 | 94 | - | 66.9 | 71.1 | 176 | 94 | - | 65.9 | 70.1 | 164 | -1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20053 | CAPE 5&6 | 20878 | CAPE #5 | 1 | 20053-20878-1 | 200 | 200 | - | 141.9 | 70.9 | 176 | 200 | - | 140.2 | 70.1 | 176 | -0.8 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | - | - | - | - | - | - | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20550-20564-1 | 478 | 478 | - | 335.8 | 70.2 | 88 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 21.7 | 70 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2030 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
99ISGM | - | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 21.7 | 70 | 176 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2030 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Duke1200MWtoCPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Duke1200MWtoCPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Duke1200MWtoCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 8 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 8 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Duke1200MWtoCPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1961.4 | 103 | 910 | 1904.3 | - | 1804.3 | 94.8 | 910 | -8.2 | 2011 | 2014 | 3 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 420.3 | 22.1
DAN3GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.6 | 93.3 | 910 | 95 | - | 87.7 | 92.3 | 910 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 994.3 | 93.2 | 910 | 1067 | - | 976.7 | 91.5 | 910 | -1.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 990.8 | 92.9 | 910 | 1067 | - | 973.3 | 91.2 | 910 | -1.7 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1233.3 | 91.4 | 910 | 1350 | - | 996.1 | 73.8 | 910 | -17.6 | 2016 | 2027 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 355.6 | 91.2 | 455 | 390 | - | 345.2 | 88.5 | 455 | -2.7 | 2016 | 2018 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 100.6 | 90.7 | 910 | 111 | - | 81.3 | 73.3 | 910 | -17.4 | 2016 | 2027 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MAR3GM | MAR4 | - | - | - | - | - | 443 | 6MARSHAL | 540 | 6MCGUIRE | 1 | 443-540-1 | 478 | 478 | - | 420.1 | 87.9 | 216 | 478 | - | 464 | 97.1 | 232 | 9.2 | 2018 | 2013 | -5 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | - | 380.4 | 79.6 | 39.7 | 8.3
BUC5GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 54.5 | 87.9 | 910 | 62 | - | 53.9 | 87 | 910 | -0.9 | 2018 | 2019 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 54.5 | 87.9 | 910 | 62 | - | 53.9 | 87 | 910 | -0.9 | 2018 | 2019 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 91.1 | 85.9 | 910 | 106 | - | 78.2 | 73.8 | 910 | -12.1 | 2019 | 2027 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714-827-1 | 576 | 576 | - | 487.5 | 84.6 | 165 | 576 | - | 482.8 | 83.8 | 21 | -0.8 | 2020 | 2020 | 0 |  | 576 | 621.4 | 576 | JACOBS | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | 576 | - | 471 | 81.8 | 16.5 | 2.8
BEL1GM | BEL2 | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 945.5 | 84.4 | 910 | 1120 | - | 931.4 | 83.2 | 910 | -1.2 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 739.3 | 84.2 | 910 | 878 | - | 732.4 | 83.4 | 910 | -0.8 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 743.8 | 84.2 | 910 | 883 | - | 714.9 | 81 | 910 | -3.2 | 2020 | 2022 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 280.5 | 84.2 | 910 | 333 | - | 260.1 | 78.1 | 910 | -6.1 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 737.9 | 83.6 | 910 | 883 | - | 715.4 | 81 | 910 | -2.6 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 443 | 6MARSHAL | 713 | 6BECKRDT | 1 | 443-713-1 | 437 | 437 | - | 362.5 | 83 | 1608 | 437 | - | 345.8 | 79.1 | 1624 | -3.9 | 2021 | 2023 | 2 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 306.2 | 70.1 | 56.3 | 12.9
BEL1GM | BEL2 | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 759.6 | 82.8 | 910 | 917 | - | 749.7 | 81.8 | 910 | -1 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 398.6 | 82.5 | 910 | 483 | - | 387.1 | 80.2 | 910 | -2.3 | 2021 | 2023 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 675.5 | 82.2 | 910 | 822 | - | 667.9 | 81.3 | 910 | -0.9 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | CLIF | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192.6 | 82 | 910 | 235 | - | 192.2 | 81.8 | 910 | -0.2 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BUC5GM | BEL1 | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 431.1 | 80.9 | 910 | 533 | - | 423.6 | 79.5 | 910 | -1.4 | 2022 | 2023 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | NANT | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 188 | 80 | 910 | 235 | - | 187.4 | 79.8 | 910 | -0.2 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | MCG1 | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 458 | 458 | - | 358.9 | 78.4 | 910 | 458 | - | 361.3 | 78.9 | 910 | 0.5 | 2024 | 2023 | -1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 458 | - | 347.6 | 75.9 | 11.3 | 2.5
ALL4GM | OCO1 | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.2 | 77.6 | 910 | 200 | - | 154.9 | 77.5 | 910 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | OCO1 | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.2 | 77.6 | 910 | 200 | - | 154.9 | 77.5 | 910 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CLI3GM | BEL1 | - | - | - | - | - | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035-20867-1 | 142 | 142 | - | 108 | 76.1 | 910 | 142 | - | 105.9 | 74.6 | 910 | -1.5 | 2025 | 2026 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1300 | 1300 | - | 984.7 | 75.7 | 455 | 1300 | - | 962 | 74 | 260 | -1.7 | 2026 | 2027 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | NANT | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 360.4 | 75.4 | 880 | 478 | - | 323.4 | 67.7 | 844 | -7.7 | 2026 | 2031 | 5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 60.5 | 12.6
MCG2GM | THRP | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 360.5 | 75.4 | 880 | 478 | - | 323.4 | 67.7 | 844 | -7.7 | 2026 | 2031 | 5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 60.6 | 12.6
BEL1GM | BEL2 | - | - | - | - | - | 20053 | CAPE 5&6 | 20879 | CAPE #6 | 1 | 20053-20879-1 | 233 | 233 | - | 174.5 | 74.9 | 910 | 233 | - | 172.5 | 74 | 910 | -0.9 | 2026 | 2027 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20001 | BLEWETT | 20894 | BLEWDUM | 1 | 20001-20894-1 | 33 | 33 | - | 24.7 | 74.8 | 910 | 33 | - | 24.5 | 74.3 | 910 | -0.5 | 2026 | 2027 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | MCG1 | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 23.1 | 74.7 | 910 | 31 | - | 23.1 | 74.4 | 910 | -0.3 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | MCG2 | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 23.1 | 74.7 | 910 | 31 | - | 23.1 | 74.4 | 910 | -0.3 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
OCO1GM | OCO2 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 71.2 | 74.1 | 455 | 96 | - | 81.1 | 84.5 | 455 | 10.4 | 2027 | 2020 | -7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | 1.5 | 1.5
OCO1GM | OCO2 | - | - | - | - | - | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236-265-1 | 409 | 409 | - | 302.6 | 74 | 834 | 409 | - | 306.5 | 74.9 | 844 | 0.9 | 2027 | 2026 | -1 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 409 | - | 304.2 | 74.4 | -1.6 | -0.4
BEL1GM | BEL2 | - | - | - | - | - | 20053 | CAPE 5&6 | 20878 | CAPE #5 | 1 | 20053-20878-1 | 200 | 200 | - | 148.1 | 74 | 910 | 200 | - | 142.4 | 71.2 | 910 | -2.8 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
MCG2GM | OCO3 | - | - | - | - | - | 112 | 8BAD CRK | 113 | 8JOCASSE | 1 | 112-113-1 | 1790.9 | 1790.9 | - | 1317.4 | 73.6 | 454 | 1790.9 | - | 1316.6 | 73.5 | 454 | -0.1 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | - | 1308.4 | 73.1 | 9 | 0.5
BEL1GM | BEL2 | - | - | - | - | - | 20378 | RICHMOND | 20972 | RICH CT2 | 1 | 20378-20972-1 | 220 | 220 | - | 161.3 | 73.3 | 910 | 220 | - | 158.2 | 71.9 | 910 | -1.4 | 2027 | 2028 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20378 | RICHMOND | 20973 | RICH CT3 | 1 | 20378-20973-1 | 220 | 220 | - | 161.3 | 73.3 | 910 | 220 | - | 158.2 | 71.9 | 910 | -1.4 | 2027 | 2028 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
BEL1GM | BEL2 | - | - | - | - | - | 20369 | FAY E | 20948 | FAYPWC9 | 1 | 20369-20948-1 | 94 | 94 | - | 68.2 | 72.6 | 910 | 94 | - | 67 | 71.3 | 910 | -1.3 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | CAT1 | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 22.1 | 71.3 | 910 | 31 | - | 22 | 71.1 | 910 | -0.2 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | MCG2 | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 22.1 | 71.3 | 910 | 31 | - | 22 | 71.1 | 910 | -0.2 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
ALL4GM | MCG2 | - | - | - | - | - | 20044 | ROB 1 F | 20874 | ROB #1 | 1 | 20044-20874-1 | 244 | 244 | - | 173.4 | 71.1 | 910 | 244 | - | 173.4 | 71.1 | 910 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CAT1GM | CAT2 | - | - | - | - | - | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443-544-1 | 478 | 478 | - | 338.6 | 70.8 | 1808 | 478 | - | 347.8 | 72.8 | 1808 | 2 | 2029 | 2028 | -1 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | - | 324.1 | 67.8 | 14.5 | 3
CLI5GM | CAT1 | - | - | - | - | - | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4-104-1 | 458 | 458 | - | 323.7 | 70.7 | 902 | 458 | - | 341.6 | 74.6 | 908 | 3.9 | 2029 | 2026 | -3 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 458 | - | 321.9 | 70.3 | 1.8 | 0.4
CLI5GM | CAT1 | - | - | - | - | - | 4 | 6CENTRAL | 105 | 6SHADYTW | 2 | 4-105-2 | 458 | 458 | - | 323.7 | 70.7 | 902 | 458 | - | 341.6 | 74.6 | 908 | 3.9 | 2029 | 2026 | -3 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 458 | - | 321.9 | 70.3 | 1.8 | 0.4
CLI3GM | BEL1 | - | - | - | - | - | 20035 | SUT 1-2F | 20866 | SUT #1 | 1 | 20035-20866-1 | 142 | 142 | - | 99.7 | 70.2 | 910 | 142 | - | 96.8 | 68.2 | 910 | -2 | 2029 | 2031 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - Duke1200MWtoCPLE | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\Duke1200MWtoCPLE\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening Duke1200MWtoCPLE Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - Duke1200MWtoCPLE | [5 empty] | 2011 Summer Screening - Base Case | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - Duke1200MWtoCPLE
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
BEL1GM | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 143.7 | 95.8 | 21 | 150 | - | 141.3 | 94.2 | 21 | -1.6 | 2014 | 2015 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 143 | #N/A | #N/A
BEL1GM | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 995 | 93.2 | 42 | 1067 | - | 977.1 | 91.6 | 42 | -1.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 959.5 | 972.7 | 994.3
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.6 | 93.2 | 42 | 95 | - | 87.7 | 92.3 | 42 | -0.9 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | 87.2 | 88.6
BEL1GM | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 991.3 | 92.9 | 42 | 1067 | - | 973.8 | 91.3 | 42 | -1.6 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | 969.3 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.1 | 92.8 | 42 | 40 | - | 36.7 | 91.8 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 35.7 | 37.2 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 299.8 | 92.2 | 42 | 325 | - | 290.2 | 89.3 | 42 | -2.9 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.8 | 295.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 318.5 | 91 | 21 | 350 | - | 315.8 | 90.2 | 21 | -0.8 | 2016 | 2017 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323.2 | 313.4 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 100.6 | 90.6 | 42 | 111 | - | 81.6 | 73.5 | 42 | -17.1 | 2016 | 2027 | 11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 105.6 | 99.5 | #N/A
BEL1GM | BADX | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1682.5 | 88.4 | 42 | 1904.3 | - | 1534.3 | 80.6 | 42 | -7.8 | 2018 | 2022 | 4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1279.9 | 67.2 | 402.6 | 21.2 | 2019.1 | 1773.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 344.4 | 88.3 | 21 | 390 | - | 343.5 | 88.1 | 21 | -0.2 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 376 | 341.6 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 54.5 | 87.9 | 42 | 62 | - | 53.9 | 87 | 42 | -0.9 | 2018 | 2019 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.7 | 53.6 | 54.5
BEL1GM | BADX | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 54.5 | 87.9 | 42 | 62 | - | 53.9 | 87 | 42 | -0.9 | 2018 | 2019 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.7 | 53.6 | 54.5
BEL1GM | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 91.1 | 85.9 | 42 | 106 | - | 78.5 | 74 | 42 | -11.9 | 2019 | 2027 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 93.8 | 89.9 | 91.1
BEL1GM | BADX | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 942.9 | 84.2 | 42 | 1120 | - | 934.8 | 83.5 | 42 | -0.7 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 922 | 926 | 945.5
BEL1GM | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 280.5 | 84.2 | 42 | 333 | - | 261 | 78.4 | 42 | -5.8 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 284 | 276.2 | 280.5
BEL1GM | BADX | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 738.2 | 84.1 | 42 | 878 | - | 734.6 | 83.7 | 42 | -0.4 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 756.9 | 722.7 | 739.3
ALL4GM | BADX | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 756.5 | 82.5 | 42 | 917 | - | 751.5 | 82 | 42 | -0.5 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 775.7 | 744.2 | 759.6
BEL1GM | BADX | - | - | - | - | - | 20329 | RAMSEUR | 20330 | I-RAMTEX | 1 | 20329-20330-1 | 19 | 19 | - | 15.7 | 82.4 | 42 | 19 | - | 15.5 | 81.8 | 42 | -0.6 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.6 | 15.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 724.6 | 82.1 | 42 | 883 | - | 705.1 | 79.9 | 42 | -2.2 | 2021 | 2023 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 759.9 | 718.1 | 737.9
ALL4GM | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192.8 | 82 | 42 | 235 | - | 192.4 | 81.9 | 42 | -0.1 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 190.5 | 192.4 | 192.6
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 723.6 | 81.9 | 42 | 883 | - | 706.2 | 80 | 42 | -1.9 | 2022 | 2023 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 771.1 | 716.2 | 743.8
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 392.1 | 81.2 | 42 | 483 | - | 381.6 | 79 | 42 | -2.2 | 2022 | 2023 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 411.9 | 388.7 | 398.6
BEL1GM | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 666.4 | 81.1 | 42 | 822 | - | 662.5 | 80.6 | 42 | -0.5 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 651.2 | 675.5
BEL1GM | BADX | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 431.4 | 80.9 | 42 | 533 | - | 424.2 | 79.6 | 42 | -1.3 | 2022 | 2023 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 424 | 422.5 | 431.1
BEL1GM | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1077 | 79.8 | 42 | 1350 | - | 842.2 | 62.4 | 42 | -17.4 | 2023 | 2035 | 12 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1526.2 | 1235.3 | #N/A
BEL1GM | BADX | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1200 | 1200 | - | 956.4 | 79.7 | 21 | 1200 | - | 947.8 | 79 | 17 | -0.7 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | - | 622.5 | 51.9 | 333.9 | 27.8 | 976.9 | 964.3 | 984.7
ALL4GM | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 187.1 | 79.6 | 42 | 235 | - | 186.7 | 79.5 | 42 | -0.1 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 187.9 | 188
OCO1GM | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 75 | 78.1 | 21 | 96 | - | 84.8 | 88.3 | 21 | 10.2 | 2024 | 2018 | -6 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | 1.5 | 1.5 | 71.1 | #N/A | 71.2
ALL4GM | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.3 | 77.7 | 42 | 200 | - | 155 | 77.5 | 42 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 156.5 | 155.1 | 155.2
CLIFGM | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.3 | 77.7 | 42 | 200 | - | 155 | 77.5 | 42 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 156.5 | 155.1 | 155.2
BEL1GM | BADX | - | - | - | - | - | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714-827-1 | 621.4 | 621.4 | - | 477 | 76.8 | 8 | 621.4 | - | 476.9 | 76.7 | 1 | -0.1 | 2025 | 2025 | 0 |  | 576 | 621.4 | 576 | JACOBS | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | 621.4 | - | 470.3 | 75.7 | 6.7 | 1.1 | 494.8 | 477.2 | 487.5
BEL1GM | BADX | - | - | - | - | - | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035-20867-1 | 142 | 142 | - | 107.1 | 75.4 | 42 | 142 | - | 106.2 | 74.8 | 42 | -0.6 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 117.3 | 104.7 | 108
ALL4GM | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 23.2 | 75 | 42 | 31 | - | 23.1 | 74.7 | 42 | -0.3 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.1 | 22.7 | 23.1
BEL1GM | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 23.2 | 75 | 42 | 31 | - | 23.1 | 74.6 | 42 | -0.4 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.1 | 22.7 | 23.1
BEL1GM | BADX | - | - | - | - | - | 20053 | CAPE 5&6 | 20879 | CAPE #6 | 1 | 20053-20879-1 | 233 | 233 | - | 174.6 | 74.9 | 42 | 233 | - | 173.1 | 74.3 | 42 | -0.6 | 2026 | 2027 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 178.4 | 171.7 | 174.5
ALL4GM | BADX | - | - | - | - | - | 20001 | BLEWETT | 20894 | BLEWDUM | 1 | 20001-20894-1 | 33 | 33 | - | 24.7 | 74.8 | 42 | 33 | - | 24.6 | 74.5 | 42 | -0.3 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.1 | 24.2 | 24.7
MCG2GM | BADX | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 356.2 | 74.5 | 42 | 478 | - | 319.7 | 66.9 | 40 | -7.6 | 2026 | 2032 | 6 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 59.5 | 12.4 | 457.8 | 360.5 | 360.4
MCG2GM | BADX | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 356.2 | 74.5 | 42 | 478 | - | 319.7 | 66.9 | 40 | -7.6 | 2026 | 2032 | 6 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 59.5 | 12.4 | 457.8 | 360.5 | 360.5
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20977 | RICH CC1 | 1 | 20378-20977-1 | 660 | 660 | - | 486.7 | 73.7 | 42 | 660 | - | 475.2 | 72 | 42 | -1.7 | 2027 | 2028 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 516 | 480 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20265 | E15-STED | 20401 | VANDER | 1 | 20265-20401-1 | 163 | 163 | - | 119.8 | 73.5 | 42 | 163 | - | 89.2 | 54.7 | 42 | -18.8 | 2027 | 2042 | 15 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 139.2 | 121.1 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20519 | M-TARAWA | 20524 | JACKSONV | 1 | 20519-20524-1 | 478 | 478 | - | 351.4 | 73.5 | 42 | 478 | - | 327.8 | 68.6 | 42 | -4.9 | 2027 | 2031 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 443 | 347.7 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20971 | RICH CT1 | 1 | 20378-20971-1 | 220 | 220 | - | 160.8 | 73.1 | 42 | 220 | - | 156.6 | 71.2 | 42 | -1.9 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.5 | 158.6 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20972 | RICH CT2 | 1 | 20378-20972-1 | 220 | 220 | - | 160.8 | 73.1 | 42 | 220 | - | 156.6 | 71.2 | 42 | -1.9 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.5 | 158.6 | 161.3
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20973 | RICH CT3 | 1 | 20378-20973-1 | 220 | 220 | - | 160.8 | 73.1 | 42 | 220 | - | 156.6 | 71.2 | 42 | -1.9 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.5 | 158.6 | 161.3
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20974 | RICH CT4 | 1 | 20378-20974-1 | 220 | 220 | - | 160.8 | 73.1 | 42 | 220 | - | 156.6 | 71.2 | 42 | -1.9 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.5 | 158.6 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20378 | RICHMOND | 20975 | RICH CT5 | 1 | 20378-20975-1 | 220 | 220 | - | 160.8 | 73.1 | 42 | 220 | - | 156.6 | 71.2 | 42 | -1.9 | 2027 | 2029 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 170.5 | 158.6 | #N/A
CLIFGM | BADX | - | - | - | - | - | 20182 | FALLS | 20185 | FALLS | 1 | 20182-20185-1 | 300 | 300 | - | 217.1 | 72.4 | 21 | 300 | - | 212.7 | 70.9 | 21 | -1.5 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 315.9 | 218.8 | #N/A
BEL1GM | BADX | - | - | - | - | - | 20369 | FAY E | 20948 | FAYPWC9 | 1 | 20369-20948-1 | 94 | 94 | - | 68 | 72.4 | 42 | 94 | - | 67.1 | 71.4 | 42 | -1 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 66.9 | 66.9 | 68.2
BEL1GM | BADX | - | - | - | - | - | 20053 | CAPE 5&6 | 20878 | CAPE #5 | 1 | 20053-20878-1 | 200 | 200 | - | 144.1 | 72.1 | 42 | 200 | - | 142.9 | 71.5 | 42 | -0.6 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 155.9 | 141.9 | 148.1
BEL1GM | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 22.2 | 71.6 | 42 | 31 | - | 22.1 | 71.3 | 42 | -0.3 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.7 | 22.1
BEL1GM | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 22.2 | 71.6 | 42 | 31 | - | 22.1 | 71.3 | 42 | -0.3 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 21.7 | 22.1
ALL4GM | BADX | - | - | - | - | - | 20044 | ROB 1 F | 20874 | ROB #1 | 1 | 20044-20874-1 | 244 | 244 | - | 174.1 | 71.4 | 42 | 244 | - | 174 | 71.3 | 42 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 195.2 | #N/A | 173.4
BEL1GM | BADX | - | - | - | - | - | 20550 | CSTL HYN | 20564 | SCOTT T | 1 | 20550-20564-1 | 478 | 478 | - | 341.1 | 71.4 | 21 | 478 | - | 310.5 | 65 | 21 | -6.4 | 2029 | 2033 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 438.6 | 335.8 | #N/A
OCO1GM | BADX | - | - | - | - | - | 20070 | PERSON | 20079 | OXF S T | 1 | 20070-20079-1 | 539 | 539 | - | 384.3 | 71.3 | 21 | 539 | - | 351.5 | 65.2 | 21 | -6.1 | 2029 | 2033 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 448.9 | 388.4 | #N/A
MCG1GM | BADX | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 478 | 478 | - | 338.8 | 70.9 | 42 | 478 | - | 339.8 | 71.1 | 42 | 0.2 | 2029 | 2029 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | - | 328.3 | 68.7 | 10.5 | 2.2 | 393.4 | 349.3 | 358.9
Populate Summary Worksheet

## Duke 1200 to CPLE Roxboro 4 Dn
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500.00 | 20377 | RICHMOND 500.00 | 1 | 337-20377-1 | 1350 | 1350 | 1214.8 | 1493.9 | 108.7 | 49 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | -3.3 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 498.4 | 851.8 | 106.9 | 19 | 796.7 | 474 | 811.3 | 101.8 | 88 | -5.1 | 2011 | 2011 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 181.8 | 22.8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1768.2 | 1958.8 | 101.4 | 73 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | 0.5 | 2011 | 2011 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 358.2 | 21.1
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 481.4 | 844.1 | 100.5 | 19 | 840 | 457.8 | 804.1 | 95.7 | 80 | -4.8 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 180.1 | 21.4
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20378 | RICHMOND 230.00 | 20976 | RICH EMC 13.800 | 1 | 20378-20976-1 | 325 | 325 | 307.2 | 314.8 | 96.9 | 8 | 325 | 307.8 | 315.2 | 97 | 679 | 0.1 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20985 | ANSON 230.00 | 20986 | LILESEMC 13.800 | 1 | 20985-20986-1 | 390 | 390 | 342.4 | 375.5 | 96.3 | 11 | 390 | 344.9 | 375.5 | 96.3 | 873 | 0 | 2013 | 2013 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230.00 | 20616 | BARNARD 115.00 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20885 | WSP #3 13.800 | 1 | 20047-20885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 2 | 95 | 88.1 | 88.1 | 92.8 | 131 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500.00 | 850 | 8PL GRDN 500.00 | 1 | 849-850-1 | 1385.6 | 1385.6 | 979.8 | 1290.8 | 92.3 | 44 | 1385.6 | 883 | 1244.2 | 88.8 | 174 | -3.5 | 2016 | 2017 | 1 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 269.5 | 21.6
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20041 | CF 5-6 F 230.00 | 20053 | CAPE 5&6 115.00 | 1 | 20041-20053-1 | 350 | 350 | 315.3 | 323 | 92.3 | 3 | 350 | 315.2 | 323 | 92.3 | 257 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20022 | BRUN 1 N 230.00 | 20862 | BRUN #1 24.000 | 1 | 20022-20862-1 | 1067 | 1067 | 964.9 | 964.9 | 90.4 | 2 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20020 | BRUN 2 N 230.00 | 20863 | BRUN #2 24.000 | 1 | 20020-20863-1 | 1067 | 1067 | 959.5 | 959.5 | 89.9 | 2 | 1067 | 959.5 | 959.5 | 89.9 | 130 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20106 | WAKEFORE 115.00 | 20107 | E18-WEMC 69.000 | 1 | 20106-20107-1 | 40 | 40 | 35.7 | 35.7 | 89.3 | 1 | 40 | 35.7 | 35.7 | 89.3 | 87 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230.00 | 848 | 6PL GRDN 230.00 | 1 | 844-848-1 | 478 | 478 | 239.8 | 401.3 | 88 | 18 | 478 | 223.9 | 382.2 | 82 | 44 | -6 | 2018 | 2022 | 4 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 844 | 6ENO 230.00 | 848 | 6PL GRDN 230.00 | 2 | 844-848-2 | 478 | 478 | 239.8 | 401.3 | 88 | 19 | 478 | 223.8 | 382.2 | 82 | 44 | -6 | 2018 | 2022 | 4 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230.00 | 445 | 6STAMEY 230.00 | 2 | 443-445-2 | 889 | 889 | 482 | 802.9 | 87.9 | 39 | 889 | 488.7 | 813.6 | 89.6 | 46 | 1.7 | 2018 | 2017 | -1 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 47.8 | 6.3
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20883 | WSP #1 13.800 | 1 | 20047-20883-1 | 62 | 62 | 53.7 | 53.7 | 86.6 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 0 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20884 | WSP #2 13.800 | 1 | 20047-20884-1 | 62 | 62 | 53.7 | 53.7 | 86.6 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 0 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20871 | ROX #3 24.000 | 1 | 20024-20871-1 | 883 | 883 | 759.4 | 759.4 | 86 | 3 | 883 | 730.1 | 759.8 | 86.1 | 3445 | 0.1 | 2019 | 2019 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 2 | 443-544-2 | 478 | 478 | 314.8 | 413.3 | 85.3 | 37 | 478 | 332.2 | 435.9 | 90.3 | 233 | 5 | 2020 | 2017 | -3 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 2 | 0.7
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20869 | ROX #1 22.000 | 1 | 20024-20869-1 | 483 | 483 | 411.4 | 411.4 | 85.2 | 2 | 483 | 393.8 | 411.4 | 85.2 | 2109 | 0 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230.00 | 20985 | ANSON 230.00 | 1 | 20350-20985-1 | 398 | 398 | 204.8 | 346.2 | 85.1 | 12 | 398 | 180.9 | 315.2 | 77.6 | 123 | -7.5 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230.00 | 20985 | ANSON 230.00 | 1 | 20349-20985-1 | 398 | 398 | 204.4 | 345.6 | 85 | 16 | 398 | 180.3 | 314.6 | 77.5 | 117 | -7.5 | 2020 | 2024 | 4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 2 | 538-542-2 | 482 | 482 | 278.7 | 411.3 | 84.9 | 38 | 437 | 270.3 | 398.8 | 91.5 | 211 | 6.6 | 2020 | 2021 | 1 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 61.4 | 12.7
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20018 | ROB 2 N 230.00 | 20864 | ROB #2 22.000 | 1 | 20018-20864-1 | 878 | 878 | 729.7 | 744.2 | 84.8 | 5 | 878 | 730.1 | 748 | 85.2 | 684 | 0.4 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20024 | ROX 1-4F 230.00 | 20870 | ROX #2 24.000 | 1 | 20024-20870-1 | 822 | 822 | 669.2 | 696.3 | 84.7 | 6 | 822 | 665.7 | 1679.8 | 204.4 | 5364 | 119.7 | 2020 | 2011 | -9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20015 | MAYO 1F 500.00 | 20873 | MAYO #1 20.000 | 1 | 20015-20873-1 | 917 | 917 | 775.7 | 775.7 | 84.6 | 3 | 917 | 775.7 | 775.7 | 84.6 | 346 | 0 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 305.6 | 406.9 | 84.5 | 26 | 478 | 359.8 | 449 | 92.9 | 376 | 8.4 | 2020 | 2015 | -5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 22 | 6.1
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 305.6 | 406.9 | 84.5 | 27 | 478 | 360 | 449 | 92.9 | 419 | 8.4 | 2020 | 2015 | -5 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 22 | 6.1
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 443.5 | 709.2 | 84.4 | 32 | 840 | 498.3 | 796.6 | 94.8 | 78 | 10.4 | 2020 | 2014 | -6 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | -22.1 | -2.7
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20030 | LEE 1-3F 115.00 | 20877 | LEE #3 18.000 | 1 | 20030-20877-1 | 333 | 333 | 260.6 | 280.9 | 84.4 | 7 | 333 | 268.6 | 284 | 85.3 | 3097 | 0.9 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 1 | 443-713-1 | 478 | 478 | 288.2 | 414.8 | 84.3 | 39 | 478 | 297.3 | 424.9 | 86.7 | 40 | 2.4 | 2020 | 2019 | -1 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 52.5 | 11.2
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 2 | 443-713-2 | 478 | 478 | 288.2 | 414.8 | 84.3 | 40 | 478 | 297.3 | 424.9 | 86.7 | 40 | 2.4 | 2020 | 2019 | -1 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 52.5 | 11.2
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 848 | 6PL GRDN 230.00 | 850 | 8PL GRDN 500.00 | 5 | 848-850-5 | 1680 | 1680 | 796.5 | 1409.7 | 83.9 | 7 | 1680 | 909.3 | 1466 | 87.3 | 43 | 3.4 | 2020 | 2018 | -2 |  | 1680 | 1680 | 1680 | PLEASANT GARDEN TIE 05 | 500/230 kV Transformer | 1680 | 1680 | 1680 | 1680 | 725.6 | 1187.3 | 70.7 | 222.4 | 13.2
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 537-540-1 | 318.6 | 318.6 | 143.3 | 269.5 | 82.5 | 14 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | 8.7 | 2021 | 2016 | -5 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 31 | 9.7
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 478 | 478 | 330.1 | 383 | 82.3 | 41 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 10.7 | 2021 | 2020 | -1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 15.5 | 3.4
| BASE CASE | 0 |  | 0 |  |  | 20009 | HARRIS1N 230.00 | 20865 | HARRIS#1 22.000 | 1 | 20009-20865-1 | 1120 | 1120 | 922 | 922 | 82.3 | 2 | 1120 | 921.6 | 921.6 | 82.3 | 319 | 0 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 49.8 | 89 | 82.2 | 3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 10.2 | 2021 | 2015 | -6 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | -0.5 | -0.5
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 49.8 | 89 | 82.2 | 3 | 108.3 | 56 | 100.1 | 92.4 | 43 | 10.2 | 2021 | 2015 | -6 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | -0.5 | -0.5
| BASE CASE | 0 |  | 0 |  |  | 20329 | RAMSEUR 69.000 | 20330 | I-RAMTEX 69.000 | 1 | 20329-20330-1 | 19 | 19 | 15.6 | 15.6 | 82 | 1 | 19 | 15.6 | 15.6 | 82 | 87 | 0 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| WOODLAWN5 | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 380.2 | 574.8 | 81 | 47 | 717 | 415.6 | 628.2 | 89.3 | 174 | 8.3 | 2022 | 2017 | -5 |  | 717 | 717 | 717 | STEELBERRY | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 394.5 | 597 | 84.4 | -22.2 | -3.4
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20851 | ASHVL #1 18.000 | 1 | 20800-20851-1 | 235 | 235 | 190.3 | 190.3 | 81 | 2 | 235 | 191.6 | 191.6 | 81.6 | 130 | 0.6 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20030 | LEE 1-3F 115.00 | 20876 | LEE #2 13.800 | 1 | 20030-20876-1 | 106 | 106 | 78.7 | 85 | 80.2 | 3 | 106 | 81.2 | 93.8 | 88.5 | 735 | 8.3 | 2023 | 2018 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 1 | 538-542-1 | 482 | 482 | 278.7 | 385.6 | 80 | 37 | 437 | 270.3 | 398.8 | 91.5 | 167 | 11.5 | 2023 | 2021 | -2 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 1 | 712-719-1 | 840 | 840 | 369.8 | 671.6 | 80 | 4 | 840 | 415.6 | 754.3 | 89.8 | 41 | 9.8 | 2023 | 2017 | -6 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | -21.1 | -2.5
| BASE CASE | 0 |  | 0 |  |  | 837 | 6ROWANG 230.00 | 840 | 6ROWANT 230.00 | 1 | 837-840-1 | 1200 | 1200 | 977.3 | 977.3 | 79.8 | 3 | 1110 | 977 | 977 | 86.7 | 175 | 6.9 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20039 | SUT 3 F 230.00 | 20868 | SUT #3 24.000 | 1 | 20039-20868-1 | 533 | 533 | 424 | 424 | 79.5 | 2 | 533 | 424 | 424 | 79.5 | 130 | 0 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20030 | LEE 1-3F 115.00 | 20875 | LEE #1 13.800 | 1 | 20030-20875-1 | 111 | 111 | 81.6 | 87.7 | 79 | 3 | 111 | 84 | 105.6 | 95.1 | 707 | 16.1 | 2023 | 2014 | -9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20852 | ASHVL #2 20.000 | 1 | 20800-20852-1 | 235 | 235 | 185.1 | 185.1 | 78.8 | 2 | 235 | 185.6 | 379.2 | 161.4 | 548 | 82.6 | 2024 | 2011 | -13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 4 | 538-540-4 | 563.7 | 563.7 | 356.6 | 444.3 | 78.7 | 41 | 490.8 | 371.4 | 413.6 | 84.8 | 1054 | 6.1 | 2024 | 2027 | 3 |  | 490.8 | 563.7 | 540.2 | MECKLENBURG WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 563.7 | 333.5 | 415.6 | 73.7 | 28.7 | 5
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 443-540-1 | 478 | 478 | 202 | 383.5 | 78.3 | 5 | 478 | 291.8 | 453 | 92.8 | 39 | 14.5 | 2024 | 2015 | -9 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | -4.5 | -0.7
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230.00 | 540 | 6MCGUIRE 230.00 | 2 | 443-540-2 | 478 | 478 | 202 | 383.5 | 78.3 | 6 | 478 | 291.8 | 453 | 92.8 | 40 | 14.5 | 2024 | 2015 | -9 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | -4.5 | -0.7
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20858 | ASHVCT#1 18.000 | 1 | 20800-20858-1 | 200 | 200 | 156.5 | 156.5 | 78.3 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20859 | ASHVCT#2 18.000 | 1 | 20800-20859-1 | 200 | 200 | 156.5 | 156.5 | 78.3 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | 0 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 290.4 | 373.8 | 78 | 36 | 478 | 313.5 | 402.6 | 84.9 | 168 | 6.9 | 2024 | 2020 | -4 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 300.9 | 384.5 | 80.7 | -10.7 | -2.7
| PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 20053 | CAPE 5&6 115.00 | 20878 | CAPE #5 13.800 | 1 | 20053-20878-1 | 200 | 200 | 144.4 | 155.5 | 77.7 | 4 | 200 | 144.3 | 155.5 | 77.8 | 335 | 0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20977 | RICH CC1 18.000 | 1 | 20378-20977-1 | 660 | 660 | 513.1 | 513.1 | 77.7 | 1 | 660 | 510 | 516 | 78.2 | 1433 | 0.5 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230.00 | 265 | 6RIVERVW 230.00 | 2 | 236-265-2 | 452.5 | 452.5 | 239.3 | 354.4 | 77.3 | 28 | 452.5 | 287.6 | 425.5 | 93.6 | 52 | 16.3 | 2025 | 2015 | -10 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -66.4 | -14.1
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20972 | RICH CT2 18.000 | 1 | 20378-20972-1 | 220 | 220 | 169 | 169 | 76.8 | 2 | 220 | 169.1 | 169.1 | 76.9 | 130 | 0.1 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20973 | RICH CT3 18.000 | 1 | 20378-20973-1 | 220 | 220 | 169 | 169 | 76.8 | 2 | 220 | 169.1 | 169.1 | 76.9 | 130 | 0.1 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20971 | RICH CT1 18.000 | 1 | 20378-20971-1 | 220 | 220 | 168.8 | 168.8 | 76.7 | 1 | 220 | 169.1 | 169.1 | 76.9 | 87 | 0.2 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20974 | RICH CT4 18.000 | 1 | 20378-20974-1 | 220 | 220 | 168.8 | 168.8 | 76.7 | 1 | 220 | 169.1 | 169.1 | 76.9 | 87 | 0.2 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20975 | RICH CT5 18.000 | 1 | 20378-20975-1 | 220 | 220 | 168.8 | 168.8 | 76.7 | 1 | 220 | 169.1 | 169.1 | 76.9 | 87 | 0.2 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PINOCAW | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 796.7 | 796.7 | 353 | 616.4 | 76.3 | 3 | 796.7 | 384.9 | 671.3 | 83.8 | 45 | 7.5 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA BLACK | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 340.3 | 594.8 | 74.1 | 21.6 | 2.2
| PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 353 | 616.4 | 76.3 | 3 | 796.7 | 384.9 | 671.3 | 83.8 | 46 | 7.5 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 340.3 | 594.8 | 74.1 | 21.6 | 2.2
| BASE CASE | 0 |  | 0 |  |  | 20251 | LEE 230.00 | 20958 | WYNCO#3 18.000 | 1 | 20251-20958-1 | 220 | 220 | 167.2 | 167.2 | 76 | 2 | 220 | 158.9 | 158.9 | 72.2 | 130 | -3.8 | 2025 | 2028 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20251 | LEE 230.00 | 20959 | WYNCO#4 18.000 | 1 | 20251-20959-1 | 220 | 220 | 167.2 | 167.2 | 76 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230.00 | 716 | 6MITCH R 230.00 | 2 | 712-716-2 | 717 | 717 | 333.6 | 555.4 | 75.9 | 4 | 717 | 383.7 | 638.6 | 87.8 | 39 | 11.9 | 2025 | 2018 | -7 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | -29.3 | -3.3
| BASE CASE | 0 |  | 0 |  |  | 20251 | LEE 230.00 | 20956 | WYNCO#1 18.000 | 1 | 20251-20956-1 | 220 | 220 | 166.9 | 166.9 | 75.9 | 2 | 220 | 158.8 | 158.8 | 72.2 | 130 | -3.7 | 2025 | 2028 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20251 | LEE 230.00 | 20957 | WYNCO#2 18.000 | 1 | 20251-20957-1 | 220 | 220 | 166.9 | 166.9 | 75.9 | 2 | 220 | 158.6 | 158.6 | 72.1 | 130 | -3.8 | 2025 | 2028 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20061 | APEX US1 230.00 | 20212 | NEW HILL 230.00 | 1 | 20061-20212-1 | 797 | 797 | 477.2 | 597.9 | 75.4 | 22 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20053 | CAPE 5&6 115.00 | 20879 | CAPE #6 18.000 | 1 | 20053-20879-1 | 233 | 233 | 174.9 | 174.9 | 75.1 | 2 | 233 | 174.7 | 174.7 | 75 | 130 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20035 | SUT 1-2F 115.00 | 20867 | SUT #2 13.800 | 1 | 20035-20867-1 | 142 | 142 | 106.2 | 106.2 | 74.8 | 2 | 142 | 106.1 | 117.2 | 82.6 | 341 | 7.8 | 2026 | 2021 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20057 | DARL CO 230.00 | 20954 | DCP#12 13.800 | 1 | 20057-20954-1 | 167 | 167 | 123.3 | 123.3 | 73.8 | 2 | 167 | 123.3 | 123.3 | 73.8 | 135 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20057 | DARL CO 230.00 | 20955 | DCP#13 13.800 | 1 | 20057-20955-1 | 167 | 167 | 123.3 | 123.3 | 73.8 | 2 | 167 | 123.3 | 123.3 | 73.8 | 135 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| KIMBRELLB | 331 | 6ALLEN | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 1 | 443-544-1 | 478 | 478 | 314.8 | 357.8 | 73.4 | 36 | 478 | 327 | 368.6 | 76.1 | 189 | 2.7 | 2027 | 2025 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 342.8 | 70 | 15 | 3.4
| BASE CASE | 0 |  | 0 |  |  | 112 | 8BAD CRK 500.00 | 113 | 8JOCASSE 500.00 | 1 | 112-113-1 | 1790.9 | 1790.9 | 1396.3 | 1396.3 | 73.1 | 2 | 1732 | 1396.9 | 1396.9 | 75.9 | 84 | 2.8 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | 1397.7 | 1397.7 | 73 | -1.4 | 0.1
| BASE CASE | 0 |  | 0 |  |  | 20001 | BLEWETT 115.00 | 20894 | BLEWDUM 4.4000 | 1 | 20001-20894-1 | 33 | 33 | 24.1 | 24.1 | 72.9 | 2 | 33 | 24.1 | 24.1 | 72.9 | 130 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 105 | 6SHADYTW 230.00 | 109 | 6SHADY G 230.00 | 2 | 105-109-2 | 478 | 478 | 216.1 | 346.7 | 72.8 | 3 | 478 | 244.5 | 391.9 | 83.3 | 44 | 10.5 | 2028 | 2021 | -7 |  | 477.96 | 477.96 | 477.96 | SHADY GROVE | 230 kV Line | 859.9297 | 1008.8939 | 859.9297 | 478 | 214.7 | 346.1 | 73.3 | 0.6 | -0.5
| DUTCHOVERB | 543 | 6RIVRBEN | 441 | 6LINCOLN | 1 | 441 | 6LINCOLN 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 441-543-2 | 597.5 | 597.5 | 258.9 | 441.7 | 72.1 | 2 | 597.5 | 284.3 | 481.1 | 79.3 | 41 | 7.2 | 2028 | 2023 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 597.5 | 285.3 | 500.9 | 82.2 | -59.2 | -10.1
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20519 | M-TARAWA 230.00 | 20524 | JACKSONV 230.00 | 1 | 20519-20524-1 | 478 | 478 | 321.1 | 327.8 | 71.7 | 3 | 478 | 321.1 | 424.7 | 92.7 | 1264 | 21 | 2028 | 2015 | -13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20044 | ROB 1 F 115.00 | 20874 | ROB #1 18.000 | 1 | 20044-20874-1 | 244 | 244 | 174.1 | 174.1 | 71.4 | 2 | 244 | 174.5 | 186.9 | 76.6 | 173 | 5.2 | 2029 | 2025 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20182 | FALLS 230.00 | 20185 | FALLS 115.00 | 1 | 20182-20185-1 | 300 | 300 | 214.3 | 214.3 | 71.4 | 5 | 300 | 214.6 | 311.1 | 103.7 | 1807 | 32.3 | 2029 | 2011 | -18 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20369 | FAY E 69.000 | 20948 | FAYPWC9 13.800 | 1 | 20369-20948-1 | 94 | 94 | 66.9 | 66.9 | 71.2 | 2 | 94 | 66.9 | 66.9 | 71.2 | 130 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 331 | 6ALLEN 230.00 | 544 | 6WINECOF 230.00 | 1 | 331-544-1 | 473.3 | 473.3 | 267.6 | 338.6 | 71.1 | 39 | 473.3 | 272.5 | 344.1 | 72.7 | 1 | 1.6 | 2029 | 2028 | -1 |  | 458.1 | 473.3 | 458.1 | KIMBRELL | 230 kV Line | 458.114 | 473.2517 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 331 | 6ALLEN 230.00 | 544 | 6WINECOF 230.00 | 2 | 331-544-2 | 473.3 | 473.3 | 267.6 | 338.6 | 71.1 | 40 | 473.3 | 272.5 | 344.1 | 72.7 | 2 | 1.6 | 2029 | 2028 | -1 |  | 458.1 | 473.3 | 458.1 | KIMBRELL | 230 kV Line | 458.114 | 473.2517 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115.00 | 20890 | TILL #3 13.800 | 1 | 20004-20890-1 | 31 | 31 | 22 | 22 | 71 | 2 | 31 | 22 | 22 | 71 | 130 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115.00 | 20891 | TILL #4 13.800 | 1 | 20004-20891-1 | 31 | 31 | 22 | 22 | 71 | 2 | 31 | 22 | 22 | 71 | 130 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230.00 | 20079 | OXF S T 230.00 | 1 | 20070-20079-1 | 539 | 539 | 335.9 | 375.7 | 70.6 | 10 | 539 | 369.7 | 430.7 | 81 | 1638 | 10.4 | 2029 | 2022 | -7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HODGBK1SHORT | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115.00 | 22 | CLARK HL 100.00 | 4 | 1-22-4 | 96 | 96 | 55.7 | 67.5 | 70.4 | 13 | 96 | 65.4 | 77 | 80.2 | 347 | 9.8 | 2029 | 2023 | -6 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | -1.7 | -1.7
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230.00 | 20097 | CG-ROX 230.00 | 1 | 20066-20097-1 | 423 | 423 | 226.8 | 292.5 | 70.2 | 9 | 423 | 272.9 | 351.7 | 84.4 | 607 | 14.2 | 2029 | 2020 | -9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 538-540-1 | 563.7 | 563.7 | 316.7 | 394.5 | 69.9 | 35 | 490.8 | 329.8 | 367.2 | 75.3 | 86 | 5.4 | 2030 | 2033 | 3 |  | 490.8 | 563.7 | 540.2 | CRAIGHEAD BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CRAIGHEADB | 540 | 6MCGUIRE | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 3 | 538-540-3 | 617.5 | 617.5 | 356.6 | 432.3 | 69.9 | 40 | 529.8 | 371.4 | 413.6 | 78.5 | 354 | 8.6 | 2030 | 2031 | 1 |  | 529.8 | 617.5 | 553.7 | MECKLENBURG BL | 230 kV Line | 556.9073 | 617.458 | 556.9073 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1886.3 | 99.1 | 42 | 1904.3 | - | 1909.2 | 100.3 | 910 | 1.2 | 2012 | 2011 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 345.2 | 18.2
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 42 | 95 | - | 88.1 | 92.7 | 910 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.7 | 92.4 | 42 | 1067 | - | 985.6 | 92.4 | 910 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.6 | 92.1 | 42 | 1067 | - | 982.5 | 92.1 | 910 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 344.4 | 88.3 | 21 | 390 | - | 349.5 | 89.6 | 455 | 1.3 | 2018 | 2017 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 54.2 | 87.4 | 42 | 62 | - | 54.2 | 87.4 | 910 | 0 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 54.2 | 87.4 | 42 | 62 | - | 54.2 | 87.4 | 910 | 0 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1171.4 | 86.8 | 42 | 1350 | - | 1123.1 | 83.2 | 910 | -3.6 | 2019 | 2021 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 736.4 | 83.9 | 42 | 878 | - | 735.9 | 83.8 | 910 | -0.1 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 739.6 | 83.8 | 42 | 883 | - | 729.3 | 82.6 | 910 | -1.2 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 936.6 | 83.6 | 42 | 1120 | - | 935.6 | 83.5 | 910 | -0.1 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 399.5 | 82.7 | 42 | 483 | - | 394.7 | 81.7 | 910 | -1 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 756 | 82.4 | 42 | 917 | - | 752.8 | 82.1 | 910 | -0.3 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 674.5 | 82.1 | 42 | 822 | - | 667.2 | 81.2 | 910 | -0.9 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192.4 | 81.9 | 42 | 235 | - | 192.2 | 81.8 | 910 | -0.1 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 427.6 | 80.2 | 42 | 533 | - | 427.6 | 80.2 | 910 | 0 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 188 | 80 | 42 | 235 | - | 187.5 | 79.8 | 910 | -0.2 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 266.1 | 79.9 | 42 | 333 | - | 271.7 | 81.6 | 910 | 1.7 | 2023 | 2022 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | RIV6 | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.1 | 77.6 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO3 | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.1 | 77.6 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 443 | 6MARSHAL | 713 | 6BECKRDT | 1 | 443-713-1 | 437 | 437 | - | 337.5 | 77.2 | 84 | 437 | - | 349.7 | 80 | 1436 | 2.8 | 2025 | 2023 | -2 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 306.2 | 70.1 | 31.3 | 7.1
STUDYL | MCG1 | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 458 | 458 | - | 352.4 | 76.9 | 42 | 458 | - | 364 | 79.5 | 910 | 2.6 | 2025 | 2023 | -2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 458 | - | 347.6 | 75.9 | 4.8 | 1
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 80.4 | 75.9 | 42 | 106 | - | 82.3 | 77.7 | 910 | 1.8 | 2025 | 2024 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 83.3 | 75 | 42 | 111 | - | 85.1 | 76.6 | 910 | 1.6 | 2026 | 2025 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 23.1 | 74.7 | 42 | 31 | - | 23.1 | 74.6 | 910 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1300 | 1300 | - | 969.2 | 74.6 | 21 | 1300 | - | 979.5 | 75.3 | 455 | 0.7 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG2 | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 23.1 | 74.6 | 42 | 31 | - | 23.1 | 74.6 | 910 | 0 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20001 | BLEWETT | 20894 | BLEWDUM | 1 | 20001-20894-1 | 33 | 33 | - | 24.6 | 74.5 | 42 | 33 | - | 24.6 | 74.5 | 910 | 0 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035-20867-1 | 142 | 142 | - | 105.7 | 74.4 | 42 | 142 | - | 105.7 | 74.4 | 910 | 0 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20053 | CAPE 5&6 | 20879 | CAPE #6 | 1 | 20053-20879-1 | 233 | 233 | - | 173.3 | 74.4 | 42 | 233 | - | 173.1 | 74.3 | 910 | -0.1 | 2026 | 2027 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO3 | - | - | - | - | - | 112 | 8BAD CRK | 113 | 8JOCASSE | 1 | 112-113-1 | 1790.9 | 1790.9 | - | 1312.3 | 73.3 | 21 | 1790.9 | - | 1319 | 73.7 | 454 | 0.4 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | - | 1308.4 | 73.1 | 3.9 | 0.2
STUDYL | BEL1 | - | - | - | - | - | 20378 | RICHMOND | 20972 | RICH CT2 | 1 | 20378-20972-1 | 220 | 220 | - | 160.3 | 72.9 | 42 | 220 | - | 160.4 | 72.9 | 910 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20378 | RICHMOND | 20973 | RICH CT3 | 1 | 20378-20973-1 | 220 | 220 | - | 160.3 | 72.9 | 42 | 220 | - | 160.4 | 72.9 | 910 | 0 | 2027 | 2027 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20251 | LEE | 20958 | WYNCO#3 | 1 | 20251-20958-1 | 220 | 220 | - | 160.2 | 72.8 | 42 | 220 | - | 152.6 | 69.4 | 910 | -3.4 | 2028 | 2030 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20251 | LEE | 20959 | WYNCO#4 | 1 | 20251-20959-1 | 220 | 220 | - | 160.2 | 72.8 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20251 | LEE | 20956 | WYNCO#1 | 1 | 20251-20956-1 | 220 | 220 | - | 160 | 72.7 | 42 | 220 | - | 152.5 | 69.3 | 910 | -3.4 | 2028 | 2030 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20251 | LEE | 20957 | WYNCO#2 | 1 | 20251-20957-1 | 220 | 220 | - | 159.9 | 72.7 | 42 | 220 | - | 152.2 | 69.2 | 910 | -3.5 | 2028 | 2030 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20369 | FAY E | 20948 | FAYPWC9 | 1 | 20369-20948-1 | 94 | 94 | - | 67.5 | 71.8 | 42 | 94 | - | 67.5 | 71.8 | 910 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20053 | CAPE 5&6 | 20878 | CAPE #5 | 1 | 20053-20878-1 | 200 | 200 | - | 143.1 | 71.5 | 42 | 200 | - | 142.9 | 71.4 | 910 | -0.1 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 22.1 | 71.3 | 42 | 31 | - | 22.1 | 71.2 | 910 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 22.1 | 71.3 | 42 | 31 | - | 22.1 | 71.2 | 910 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG2 | - | - | - | - | - | 20044 | ROB 1 F | 20874 | ROB #1 | 1 | 20044-20874-1 | 244 | 244 | - | 173.5 | 71.1 | 42 | 244 | - | 173.4 | 71.1 | 910 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG2 | - | - | - | - | - | 20057 | DARL CO | 20954 | DCP#12 | 1 | 20057-20954-1 | 167 | 167 | - | 118.8 | 71.1 | 42 | 167 | - | 118.7 | 71.1 | 910 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG2 | - | - | - | - | - | 20057 | DARL CO | 20955 | DCP#13 | 1 | 20057-20955-1 | 167 | 167 | - | 118.8 | 71.1 | 42 | 167 | - | 118.7 | 71.1 | 910 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO1 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 67.2 | 70 | 21 | 96 | - | 77.7 | 80.9 | 455 | 10.9 | 2030 | 2022 | -8 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | -2.5 | -2.6
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Duke1200MWtoCPLE_Rox4Dn
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 142.4 | 94.9 | 1 | 150 | - | 142.5 | 95 | 21 | 0.1 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 88.1 | 92.8 | 2 | 95 | - | 88.1 | 92.7 | 42 | -0.1 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 985.9 | 92.4 | 2 | 1067 | - | 985.7 | 92.4 | 42 | 0 | 2015 | 2015 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 959.5 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 982.8 | 92.1 | 2 | 1067 | - | 982.6 | 92.1 | 42 | 0 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 964.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 36.8 | 91.9 | 2 | 40 | - | 36.8 | 92.1 | 42 | 0.2 | 2016 | 2016 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 35.7 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 316.5 | 90.4 | 1 | 350 | - | 316.1 | 90.3 | 21 | -0.1 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 323 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 293 | 90.2 | 2 | 325 | - | 293 | 90.2 | 42 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 314.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 344.1 | 88.2 | 1 | 390 | - | 344.7 | 88.4 | 21 | 0.2 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 375.5 | #N/A | 344.4
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 54.2 | 87.4 | 2 | 62 | - | 54.2 | 87.4 | 42 | 0 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.7 | #N/A | 54.2
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 54.2 | 87.4 | 2 | 62 | - | 54.2 | 87.4 | 42 | 0 | 2018 | 2018 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 53.7 | #N/A | 54.2
STUDYL | BADX | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1623.3 | 85.2 | 2 | 1904.3 | - | 1636.2 | 85.9 | 42 | 0.7 | 2020 | 2019 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1279.9 | 67.2 | 343.4 | 18 | 1958.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 737.1 | 84 | 2 | 878 | - | 736.3 | 83.9 | 42 | -0.1 | 2020 | 2020 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 744.2 | #N/A | 736.4
STUDYL | BADX | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 936.2 | 83.6 | 2 | 1120 | - | 935.3 | 83.5 | 42 | -0.1 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 922 | #N/A | 936.6
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 736.7 | 83.4 | 2 | 883 | - | 712.3 | 80.7 | 42 | -2.7 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 759.4 | #N/A | 739.6
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 398 | 82.4 | 2 | 483 | - | 385.5 | 79.8 | 42 | -2.6 | 2021 | 2023 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 411.4 | #N/A | 399.5
STUDYL | BADX | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 753.8 | 82.2 | 2 | 917 | - | 753.5 | 82.2 | 42 | 0 | 2021 | 2021 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 775.7 | #N/A | 756
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192.7 | 82 | 2 | 235 | - | 192.4 | 81.9 | 42 | -0.1 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 190.3 | #N/A | 192.4
STUDYL | BADX | - | - | - | - | - | 20329 | RAMSEUR | 20330 | I-RAMTEX | 1 | 20329-20330-1 | 19 | 19 | - | 15.6 | 81.9 | 2 | 19 | - | 15.6 | 81.9 | 42 | 0 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.6 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 664.4 | 80.8 | 2 | 822 | - | 661.7 | 80.5 | 42 | -0.3 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 696.3 | #N/A | 674.5
STUDYL | BADX | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 427.8 | 80.3 | 2 | 533 | - | 427.8 | 80.3 | 42 | 0 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 424 | #N/A | 427.6
STUDYL | BADX | - | - | - | - | - | 2447 | 1SAXAPAW | 2448 | 1SWEPSVL | 1 | 2447-2448-1 | 27 | 27 | - | 21.7 | 80.2 | 1 | 27 | - | 21.7 | 80.4 | 21 | 0.2 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 27 | - | 18.6 | 68.8 | 3.1 | 11.4 | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 1006 | 1ARMORYB | 1123 | 1N GWOOD | 1 | 1006-1123-1 | 41.7 | 41.7 | - | 33.4 | 80.1 | 1 | 41.7 | - | 35.4 | 84.9 | 21 | 4.8 | 2023 | 2020 | -3 |  | 38.1 | 41.7 | 38.1 | GATEWAY NO. 2 - TAP LINE | 44 kV Line | 0 | 0 | 0 | 41.7 | - | 33.9 | 81.3 | -0.5 | -1.2 | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 187.2 | 79.6 | 2 | 235 | - | 186.8 | 79.5 | 42 | -0.1 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 185.1 | #N/A | 188
STUDYL | BADX | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1200 | 1200 | - | 951.9 | 79.3 | 1 | 1200 | - | 955.1 | 79.6 | 21 | 0.3 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | - | 622.5 | 51.9 | 329.4 | 27.4 | 977.3 | #N/A | 969.2
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 263.7 | 79.2 | 2 | 333 | - | 268.8 | 80.7 | 42 | 1.5 | 2023 | 2022 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 280.9 | #N/A | 266.1
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.3 | 77.6 | 2 | 200 | - | 155 | 77.5 | 42 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 156.5 | #N/A | 155.1
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.3 | 77.6 | 2 | 200 | - | 155 | 77.5 | 42 | -0.1 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 156.5 | #N/A | 155.1
STUDYL | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1014.5 | 75.2 | 2 | 1350 | - | 966.8 | 71.6 | 42 | -3.6 | 2026 | 2028 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1493.9 | #N/A | 1171.4
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 79.6 | 75.1 | 2 | 106 | - | 81.3 | 76.7 | 42 | 1.6 | 2026 | 2025 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 85 | #N/A | 80.4
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 23.2 | 74.9 | 2 | 31 | - | 23.2 | 74.8 | 42 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22 | #N/A | 23.1
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 23.2 | 74.8 | 2 | 31 | - | 23.2 | 74.8 | 42 | 0 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22 | #N/A | 23.1
STUDYL | BADX | - | - | - | - | - | 20001 | BLEWETT | 20894 | BLEWDUM | 1 | 20001-20894-1 | 33 | 33 | - | 24.7 | 74.7 | 2 | 33 | - | 24.6 | 74.6 | 42 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 24.1 | #N/A | 24.6
STUDYL | BADX | - | - | - | - | - | 20035 | SUT 1-2F | 20867 | SUT #2 | 1 | 20035-20867-1 | 142 | 142 | - | 105.9 | 74.6 | 2 | 142 | - | 105.8 | 74.5 | 42 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 106.2 | #N/A | 105.7
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 82.5 | 74.4 | 2 | 111 | - | 84.1 | 75.8 | 42 | 1.4 | 2026 | 2025 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 87.7 | #N/A | 83.3
STUDYL | BADX | - | - | - | - | - | 20053 | CAPE 5&6 | 20879 | CAPE #6 | 1 | 20053-20879-1 | 233 | 233 | - | 173.4 | 74.4 | 2 | 233 | - | 173.3 | 74.4 | 42 | 0 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 174.9 | #N/A | 173.3
STUDYL | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 71.2 | 74.1 | 1 | 96 | - | 81.3 | 84.7 | 21 | 10.6 | 2027 | 2020 | -7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | -2.3 | -2.5 | 67.5 | #N/A | 67.2
STUDYL | BADX | - | - | - | - | - | 20251 | LEE | 20958 | WYNCO#3 | 1 | 20251-20958-1 | 220 | 220 | - | 160.4 | 72.9 | 2 | 220 | - | 152.8 | 69.5 | 42 | -3.4 | 2027 | 2030 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 167.2 | #N/A | 160.2
STUDYL | BADX | - | - | - | - | - | 20251 | LEE | 20959 | WYNCO#4 | 1 | 20251-20959-1 | 220 | 220 | - | 160.3 | 72.9 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 167.2 | #N/A | 160.2
STUDYL | BADX | - | - | - | - | - | 20251 | LEE | 20956 | WYNCO#1 | 1 | 20251-20956-1 | 220 | 220 | - | 160.1 | 72.8 | 2 | 220 | - | 152.6 | 69.4 | 42 | -3.4 | 2028 | 2030 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 166.9 | #N/A | 160
STUDYL | BADX | - | - | - | - | - | 20251 | LEE | 20957 | WYNCO#2 | 1 | 20251-20957-1 | 220 | 220 | - | 160.1 | 72.8 | 2 | 220 | - | 152.4 | 69.3 | 42 | -3.5 | 2028 | 2030 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 166.9 | #N/A | 159.9
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20977 | RICH CC1 | 1 | 20378-20977-1 | 660 | 660 | - | 480.7 | 72.8 | 2 | 660 | - | 480.8 | 72.8 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 513.1 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20971 | RICH CT1 | 1 | 20378-20971-1 | 220 | 220 | - | 158.4 | 72 | 2 | 220 | - | 158.4 | 72 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 168.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20972 | RICH CT2 | 1 | 20378-20972-1 | 220 | 220 | - | 158.4 | 72 | 2 | 220 | - | 158.4 | 72 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 169 | #N/A | 160.3
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20973 | RICH CT3 | 1 | 20378-20973-1 | 220 | 220 | - | 158.4 | 72 | 2 | 220 | - | 158.4 | 72 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 169 | #N/A | 160.3
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20974 | RICH CT4 | 1 | 20378-20974-1 | 220 | 220 | - | 158.4 | 72 | 2 | 220 | - | 158.4 | 72 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 168.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20975 | RICH CT5 | 1 | 20378-20975-1 | 220 | 220 | - | 158.4 | 72 | 2 | 220 | - | 158.4 | 72 | 42 | 0 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 168.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20369 | FAY E | 20948 | FAYPWC9 | 1 | 20369-20948-1 | 94 | 94 | - | 67.5 | 71.8 | 2 | 94 | - | 67.4 | 71.7 | 42 | -0.1 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 66.9 | #N/A | 67.5
STUDYL | BADX | - | - | - | - | - | 20053 | CAPE 5&6 | 20878 | CAPE #5 | 1 | 20053-20878-1 | 200 | 200 | - | 143.2 | 71.6 | 2 | 200 | - | 143 | 71.5 | 42 | -0.1 | 2028 | 2028 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 155.5 | #N/A | 143.1
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 22.2 | 71.5 | 2 | 31 | - | 22.1 | 71.4 | 42 | -0.1 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.1
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 22.2 | 71.5 | 2 | 31 | - | 22.1 | 71.4 | 42 | -0.1 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.1
STUDYL | BADX | - | - | - | - | - | 20044 | ROB 1 F | 20874 | ROB #1 | 1 | 20044-20874-1 | 244 | 244 | - | 174.2 | 71.4 | 2 | 244 | - | 174 | 71.3 | 42 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 174.1 | #N/A | 173.5
STUDYL | BADX | - | - | - | - | - | 20057 | DARL CO | 20954 | DCP#12 | 1 | 20057-20954-1 | 167 | 167 | - | 119.2 | 71.4 | 2 | 167 | - | 119.1 | 71.3 | 42 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 123.3 | #N/A | 118.8
STUDYL | BADX | - | - | - | - | - | 20057 | DARL CO | 20955 | DCP#13 | 1 | 20057-20955-1 | 167 | 167 | - | 119.2 | 71.4 | 2 | 167 | - | 119.1 | 71.3 | 42 | -0.1 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 123.3 | #N/A | 118.8
STUDYL | BADX | - | - | - | - | - | 20182 | FALLS | 20185 | FALLS | 1 | 20182-20185-1 | 300 | 300 | - | 214.3 | 71.4 | 1 | 300 | - | 215 | 71.7 | 21 | 0.3 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 214.3 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20519 | M-TARAWA | 20524 | JACKSONV | 1 | 20519-20524-1 | 478 | 478 | - | 336.8 | 70.5 | 2 | 478 | - | 337 | 70.5 | 42 | 0 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 327.8 | #N/A | #N/A
Populate Summary Worksheet

## PEC TRM BR1 Down 1200 DKCPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 17 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 8 | Not in original screening
[25 empty] | 25 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500.00 | 20377 | RICHMOND 500.00 | 1 | 337-20377-1 | 1350 | 1350 | 1559.2 | 1791.4 | 135.5 | 48 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | -30.1 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 549.9 | 940.4 | 118 | 22 | 796.7 | 474 | 811.3 | 101.8 | 88 | -16.2 | 2011 | 2011 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 270.4 | 33.9
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 531.1 | 931.9 | 110.9 | 21 | 840 | 457.8 | 804.1 | 95.7 | 80 | -15.2 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 267.9 | 31.8
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 2 | 538-542-2 | 482 | 482 | 353 | 522.4 | 108.3 | 42 | 437 | 270.3 | 398.8 | 91.5 | 211 | -16.8 | 2011 | 2021 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 172.5 | 36.1
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.7 | 110.5 | 102 | 6 | 108.3 | 56 | 100.1 | 92.4 | 43 | -9.6 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 21 | 19.3
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.7 | 110.5 | 102 | 6 | 108.3 | 56 | 100.1 | 92.4 | 43 | -9.6 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 21 | 19.3
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 365.2 | 464.8 | 97.6 | 24 | 478 | 359.8 | 449 | 92.9 | 376 | -4.7 | 2013 | 2015 | 2 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 79.9 | 19.2
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 365.2 | 464.8 | 97.6 | 25 | 478 | 360 | 449 | 92.9 | 419 | -4.7 | 2013 | 2015 | 2 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 79.9 | 19.2
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230.00 | 20097 | CG-ROX 230.00 | 1 | 20066-20097-1 | 423 | 423 | 311.4 | 389.6 | 97.2 | 10 | 423 | 272.9 | 351.7 | 84.4 | 607 | -12.8 | 2013 | 2020 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500.00 | 850 | 8PL GRDN 500.00 | 1 | 849-850-1 | 1385.6 | 1385.6 | 1081 | 1320.9 | 95.7 | 46 | 1385.6 | 883 | 1244.2 | 88.8 | 174 | -6.9 | 2014 | 2017 | 3 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 299.6 | 25
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230.00 | 20616 | BARNARD 115.00 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ROCK_SPRINGS | 546 | 8MCGUIRE | 719 | 8ANTIOCH | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1713 | 1824.1 | 94.1 | 73 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | 7.8 | 2015 | 2011 | -4 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 223.5 | 13.8
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 845 | 6E.DURHM 230.00 | 20076 | LEESVILL 230.00 | 1 | 845-20076-1 | 745 | 745 | 478.4 | 678.3 | 93.6 | 18 | 745 | 380.8 | 525.8 | 71.3 | 8 | -22.3 | 2015 | 2029 | 14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230.00 | 20124 | METHOD 230.00 | 1 | 20073-20124-1 | 637 | 637 | 373.5 | 573.6 | 92.6 | 18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230.00 | 20157 | HOMESTED 230.00 | 1 | 20066-20157-1 | 423 | 423 | 288.4 | 366.6 | 91.5 | 10 | 423 | 250 | 328.9 | 79 | 223 | -12.5 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20875 | LEE #1 13.800 | 1 | 20030-20875-1 | 111 | 111 | 100.3 | 100.3 | 90.4 | 2 | 111 | 84 | 105.6 | 95.1 | 707 | 4.7 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20976 | RICH EMC 13.800 | 1 | 20378-20976-1 | 325 | 325 | 292.1 | 292.1 | 89.9 | 1 | 325 | 307.8 | 315.2 | 97 | 679 | 7.1 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20039 | SUT 3 F 230.00 | 20868 | SUT #3 24.000 | 1 | 20039-20868-1 | 533 | 533 | 400.8 | 478.4 | 89.8 | 13 | 533 | 424 | 424 | 79.5 | 130 | -10.3 | 2017 | 2023 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MORNSTAR4 | 541 | 6MORN ST | 630 | MORN STR | 4 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 1 | 538-542-1 | 437 | 437 | 353.8 | 389 | 89.4 | 41 | 437 | 270.3 | 398.8 | 91.5 | 167 | 2.1 | 2017 | 2016 | -1 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20985 | ANSON 230.00 | 20986 | LILESEMC 13.800 | 1 | 20985-20986-1 | 390 | 390 | 348.6 | 348.6 | 89.4 | 4 | 390 | 344.9 | 375.5 | 96.3 | 873 | 6.9 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 537-540-1 | 318.6 | 318.6 | 165.7 | 289.1 | 89.2 | 49 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | 2 | 2017 | 2016 | -1 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 50.6 | 16.4
| DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 2 | 443-544-2 | 478 | 478 | 318.9 | 418.7 | 86.6 | 34 | 478 | 332.2 | 435.9 | 90.3 | 233 | 3.7 | 2019 | 2017 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 7.4 | 2
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 4 | 538-540-4 | 563.7 | 563.7 | 390 | 485.9 | 86.6 | 42 | 490.8 | 371.4 | 413.6 | 84.8 | 1054 | -1.8 | 2019 | 2027 | 8 |  | 490.8 | 563.7 | 540.2 | MECKLENBURG WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 563.7 | 333.5 | 415.6 | 73.7 | 70.3 | 12.9
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20885 | WSP #3 13.800 | 1 | 20047-20885-1 | 95 | 95 | 81.9 | 81.9 | 86.2 | 2 | 95 | 88.1 | 88.1 | 92.8 | 131 | 6.6 | 2019 | 2015 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230.00 | 20076 | LEESVILL 230.00 | 1 | 20073-20076-1 | 745 | 745 | 424 | 624 | 86.1 | 18 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2019 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230.00 | 20097 | CG-ROX 230.00 | 1 | 20070-20097-1 | 423 | 423 | 273.5 | 361.8 | 85.6 | 10 | 423 | 223.3 | 307.3 | 71.4 | 38 | -14.2 | 2019 | 2029 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20024 | ROX 1-4F 230.00 | 20870 | ROX #2 24.000 | 1 | 20024-20870-1 | 822 | 822 | 658.3 | 691.2 | 84.1 | 7 | 822 | 665.7 | 1679.8 | 204.4 | 5364 | 120.3 | 2020 | 2011 | -9 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20041 | CF 5-6 F 230.00 | 20053 | CAPE 5&6 115.00 | 1 | 20041-20053-1 | 350 | 350 | 293.9 | 293.9 | 84 | 1 | 350 | 315.2 | 323 | 92.3 | 257 | 8.3 | 2020 | 2016 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230.00 | 20079 | OXF S T 230.00 | 1 | 20070-20079-1 | 539 | 539 | 387 | 436.6 | 83.7 | 10 | 539 | 369.7 | 430.7 | 81 | 1638 | -2.7 | 2020 | 2022 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20089 | HENDERSN 115.00 | 20105 | FRANKLIN 115.00 | 1 | 20089-20105-1 | 201 | 201 | 132.7 | 155.2 | 83.6 | 4 | 201 | 118.3 | 161.4 | 86.9 | 429 | 3.3 | 2021 | 2019 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20876 | LEE #2 13.800 | 1 | 20030-20876-1 | 106 | 106 | 88.3 | 88.3 | 83.3 | 2 | 106 | 81.2 | 93.8 | 88.5 | 735 | 5.2 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL3 | 20734 | WATRE | 20723 | CAMD JCT | 1 | 20716 | CAMCTY02 115.00 | 20725 | CAMDEN 115.00 | 1 | 20716-20725-1 | 108 | 108 | 58.2 | 90.3 | 83.1 | 2 | 108 | 63.5 | 107.9 | 101.1 | 46 | 18 | 2021 | 2011 | -10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| WOODLAWN5 | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 388.3 | 587.1 | 82.9 | 47 | 717 | 415.6 | 628.2 | 89.3 | 174 | 6.4 | 2021 | 2017 | -4 |  | 717 | 717 | 717 | STEELBERRY | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 394.5 | 597 | 84.4 | -9.9 | -1.5
| BASE CASE | 0 |  | 0 |  |  | 20329 | RAMSEUR 69.000 | 20330 | I-RAMTEX 69.000 | 1 | 20329-20330-1 | 19 | 19 | 15.6 | 15.6 | 82.7 | 1 | 19 | 15.6 | 15.6 | 82 | 87 | -0.7 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230.00 | 445 | 6STAMEY 230.00 | 2 | 443-445-2 | 889 | 889 | 451.6 | 752.6 | 82.4 | 24 | 889 | 488.7 | 813.6 | 89.6 | 46 | 7.2 | 2021 | 2017 | -4 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | -2.5 | 0.8
| BASE CASE | 0 |  | 0 |  |  | 20020 | BRUN 2 N 230.00 | 20863 | BRUN #2 24.000 | 1 | 20020-20863-1 | 1067 | 1067 | 874.2 | 874.2 | 81.9 | 2 | 1067 | 959.5 | 959.5 | 89.9 | 130 | 8 | 2022 | 2017 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20632 | MARION 115.00 | 20654 | DILLON T 115.00 | 1 | 20632-20654-1 | 97 | 97 | 70.2 | 76.3 | 81.1 | 2 | 97 | 49.8 | 80.7 | 82.9 | 43 | 1.8 | 2022 | 2021 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20851 | ASHVL #1 18.000 | 1 | 20800-20851-1 | 235 | 235 | 190.7 | 190.7 | 81.1 | 2 | 235 | 191.6 | 191.6 | 81.6 | 130 | 0.5 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MORNSTAR_CAP | 5630 | MORN CAP | 630 | MORN STR | 1 | 20024 | ROX 1-4F 230.00 | 20872 | ROX #4 24.000 | 1 | 20024-20872-1 | 883 | 883 | 708.7 | 714.9 | 81 | 48 | 883 | 727 | 769.6 | 87.2 | 3191 | 6.2 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20018 | ROB 2 N 230.00 | 20864 | ROB #2 22.000 | 1 | 20018-20864-1 | 878 | 878 | 709.3 | 709.3 | 80.8 | 2 | 878 | 730.1 | 748 | 85.2 | 684 | 4.4 | 2022 | 2020 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| WOODLAWN4 | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 458 | 458 | 346.5 | 358.2 | 80.7 | 41 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 12.3 | 2022 | 2018 | -4 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | -9.3 | 1.8
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 845 | 6E.DURHM 230.00 | 20117 | DURHAM 230.00 | 1 | 845-20117-1 | 1014 | 1014 | 533 | 780.2 | 80.5 | 26 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20044 | ROB 1 F 115.00 | 20874 | ROB #1 18.000 | 1 | 20044-20874-1 | 244 | 244 | 159.1 | 196.1 | 80.4 | 5 | 244 | 174.5 | 186.9 | 76.6 | 173 | -3.8 | 2023 | 2025 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BEAVERWN | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 10250 | COLPIPTW 100.00 | 324 | CHEROKEE 100.00 | 1 | 324-10250-1 | 113.1 | 113.1 | 4.5 | 97 | 80.3 | 1 | 113.1 | 4 | 95.6 | 79.6 | 44 | -0.7 | 2023 | 2023 | 0 |  | 102.7 | 113.1 | 102.7 | BEAVER WHITE | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 1.6 | 93.6 | 78.6 | 3.4 | 1.7
| BASE CASE | 0 |  | 0 |  |  | 837 | 6ROWANG 230.00 | 840 | 6ROWANT 230.00 | 1 | 837-840-1 | 1200 | 1200 | 977 | 977 | 80.2 | 2 | 1110 | 977 | 977 | 86.7 | 175 | 6.5 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20883 | WSP #1 13.800 | 1 | 20047-20883-1 | 62 | 62 | 49.7 | 49.7 | 80.1 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 6.5 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20884 | WSP #2 13.800 | 1 | 20047-20884-1 | 62 | 62 | 49.7 | 49.7 | 80.1 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 6.5 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20871 | ROX #3 24.000 | 1 | 20024-20871-1 | 883 | 883 | 704.3 | 704.3 | 79.8 | 3 | 883 | 730.1 | 759.8 | 86.1 | 3445 | 6.3 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20350 | PH SH 1B 230.00 | 20985 | ANSON 230.00 | 1 | 20350-20985-1 | 398 | 398 | 285.2 | 310.9 | 79.7 | 23 | 398 | 180.9 | 315.2 | 77.6 | 123 | -2.1 | 2023 | 2024 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20349 | PH SH 2W 230.00 | 20985 | ANSON 230.00 | 1 | 20349-20985-1 | 398 | 398 | 284.7 | 310.3 | 79.6 | 28 | 398 | 180.3 | 314.6 | 77.5 | 117 | -2.1 | 2023 | 2024 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20877 | LEE #3 18.000 | 1 | 20030-20877-1 | 333 | 333 | 263.9 | 263.9 | 79.3 | 2 | 333 | 268.6 | 284 | 85.3 | 3097 | 6 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20869 | ROX #1 22.000 | 1 | 20024-20869-1 | 483 | 483 | 381.7 | 381.7 | 79 | 3 | 483 | 393.8 | 411.4 | 85.2 | 2109 | 6.2 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 412.9 | 660.3 | 78.6 | 15 | 840 | 498.3 | 796.6 | 94.8 | 78 | 16.2 | 2024 | 2014 | -10 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | -71 | -8.5
| MICHIEW | 845 | 6E.DURHM | 847 | 6PARKWOD | 1 | 843 | 6BRASFLD 230.00 | 847 | 6PARKWOD 230.00 | 1 | 843-847-1 | 478 | 478 | 263 | 366.9 | 78.5 | 29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | MICHIE | 230 kV Line | 575.9418 | 718.1349 | 575.9418 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20858 | ASHVCT#1 18.000 | 1 | 20800-20858-1 | 200 | 200 | 157 | 157 | 78.5 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20859 | ASHVCT#2 18.000 | 1 | 20800-20859-1 | 200 | 200 | 157 | 157 | 78.5 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 1 | 443-713-1 | 478 | 478 | 252.8 | 368 | 78.4 | 27 | 478 | 297.3 | 424.9 | 86.7 | 40 | 8.3 | 2024 | 2019 | -5 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 5.7 | 5.3
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 2 | 443-713-2 | 478 | 478 | 252.8 | 368 | 78.4 | 28 | 478 | 297.3 | 424.9 | 86.7 | 40 | 8.3 | 2024 | 2019 | -5 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 5.7 | 5.3
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 841 | 6BOBWH B 230.00 | 848 | 6PL GRDN 230.00 | 1 | 841-848-1 | 478 | 478 | 175.1 | 364.4 | 78.3 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 842 | 6BOBWH W 230.00 | 848 | 6PL GRDN 230.00 | 2 | 842-848-2 | 478 | 478 | 175.1 | 364.4 | 78.3 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20015 | MAYO 1F 500.00 | 20873 | MAYO #1 20.000 | 1 | 20015-20873-1 | 917 | 917 | 714.9 | 714.9 | 78 | 2 | 917 | 775.7 | 775.7 | 84.6 | 346 | 6.6 | 2024 | 2020 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20852 | ASHVL #2 20.000 | 1 | 20800-20852-1 | 235 | 235 | 181.8 | 181.8 | 77.4 | 2 | 235 | 185.6 | 379.2 | 161.4 | 548 | 84 | 2024 | 2011 | -13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PINOCAW | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 796.7 | 796.7 | 356.3 | 622.2 | 77.2 | 4 | 796.7 | 384.9 | 671.3 | 83.8 | 45 | 6.6 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA BLACK | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 340.3 | 594.8 | 74.1 | 27.4 | 3.1
| PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 356.3 | 622.2 | 77.2 | 4 | 796.7 | 384.9 | 671.3 | 83.8 | 46 | 6.6 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 340.3 | 594.8 | 74.1 | 27.4 | 3.1
| BASE CASE | 0 |  | 0 |  |  | 20265 | E15-STED 115.00 | 20401 | VANDER 115.00 | 1 | 20265-20401-1 | 163 | 163 | 123.8 | 123.8 | 77.2 | 1 | 163 | 103.6 | 126.5 | 79 | 204 | 1.8 | 2025 | 2023 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| YAD4 | 2511 | BADIN | 20343 | BADIN #2 | 1 | 20342 | BADIN #1 115.00 | 2511 | BADIN 100.00 | 1 | 2511-20342-1 | 100 | 100 | 49.8 | 77.1 | 77.1 | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20079 | OXF S T 230.00 | 20085 | OXFORD N 230.00 | 1 | 20079-20085-1 | 539 | 539 | 351.1 | 400.3 | 77 | 10 | 539 | 334.1 | 394.5 | 74.5 | 387 | -2.5 | 2025 | 2026 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 538-540-1 | 563.7 | 563.7 | 346.3 | 431.5 | 76.9 | 35 | 490.8 | 329.8 | 367.2 | 75.3 | 86 | -1.6 | 2025 | 2033 | 8 |  | 490.8 | 563.7 | 540.2 | CRAIGHEAD BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CRAIGHEADB | 540 | 6MCGUIRE | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 3 | 538-540-3 | 617.5 | 617.5 | 390 | 472.9 | 76.8 | 41 | 529.8 | 371.4 | 413.6 | 78.5 | 354 | 1.7 | 2025 | 2031 | 6 |  | 529.8 | 617.5 | 553.7 | MECKLENBURG BL | 230 kV Line | 556.9073 | 617.458 | 556.9073 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20222 | ROCKY MT 230.00 | 44591 | 6NASH 230.00 | 1 | 20222-44591-1 | 429 | 429 | 259.3 | 308.8 | 76.7 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| SCEG1 | 42012 | 6VCS #1 | 43002 | 6BLYTHEW | 1 | 20700 | SUMTER 230.00 | 42002 | 6WATEREE 230.00 | 1 | 20700-42002-1 | 500 | 500 | 324.8 | 388.1 | 76.7 | 15 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| SADLERB | 826 | 6ERNEST2 | 718 | 6SADLER | 1 | 718 | 6SADLER 230.00 | 826 | 6ERNEST2 230.00 | 2 | 718-826-2 | 717 | 717 | 316.4 | 558.1 | 76.6 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | 576 | 717 | 576 | SADLER | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| DUTCHOVERB | 543 | 6RIVRBEN | 441 | 6LINCOLN | 1 | 441 | 6LINCOLN 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 441-543-2 | 597.5 | 597.5 | 272.2 | 463.9 | 75.9 | 2 | 597.5 | 284.3 | 481.1 | 79.3 | 41 | 3.4 | 2025 | 2023 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 597.5 | 285.3 | 500.9 | 82.2 | -37 | -6.3
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 281.3 | 363 | 75.7 | 35 | 478 | 313.5 | 402.6 | 84.9 | 168 | 9.2 | 2026 | 2020 | -6 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 300.9 | 384.5 | 80.7 | -21.5 | -5
| YAD4 | 2511 | BADIN | 20343 | BADIN #2 | 1 | 20004 | TIL 1-4H 115.00 | 20342 | BADIN #1 115.00 | 1 | 20004-20342-1 | 100 | 100 | 49.8 | 77 | 75.7 | 6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20157 | HOMESTED 230.00 | 20160 | PINE LK 230.00 | 1 | 20157-20160-1 | 423 | 423 | 223.4 | 301.8 | 75.5 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| YAD3 | 2511 | BADIN | 20342 | BADIN #1 | 1 | 20343 | BADIN #2 115.00 | 2511 | BADIN 100.00 | 1 | 2511-20343-1 | 100 | 100 | 47.3 | 75.3 | 75.3 | 7 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ALBRIGHTB | 844 | 6ENO | 848 | 6PL GRDN | 1 | 844 | 6ENO 230.00 | 848 | 6PL GRDN 230.00 | 2 | 844-848-2 | 478 | 478 | 291.9 | 360.2 | 75.1 | 31 | 478 | 223.8 | 382.2 | 82 | 44 | 6.9 | 2026 | 2022 | -4 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20009 | HARRIS1N 230.00 | 20865 | HARRIS#1 22.000 | 1 | 20009-20865-1 | 1120 | 1120 | 840.5 | 840.5 | 75 | 2 | 1120 | 921.6 | 921.6 | 82.3 | 319 | 7.3 | 2026 | 2021 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20145 | NEUSE 115.00 | 20185 | FALLS 115.00 | 1 | 20145-20185-1 | 201 | 201 | 131 | 139.6 | 74.9 | 2 | 201 | 117.9 | 147.4 | 75.7 | 128 | 0.8 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 1 | 712-719-1 | 840 | 840 | 344.3 | 625.3 | 74.4 | 2 | 840 | 415.6 | 754.3 | 89.8 | 41 | 15.4 | 2026 | 2017 | -9 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | -67.4 | -8.1
| LONGVIEW1 | 442 | 6LONGVW | 2630 | LONGV 1 | 1 | 442 | 6LONGVW 230.00 | 2633 | LONGV 4 1.0000 | 4 | 442-2633-4 | 478 | 478 | 263.2 | 355.1 | 74.3 | 17 | 478 | 280.9 | 378.9 | 79.3 | 88 | 5 | 2027 | 2023 | -4 |  | 478 | 478 | 478 | LONGVIEW TIE 04 | 230/100/44 kV Transformer | 520.9 | 597.7 | 560.6 | 478 | 259.6 | 350.2 | 73.3 | 4.9 | 1
| PISGHBK2 | 108 | 6PISGAH | 2666 | PISGA 2 | 2 | 209 | 3MILLSRV 115.00 | 20800 | ASHEVIL 115.00 | 1 | 209-20800-1 | 207 | 207 | 140.9 | 155.1 | 73.9 | 12 | 207 | 131 | 163.4 | 78.8 | 95 | 4.9 | 2027 | 2024 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| YAD3 | 2511 | BADIN | 20342 | BADIN #1 | 1 | 20004 | TIL 1-4H 115.00 | 20343 | BADIN #2 115.00 | 1 | 20004-20343-1 | 100 | 100 | 47.3 | 75.3 | 73.9 | 6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| KIMBRELLB | 331 | 6ALLEN | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 1 | 443-544-1 | 478 | 478 | 318.9 | 358.6 | 73.6 | 33 | 478 | 327 | 368.6 | 76.1 | 189 | 2.5 | 2027 | 2025 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 342.8 | 70 | 15.8 | 3.6
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20162 | MILBURNE 230.00 | 20182 | FALLS 230.00 | 1 | 20162-20182-1 | 423 | 423 | 255.8 | 293.7 | 73.5 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20024 | ROX 1-4F 230.00 | 20182 | FALLS 230.00 | 1 | 20024-20182-1 | 539 | 539 | 293.4 | 373.3 | 73.4 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20035 | SUT 1-2F 115.00 | 20867 | SUT #2 13.800 | 1 | 20035-20867-1 | 142 | 142 | 96.4 | 104.2 | 73.4 | 3 | 142 | 106.1 | 117.2 | 82.6 | 341 | 9.2 | 2027 | 2021 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230.00 | 265 | 6RIVERVW 230.00 | 2 | 236-265-2 | 452.5 | 452.5 | 227 | 336.2 | 73.3 | 19 | 452.5 | 287.6 | 425.5 | 93.6 | 52 | 20.3 | 2027 | 2015 | -12 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -84.6 | -18.1
| BASE CASE | 0 |  | 0 |  |  | 112 | 8BAD CRK 500.00 | 113 | 8JOCASSE 500.00 | 1 | 112-113-1 | 1790.9 | 1790.9 | 1396.3 | 1396.3 | 73.1 | 2 | 1732 | 1396.9 | 1396.9 | 75.9 | 84 | 2.8 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | 1397.7 | 1397.7 | 73 | -1.4 | 0.1
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 105 | 6SHADYTW 230.00 | 109 | 6SHADY G 230.00 | 2 | 105-109-2 | 478 | 478 | 216.2 | 346.8 | 72.8 | 3 | 478 | 244.5 | 391.9 | 83.3 | 44 | 10.5 | 2028 | 2021 | -7 |  | 477.96 | 477.96 | 477.96 | SHADY GROVE | 230 kV Line | 859.9297 | 1008.8939 | 859.9297 | 478 | 214.7 | 346.1 | 73.3 | 0.7 | -0.5
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 848 | 6PL GRDN 230.00 | 1 | 713-848-1 | 478 | 478 | 128.4 | 340.4 | 72.5 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | 436.9351 | 477.96 | 436.9351 | FAGO | 230 kV Line | 458.045 | 506.6376 | 458.045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 848 | 6PL GRDN 230.00 | 2 | 713-848-2 | 478 | 478 | 128.4 | 340.4 | 72.5 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2028 | #N/A | #N/A |  | 436.9351 | 477.96 | 436.9351 | FAGO | 230 kV Line | 458.045 | 506.6376 | 458.045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20977 | RICH CC1 18.000 | 1 | 20378-20977-1 | 660 | 660 | 477.5 | 477.5 | 72.3 | 1 | 660 | 510 | 516 | 78.2 | 1433 | 5.9 | 2028 | 2024 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20004 | TIL 1-4H 115.00 | 20302 | E14-TROY 115.00 | 1 | 20004-20302-1 | 269 | 269 | 175 | 184.6 | 70.7 | 14 | 269 | 133.3 | 217.9 | 80.3 | 86 | 9.6 | 2029 | 2023 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20053 | CAPE 5&6 115.00 | 20879 | CAPE #6 18.000 | 1 | 20053-20879-1 | 233 | 233 | 163.3 | 163.3 | 70.1 | 2 | 233 | 174.7 | 174.7 | 75 | 130 | 4.9 | 2029 | 2026 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20182 | FALLS 230.00 | 20185 | FALLS 115.00 | 1 | 20182-20185-1 | 300 | 300 | 210.2 | 210.2 | 70.1 | 5 | 300 | 214.6 | 311.1 | 103.7 | 1807 | 33.6 | 2029 | 2011 | -18 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 7 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 8 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1535.4 | 113.7 | 42 | 1350 | - | 1123.1 | 83.2 | 910 | -30.5 | 2011 | 2021 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1840.4 | 96.6 | 42 | 1904.3 | - | 1909.2 | 100.3 | 910 | 3.7 | 2013 | 2011 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 299.3 | 15.7
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 83.4 | 87.8 | 42 | 95 | - | 88.1 | 92.7 | 910 | 4.9 | 2018 | 2015 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 336.6 | 86.3 | 21 | 390 | - | 349.5 | 89.6 | 455 | 3.3 | 2019 | 2017 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 95.5 | 86 | 42 | 111 | - | 85.1 | 76.6 | 910 | -9.4 | 2019 | 2025 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 896.3 | 84 | 42 | 1067 | - | 985.6 | 92.4 | 910 | 8.4 | 2020 | 2015 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 51.1 | 82.4 | 42 | 62 | - | 54.2 | 87.4 | 910 | 5 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 51.1 | 82.4 | 42 | 62 | - | 54.2 | 87.4 | 910 | 5 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 193.1 | 82.2 | 42 | 235 | - | 192.2 | 81.8 | 910 | -0.4 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG1 | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 458 | 458 | - | 370.6 | 80.9 | 42 | 458 | - | 364 | 79.5 | 910 | -1.4 | 2022 | 2023 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 458 | - | 347.6 | 75.9 | 23 | 5
STUDYL | THRP | - | - | - | - | - | 538 | 6HARRISB | 542 | 6OAKBORO | 1 | 538-542-1 | 437 | 437 | - | 352.9 | 80.8 | 42 | 437 | - | 270.3 | 61.9 | 854 | -18.9 | 2022 | 2036 | 14 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 235.4 | 53.9 | 117.5 | 26.9
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 85.7 | 80.8 | 42 | 106 | - | 82.3 | 77.7 | 910 | -3.1 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 700.4 | 79.8 | 42 | 878 | - | 735.9 | 83.8 | 910 | 4 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 185 | 78.7 | 42 | 235 | - | 187.5 | 79.8 | 910 | 1.1 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 260.5 | 78.2 | 42 | 333 | - | 271.7 | 81.6 | 910 | 3.4 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 687.9 | 77.9 | 42 | 883 | - | 727.4 | 82.4 | 910 | 4.5 | 2024 | 2021 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.3 | 77.7 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.3 | 77.7 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 638.2 | 77.6 | 42 | 822 | - | 667.2 | 81.2 | 910 | 3.6 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 865.4 | 77.3 | 42 | 1120 | - | 935.6 | 83.5 | 910 | 6.2 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 849-850-1 | 1385.6 | 1385.6 | - | 1070.4 | 77.2 | 21 | 1385.6 | - | 904.6 | 65.3 | 455 | -11.9 | 2025 | 2033 | 8 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | - | 732.8 | 52.9 | 337.6 | 24.3
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 681.8 | 77.2 | 42 | 883 | - | 729.3 | 82.6 | 910 | 5.4 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 700.8 | 76.4 | 42 | 917 | - | 752.8 | 82.1 | 910 | 5.7 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 368.4 | 76.3 | 42 | 483 | - | 394.7 | 81.7 | 910 | 5.4 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 359 | 75.1 | 42 | 478 | - | 353.9 | 74.1 | 872 | -1 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 59.1 | 12.3
STUDYL | THRP | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 359 | 75.1 | 42 | 478 | - | 353.9 | 74.1 | 872 | -1 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 59.1 | 12.3
STUDYL | BEL1 | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 400.4 | 75.1 | 42 | 533 | - | 427.6 | 80.2 | 910 | 5.1 | 2026 | 2023 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1300 | 1300 | - | 972.1 | 74.8 | 21 | 1300 | - | 979.5 | 75.3 | 455 | 0.5 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO3 | - | - | - | - | - | 112 | 8BAD CRK | 113 | 8JOCASSE | 1 | 112-113-1 | 1790.9 | 1790.9 | - | 1313.8 | 73.4 | 21 | 1790.9 | - | 1319 | 73.7 | 454 | 0.3 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | - | 1308.4 | 73.1 | 5.4 | 0.3
STUDYL | CAT1 | - | - | - | - | - | 209 | 3MILLSRV | 20800 | ASHEVIL | 1 | 209-20800-1 | 207 | 207 | - | 147.6 | 71.3 | 42 | 207 | - | 139.4 | 67.3 | 910 | -4 | 2029 | 2031 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 443 | 6MARSHAL | 713 | 6BECKRDT | 1 | 443-713-1 | 437 | 437 | - | 309.3 | 70.8 | 80 | 437 | - | 349.7 | 80 | 1436 | 9.2 | 2029 | 2023 | -6 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 306.2 | 70.1 | 3.1 | 0.7
STUDYL | THRP | - | - | - | - | - | 20349 | PH SH 2W | 20985 | ANSON | 1 | 20349-20985-1 | 400 | 400 | - | 281.2 | 70.3 | 42 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 4 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_Brun1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1378.9 | 102.1 | 2 | 1350 | - | 966.8 | 71.6 | 42 | -30.5 | 2011 | 2028 | 17 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 141.1 | 94.1 | 1 | 150 | - | 142.5 | 95 | 21 | 0.9 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.2 | 93.1 | 2 | 40 | - | 36.8 | 92.1 | 42 | -1 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 83.1 | 87.5 | 2 | 95 | - | 88.1 | 92.7 | 42 | 5.2 | 2018 | 2015 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 81.9 | #N/A | 83.4
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 280.9 | 86.4 | 2 | 325 | - | 293 | 90.2 | 42 | 3.8 | 2019 | 2017 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 292.1 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 95.4 | 86 | 2 | 111 | - | 84.1 | 75.8 | 42 | -10.2 | 2019 | 2025 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 100.3 | #N/A | 95.5
STUDYL | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 897.3 | 84.1 | 2 | 1067 | - | 985.7 | 92.4 | 42 | 8.3 | 2020 | 2015 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 874.2 | #N/A | 896.3
STUDYL | BADX | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 327.2 | 83.9 | 1 | 390 | - | 344.7 | 88.4 | 21 | 4.5 | 2020 | 2018 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 348.6 | #N/A | 336.6
STUDYL | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 293.2 | 83.8 | 1 | 350 | - | 316.1 | 90.3 | 21 | 6.5 | 2020 | 2017 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 293.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1580.7 | 83 | 2 | 1904.3 | - | 1636.2 | 85.9 | 42 | 2.9 | 2021 | 2019 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1279.9 | 67.2 | 300.8 | 15.8 | 1824.1 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20329 | RAMSEUR | 20330 | I-RAMTEX | 1 | 20329-20330-1 | 19 | 19 | - | 15.6 | 82.3 | 2 | 19 | - | 15.6 | 81.9 | 42 | -0.4 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 15.6 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 50.9 | 82.1 | 2 | 62 | - | 54.2 | 87.4 | 42 | 5.3 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.7 | #N/A | 51.1
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 50.9 | 82.1 | 2 | 62 | - | 54.2 | 87.4 | 42 | 5.3 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.7 | #N/A | 51.1
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 191.9 | 81.7 | 2 | 235 | - | 192.4 | 81.9 | 42 | 0.2 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 190.7 | #N/A | 193.1
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 85.6 | 80.8 | 2 | 106 | - | 81.3 | 76.7 | 42 | -4.1 | 2022 | 2025 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.3 | #N/A | 85.7
STUDYL | BADX | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 701.2 | 79.9 | 2 | 878 | - | 736.3 | 83.9 | 42 | 4 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 709.3 | #N/A | 700.4
STUDYL | BADX | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1200 | 1200 | - | 956 | 79.7 | 1 | 1200 | - | 955.1 | 79.6 | 21 | -0.1 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | - | 622.5 | 51.9 | 333.5 | 27.8 | 977 | #N/A | 972.1
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 260.5 | 78.2 | 2 | 333 | - | 268.8 | 80.7 | 42 | 2.5 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 263.9 | #N/A | 260.5
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 183.5 | 78.1 | 2 | 235 | - | 186.8 | 79.5 | 42 | 1.4 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 181.8 | #N/A | 185
STUDYL | BADX | - | - | - | - | - | 20009 | HARRIS1N | 20865 | HARRIS#1 | 1 | 20009-20865-1 | 1120 | 1120 | - | 865.7 | 77.3 | 2 | 1120 | - | 935.3 | 83.5 | 42 | 6.2 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 840.5 | #N/A | 865.4
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 154.4 | 77.2 | 2 | 200 | - | 155 | 77.5 | 42 | 0.3 | 2025 | 2024 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 157 | #N/A | 155.3
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 154.4 | 77.2 | 2 | 200 | - | 155 | 77.5 | 42 | 0.3 | 2025 | 2024 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 157 | #N/A | 155.3
STUDYL | BADX | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 702.2 | 76.6 | 2 | 917 | - | 753.5 | 82.2 | 42 | 5.6 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 714.9 | #N/A | 700.8
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 629.9 | 76.6 | 2 | 822 | - | 661.7 | 80.5 | 42 | 3.9 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 691.2 | #N/A | 638.2
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 676.2 | 76.6 | 2 | 883 | - | 712.3 | 80.7 | 42 | 4.1 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 704.3 | #N/A | 681.8
STUDYL | BADX | - | - | - | - | - | 20632 | MARION | 20654 | DILLON T | 1 | 20632-20654-1 | 97 | 97 | - | 74.3 | 76.6 | 1 | 97 | - | 53.3 | 54.9 | 21 | -21.7 | 2025 | 2042 | 17 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 76.3 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 674 | 76.3 | 2 | 883 | - | 712.6 | 80.7 | 42 | 4.4 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 714.9 | #N/A | 687.9
STUDYL | BADX | - | - | - | - | - | 20265 | E15-STED | 20401 | VANDER | 1 | 20265-20401-1 | 163 | 163 | - | 124.4 | 76.3 | 2 | 163 | - | 102.7 | 63 | 42 | -13.3 | 2025 | 2035 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 123.8 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 366.1 | 75.8 | 2 | 483 | - | 385.5 | 79.8 | 42 | 4 | 2025 | 2023 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 381.7 | #N/A | 368.4
STUDYL | BADX | - | - | - | - | - | 20066 | FALLS23 | 20097 | CG-ROX | 1 | 20066-20097-1 | 423 | 423 | - | 315.5 | 74.6 | 2 | 423 | - | 272.8 | 64.5 | 42 | -10.1 | 2026 | 2034 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 389.6 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 354.3 | 74.1 | 2 | 478 | - | 349.9 | 73.2 | 42 | -0.9 | 2027 | 2027 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 57.6 | 12 | 464.8 | #N/A | 359
STUDYL | BADX | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 354.3 | 74.1 | 2 | 478 | - | 349.9 | 73.2 | 42 | -0.9 | 2027 | 2027 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 57.6 | 12 | 464.8 | #N/A | 359
STUDYL | BADX | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 393.9 | 73.9 | 2 | 533 | - | 427.8 | 80.3 | 42 | 6.4 | 2027 | 2023 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 478.4 | #N/A | 400.4
STUDYL | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 69.8 | 72.7 | 1 | 96 | - | 81.3 | 84.7 | 21 | 12 | 2028 | 2020 | -8 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | -3.7 | -3.9 | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 849-850-1 | 1385.6 | 1385.6 | - | 1005.5 | 72.6 | 1 | 1385.6 | - | 843.3 | 60.9 | 21 | -11.7 | 2028 | 2037 | 9 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1320.9 | #N/A | 1070.4
STUDYL | BADX | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 478 | 478 | - | 344.9 | 72.2 | 2 | 478 | - | 344 | 72 | 42 | -0.2 | 2028 | 2028 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | - | 328.3 | 68.7 | 16.6 | 3.5 | 358.2 | #N/A | 370.6
STUDYL | BADX | - | - | - | - | - | 20070 | PERSON | 20079 | OXF S T | 1 | 20070-20079-1 | 539 | 539 | - | 386.5 | 71.7 | 1 | 539 | - | 367.6 | 68.2 | 21 | -3.5 | 2028 | 2031 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 436.6 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20182 | FALLS | 20185 | FALLS | 1 | 20182-20185-1 | 300 | 300 | - | 213.3 | 71.1 | 1 | 300 | - | 215 | 71.7 | 21 | 0.6 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 210.2 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 209 | 3MILLSRV | 20800 | ASHEVIL | 1 | 209-20800-1 | 207 | 207 | - | 145.3 | 70.2 | 2 | 207 | - | 136.6 | 66 | 42 | -4.2 | 2029 | 2032 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 155.1 | #N/A | 147.6
Populate Summary Worksheet

## PEC TRM HR Down 1200 DKCPLE
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 26 | > 5% worse
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 14 | Not in original screening
[25 empty] | 40 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 337 | 8NEWPORT 500.00 | 20377 | RICHMOND 500.00 | 1 | 337-20377-1 | 1350 | 1350 | 1537.5 | 1764.6 | 134.9 | 47 | 1350 | 1164 | 1448.3 | 105.4 | 8993 | -29.5 | 2011 | 2011 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 561.4 | 959.1 | 120.4 | 24 | 796.7 | 474 | 811.3 | 101.8 | 88 | -18.6 | 2011 | 2011 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 390.3 | 670 | 84.1 | 289.1 | 36.3
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20350 | PH SH 1B 230.00 | 20985 | ANSON 230.00 | 1 | 20350-20985-1 | 398 | 398 | 281.3 | 451.6 | 118.5 | 23 | 398 | 180.9 | 315.2 | 77.6 | 123 | -40.9 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20349 | PH SH 2W 230.00 | 20985 | ANSON 230.00 | 1 | 20349-20985-1 | 398 | 398 | 280.8 | 450.8 | 118.3 | 26 | 398 | 180.3 | 314.6 | 77.5 | 117 | -40.8 | 2011 | 2024 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 542.2 | 950.6 | 113.2 | 23 | 840 | 457.8 | 804.1 | 95.7 | 80 | -17.5 | 2011 | 2014 | 3 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 377 | 664 | 79.1 | 286.6 | 34.1
| HARRISBURGB | 542 | 6OAKBORO | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 2 | 538-542-2 | 482 | 482 | 352.7 | 522 | 108.3 | 43 | 437 | 270.3 | 398.8 | 91.5 | 211 | -16.8 | 2011 | 2021 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 482 | 236.8 | 349.9 | 72.2 | 172.1 | 36.1
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1736.2 | 1940.9 | 105.1 | 77 | 1904.3 | 1783.1 | 1971.6 | 101.9 | 7742 | -3.2 | 2011 | 2011 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1444.4 | 1600.6 | 80.3 | 340.3 | 24.8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 538 | 6HARRISB 230.00 | 542 | 6OAKBORO 230.00 | 1 | 538-542-1 | 482 | 482 | 352.7 | 478.4 | 101.8 | 42 | 437 | 270.3 | 398.8 | 91.5 | 167 | -10.3 | 2011 | 2021 | 10 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.6 | 110.2 | 101.8 | 6 | 108.3 | 56 | 100.1 | 92.4 | 43 | -9.4 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 49.9 | 89.5 | 82.7 | 20.7 | 19.1
| HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.6 | 110.2 | 101.8 | 6 | 108.3 | 56 | 100.1 | 92.4 | 43 | -9.4 | 2011 | 2015 | 4 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 49.9 | 89.5 | 82.7 | 20.7 | 19.1
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20004 | TIL 1-4H 115.00 | 20342 | BADIN #1 115.00 | 1 | 20004-20342-1 | 100 | 100 | 56.7 | 99.5 | 101.1 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 845 | 6E.DURHM 230.00 | 20076 | LEESVILL 230.00 | 1 | 845-20076-1 | 745 | 745 | 512.9 | 723 | 100.7 | 20 | 745 | 380.8 | 525.8 | 71.3 | 8 | -29.4 | 2011 | 2029 | 18 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230.00 | 20124 | METHOD 230.00 | 1 | 20073-20124-1 | 637 | 637 | 407.8 | 617.9 | 100.7 | 19 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2011 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20342 | BADIN #1 115.00 | 2511 | BADIN 100.00 | 1 | 2511-20342-1 | 100 | 100 | 56.7 | 99.6 | 99.6 | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2012 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 367.5 | 467.7 | 99.4 | 25 | 478 | 359.8 | 449 | 92.9 | 376 | -6.5 | 2012 | 2015 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 82.8 | 21
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 367.5 | 467.7 | 99.4 | 26 | 478 | 360 | 449 | 92.9 | 419 | -6.5 | 2012 | 2015 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 306.6 | 384.9 | 78.4 | 82.8 | 21
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230.00 | 20097 | CG-ROX 230.00 | 1 | 20066-20097-1 | 423 | 423 | 313.1 | 390.7 | 98 | 10 | 423 | 272.9 | 351.7 | 84.4 | 607 | -13.6 | 2013 | 2020 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 849 | 8PARKWOD 500.00 | 850 | 8PL GRDN 500.00 | 1 | 849-850-1 | 1385.6 | 1385.6 | 1103.5 | 1338.7 | 97.8 | 47 | 1385.6 | 883 | 1244.2 | 88.8 | 174 | -9 | 2013 | 2017 | 4 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | 723.5 | 1021.3 | 70.7 | 317.4 | 27.1
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20004 | TIL 1-4H 115.00 | 20343 | BADIN #2 115.00 | 1 | 20004-20343-1 | 100 | 100 | 53.8 | 94.5 | 96 | 8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 537 | 6COWANS1 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 537-540-1 | 318.6 | 318.6 | 174 | 308.2 | 95.4 | 74 | 318.6 | 163.1 | 295.6 | 91.2 | 44 | -4.2 | 2014 | 2016 | 2 |  | 306.691 | 318.64 | 318.64 | COWANS FORD | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | 163 | 238.5 | 72.8 | 69.7 | 22.6
| BASE CASE | 0 |  | 0 |  |  | 20615 | BARNARD 230.00 | 20616 | BARNARD 115.00 | 1 | 20615-20616-1 | 150 | 150 | 142.9 | 142.9 | 95.3 | 1 | 150 | 142.9 | 142.9 | 95.3 | 87 | 0 | 2014 | 2014 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20343 | BADIN #2 115.00 | 2511 | BADIN 100.00 | 1 | 2511-20343-1 | 100 | 100 | 53.8 | 94.6 | 94.6 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2014 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20004 | TIL 1-4H 115.00 | 20302 | E14-TROY 115.00 | 1 | 20004-20302-1 | 269 | 269 | 194.8 | 234.2 | 93.3 | 24 | 269 | 133.3 | 217.9 | 80.3 | 86 | -13 | 2015 | 2023 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| EDURHAMTIE4 | 845 | 6E.DURHM | 20117 | DURHAM | 1 | 20073 | BLUE RDG 230.00 | 20076 | LEESVILL 230.00 | 1 | 20073-20076-1 | 745 | 745 | 458.5 | 668.7 | 93.1 | 19 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2015 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20066 | FALLS23 230.00 | 20157 | HOMESTED 230.00 | 1 | 20066-20157-1 | 423 | 423 | 289.6 | 367.7 | 92.3 | 11 | 423 | 250 | 328.9 | 79 | 223 | -13.3 | 2016 | 2023 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 478 | 478 | 347.9 | 412.3 | 91.2 | 42 | 436.9 | 342.4 | 390.1 | 93 | 2107 | 1.8 | 2016 | 2020 | 4 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 330.1 | 367.5 | 78.9 | 44.8 | 12.3
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20302 | E14-TROY 115.00 | 20683 | BURNETTE 115.00 | 1 | 20302-20683-1 | 269 | 269 | 183 | 226.4 | 90.2 | 15 | 269 | 124.3 | 206.1 | 77.4 | 86 | -12.8 | 2017 | 2024 | 7 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20875 | LEE #1 13.800 | 1 | 20030-20875-1 | 111 | 111 | 100.1 | 100.1 | 90.2 | 2 | 111 | 84 | 105.6 | 95.1 | 707 | 4.9 | 2017 | 2014 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20976 | RICH EMC 13.800 | 1 | 20378-20976-1 | 325 | 325 | 291.3 | 291.3 | 89.6 | 1 | 325 | 307.8 | 315.2 | 97 | 679 | 7.4 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20039 | SUT 3 F 230.00 | 20868 | SUT #3 24.000 | 1 | 20039-20868-1 | 533 | 533 | 394.1 | 477.2 | 89.5 | 18 | 533 | 424 | 424 | 79.5 | 130 | -10 | 2017 | 2023 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20106 | WAKEFORE 115.00 | 20107 | E18-WEMC 69.000 | 1 | 20106-20107-1 | 40 | 40 | 35.7 | 35.7 | 89.3 | 1 | 40 | 35.7 | 35.7 | 89.3 | 87 | 0 | 2017 | 2017 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20985 | ANSON 230.00 | 20986 | LILESEMC 13.800 | 1 | 20985-20986-1 | 390 | 390 | 347.6 | 347.6 | 89.1 | 2 | 390 | 344.9 | 375.5 | 96.3 | 873 | 7.2 | 2017 | 2013 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| DOOLEYB | 443 | 6MARSHAL | 544 | 6WINECOF | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 2 | 443-544-2 | 478 | 478 | 319.4 | 419.2 | 86.8 | 35 | 478 | 332.2 | 435.9 | 90.3 | 233 | 3.5 | 2019 | 2017 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 411.3 | 84.6 | 7.9 | 2.2
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 4 | 538-540-4 | 563.7 | 563.7 | 389.9 | 485.9 | 86.7 | 43 | 490.8 | 371.4 | 413.6 | 84.8 | 1054 | -1.9 | 2019 | 2027 | 8 |  | 490.8 | 563.7 | 540.2 | MECKLENBURG WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 563.7 | 333.5 | 415.6 | 73.7 | 70.3 | 13
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230.00 | 20097 | CG-ROX 230.00 | 1 | 20070-20097-1 | 423 | 423 | 276.3 | 364.2 | 86.4 | 10 | 423 | 223.3 | 307.3 | 71.4 | 38 | -15 | 2019 | 2029 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20024 | ROX 1-4F 230.00 | 20870 | ROX #2 24.000 | 1 | 20024-20870-1 | 822 | 822 | 665.6 | 708.6 | 86.2 | 15 | 822 | 665.7 | 1679.8 | 204.4 | 5364 | 118.2 | 2019 | 2011 | -8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20885 | WSP #3 13.800 | 1 | 20047-20885-1 | 95 | 95 | 81.7 | 81.7 | 86 | 2 | 95 | 88.1 | 88.1 | 92.8 | 131 | 6.8 | 2019 | 2015 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20301 | TROY 115.00 | 20683 | BURNETTE 115.00 | 1 | 20301-20683-1 | 269 | 269 | 170 | 212.5 | 85.5 | 16 | 269 | 112.5 | 193.3 | 73 | 47 | -12.5 | 2019 | 2027 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20041 | CF 5-6 F 230.00 | 20053 | CAPE 5&6 115.00 | 1 | 20041-20053-1 | 350 | 350 | 295.4 | 295.4 | 84.4 | 1 | 350 | 315.2 | 323 | 92.3 | 257 | 7.9 | 2020 | 2016 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20632 | MARION 115.00 | 20654 | DILLON T 115.00 | 1 | 20632-20654-1 | 97 | 97 | 65.4 | 78.7 | 84.4 | 3 | 97 | 49.8 | 80.7 | 82.9 | 43 | -1.5 | 2020 | 2021 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20089 | HENDERSN 115.00 | 20105 | FRANKLIN 115.00 | 1 | 20089-20105-1 | 201 | 201 | 133.4 | 155.8 | 84.3 | 6 | 201 | 118.3 | 161.4 | 86.9 | 429 | 2.6 | 2020 | 2019 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 845 | 6E.DURHM 230.00 | 20117 | DURHAM 230.00 | 1 | 845-20117-1 | 1014 | 1014 | 561 | 805.9 | 83.8 | 29 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2020 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20348 | RKH 230.00 | 20350 | PH SH 1B 230.00 | 1 | 20348-20350-1 | 540 | 540 | 281.4 | 452.6 | 83.8 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2020 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20348 | RKH 230.00 | 20349 | PH SH 2W 230.00 | 1 | 20348-20349-1 | 540 | 540 | 280.8 | 451.8 | 83.7 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2020 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20876 | LEE #2 13.800 | 1 | 20030-20876-1 | 106 | 106 | 88.1 | 88.1 | 83.1 | 2 | 106 | 81.2 | 93.8 | 88.5 | 735 | 5.4 | 2021 | 2018 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| STAMEYB | 443 | 6MARSHAL | 445 | 6STAMEY | 1 | 443 | 6MARSHAL 230.00 | 445 | 6STAMEY 230.00 | 2 | 443-445-2 | 889 | 889 | 454.3 | 757 | 83 | 26 | 889 | 488.7 | 813.6 | 89.6 | 46 | 6.6 | 2021 | 2017 | -4 |  | 701 | 889 | 725 | STAMEY WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 889 | 451.2 | 755.1 | 81.6 | 1.9 | 1.4
| MICHIEW | 845 | 6E.DURHM | 847 | 6PARKWOD | 1 | 843 | 6BRASFLD 230.00 | 847 | 6PARKWOD 230.00 | 1 | 843-847-1 | 478 | 478 | 273.8 | 382.6 | 82.3 | 32 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2021 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | MICHIE | 230 kV Line | 575.9418 | 718.1349 | 575.9418 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20022 | BRUN 1 N 230.00 | 20862 | BRUN #1 24.000 | 1 | 20022-20862-1 | 1067 | 1067 | 868.4 | 876.8 | 82.2 | 6 | 1067 | 964.9 | 964.9 | 90.4 | 130 | 8.2 | 2021 | 2017 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20020 | BRUN 2 N 230.00 | 20863 | BRUN #2 24.000 | 1 | 20020-20863-1 | 1067 | 1067 | 870.9 | 870.9 | 81.6 | 2 | 1067 | 959.5 | 959.5 | 89.9 | 130 | 8.3 | 2022 | 2017 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20070 | PERSON 230.00 | 20079 | OXF S T 230.00 | 1 | 20070-20079-1 | 539 | 539 | 374.8 | 424.5 | 81.3 | 11 | 539 | 369.7 | 430.7 | 81 | 1638 | -0.3 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 542 | 6OAKBORO 230.00 | 20248 | I-ANSONV 230.00 | 1 | 542-20248-1 | 398 | 398 | 143.8 | 309.3 | 81.1 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL3 | 20734 | WATRE | 20723 | CAMD JCT | 1 | 20716 | CAMCTY02 115.00 | 20725 | CAMDEN 115.00 | 1 | 20716-20725-1 | 108 | 108 | 59 | 88.2 | 81.1 | 2 | 108 | 63.5 | 107.9 | 101.1 | 46 | 20 | 2022 | 2011 | -11 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20851 | ASHVL #1 18.000 | 1 | 20800-20851-1 | 235 | 235 | 190.7 | 190.7 | 81.1 | 2 | 235 | 191.6 | 191.6 | 81.6 | 130 | 0.5 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 844 | 6ENO 230.00 | 848 | 6PL GRDN 230.00 | 1 | 844-848-1 | 478 | 478 | 300.6 | 353.4 | 80.9 | 31 | 478 | 223.9 | 382.2 | 82 | 44 | 1.1 | 2022 | 2022 | 0 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 844 | 6ENO 230.00 | 848 | 6PL GRDN 230.00 | 2 | 844-848-2 | 478 | 478 | 300.6 | 353.4 | 80.9 | 32 | 478 | 223.8 | 382.2 | 82 | 44 | 1.1 | 2022 | 2022 | 0 |  | 437 | 478 | 437 | ALBRIGHT | 230 kV Line | 458.114 | 506.7139 | 458.114 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20314 | E3-CTRCH 230.00 | 20361 | WEST END 230.00 | 1 | 20314-20361-1 | 507 | 507 | 345.6 | 387 | 80.8 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20872 | ROX #4 24.000 | 1 | 20024-20872-1 | 883 | 883 | 712.6 | 712.6 | 80.7 | 3 | 883 | 727 | 769.6 | 87.2 | 3191 | 6.5 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 841 | 6BOBWH B 230.00 | 848 | 6PL GRDN 230.00 | 1 | 841-848-1 | 478 | 478 | 178.9 | 369.1 | 80.5 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 842 | 6BOBWH W 230.00 | 848 | 6PL GRDN 230.00 | 2 | 842-848-2 | 478 | 478 | 178.9 | 369.1 | 80.5 | 3 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2022 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 765.1343 | 851.5654 | 765.1343 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20018 | ROB 2 N 230.00 | 20864 | ROB #2 22.000 | 1 | 20018-20864-1 | 878 | 878 | 706.9 | 706.9 | 80.5 | 2 | 878 | 730.1 | 748 | 85.2 | 684 | 4.7 | 2022 | 2020 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 542 | 6OAKBORO 230.00 | 20985 | ANSON 230.00 | 1 | 542-20985-1 | 398 | 398 | 141.8 | 306.6 | 80.4 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 837 | 6ROWANG 230.00 | 840 | 6ROWANT 230.00 | 1 | 837-840-1 | 1200 | 1200 | 976.9 | 976.9 | 80.4 | 2 | 1110 | 977 | 977 | 86.7 | 175 | 6.3 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20044 | ROB 1 F 115.00 | 20874 | ROB #1 18.000 | 1 | 20044-20874-1 | 244 | 244 | 157.6 | 195.7 | 80.2 | 6 | 244 | 174.5 | 186.9 | 76.6 | 173 | -3.6 | 2023 | 2025 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20248 | I-ANSONV 230.00 | 20358 | BOWMAN T 230.00 | 1 | 20248-20358-1 | 398 | 398 | 140.2 | 304.6 | 80.1 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 1 | 443-713-1 | 478 | 478 | 256.3 | 371.4 | 80 | 29 | 478 | 297.3 | 424.9 | 86.7 | 40 | 6.7 | 2023 | 2019 | -4 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 9.1 | 6.9
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 443 | 6MARSHAL 230.00 | 2 | 443-713-2 | 478 | 478 | 256.3 | 371.4 | 80 | 30 | 478 | 297.3 | 424.9 | 86.7 | 40 | 6.7 | 2023 | 2019 | -4 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 257.8 | 362.3 | 73.1 | 9.1 | 6.9
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20358 | BOWMAN T 230.00 | 20985 | ANSON 230.00 | 1 | 20358-20985-1 | 398 | 398 | 139.9 | 304.4 | 80 | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20883 | WSP #1 13.800 | 1 | 20047-20883-1 | 62 | 62 | 49.5 | 49.5 | 79.9 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 6.7 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20047 | WSP BUS 115.00 | 20884 | WSP #2 13.800 | 1 | 20047-20884-1 | 62 | 62 | 49.5 | 49.5 | 79.9 | 2 | 62 | 53.7 | 53.7 | 86.6 | 130 | 6.7 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20301 | TROY 115.00 | 20428 | BISCOE W 115.00 | 1 | 20301-20428-1 | 269 | 269 | 155.8 | 198.1 | 79.9 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20871 | ROX #3 24.000 | 1 | 20024-20871-1 | 883 | 883 | 702.2 | 702.2 | 79.5 | 2 | 883 | 730.1 | 759.8 | 86.1 | 3445 | 6.6 | 2023 | 2019 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20387 | P1-FAY 0 230.00 | 20388 | P3-FAYRR 230.00 | 1 | 20387-20388-1 | 637 | 637 | 443.2 | 471.5 | 79.5 | 6 | 637 | 382.3 | 522.4 | 82.2 | 179 | 2.7 | 2023 | 2021 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 415.6 | 664.6 | 79.1 | 16 | 840 | 498.3 | 796.6 | 94.8 | 78 | 15.7 | 2023 | 2014 | -9 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 457.1 | 731.3 | 87.1 | -66.7 | -8
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20091 | BRIERCK 230.00 | 20117 | DURHAM 230.00 | 1 | 20091-20117-1 | 539 | 539 | 353.2 | 390 | 79.1 | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2023 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20030 | LEE 1-3F 115.00 | 20877 | LEE #3 18.000 | 1 | 20030-20877-1 | 333 | 333 | 263.2 | 263.2 | 79 | 2 | 333 | 268.6 | 284 | 85.3 | 3097 | 6.3 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20024 | ROX 1-4F 230.00 | 20869 | ROX #1 22.000 | 1 | 20024-20869-1 | 483 | 483 | 380.5 | 380.5 | 78.8 | 2 | 483 | 393.8 | 411.4 | 85.2 | 2109 | 6.4 | 2024 | 2020 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20858 | ASHVCT#1 18.000 | 1 | 20800-20858-1 | 200 | 200 | 157 | 157 | 78.5 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20859 | ASHVCT#2 18.000 | 1 | 20800-20859-1 | 200 | 200 | 157 | 157 | 78.5 | 2 | 200 | 156.5 | 156.5 | 78.3 | 130 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20314 | E3-CTRCH 230.00 | 20373 | S GARD T 230.00 | 1 | 20314-20373-1 | 507 | 507 | 331.6 | 372.6 | 78.3 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20700 | SUMTER 230.00 | 42002 | 6WATEREE 230.00 | 1 | 20700-42002-1 | 500 | 500 | 317.4 | 385.4 | 78 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2024 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20015 | MAYO 1F 500.00 | 20873 | MAYO #1 20.000 | 1 | 20015-20873-1 | 917 | 917 | 712.5 | 712.5 | 77.7 | 2 | 917 | 775.7 | 775.7 | 84.6 | 346 | 6.9 | 2024 | 2020 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20800 | ASHEVIL 115.00 | 20852 | ASHVL #2 20.000 | 1 | 20800-20852-1 | 235 | 235 | 181.8 | 181.8 | 77.4 | 2 | 235 | 185.6 | 379.2 | 161.4 | 548 | 84 | 2024 | 2011 | -13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PINOCAW | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 796.7 | 796.7 | 356.6 | 622.8 | 77.3 | 4 | 796.7 | 384.9 | 671.3 | 83.8 | 45 | 6.5 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA BLACK | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 340.3 | 594.8 | 74.1 | 28 | 3.2
| PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 356.6 | 622.8 | 77.3 | 4 | 796.7 | 384.9 | 671.3 | 83.8 | 46 | 6.5 | 2025 | 2020 | -5 |  | 735 | 796.7 | 735 | PINOCA WHITE | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 340.3 | 594.8 | 74.1 | 28 | 3.2
| SADLERB | 826 | 6ERNEST2 | 718 | 6SADLER | 1 | 718 | 6SADLER 230.00 | 826 | 6ERNEST2 230.00 | 2 | 718-826-2 | 717 | 717 | 318.3 | 561.2 | 77.1 | 5 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | 576 | 717 | 576 | SADLER | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1B | 20183 | WAKE | 44902 | 8CARSON | 1 | 20222 | ROCKY MT 230.00 | 44591 | 6NASH 230.00 | 1 | 20222-44591-1 | 429 | 429 | 257 | 309.7 | 77.1 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| MECKLENBURGB | 540 | 6MCGUIRE | 538 | 6HARRISB | 3 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 538-540-1 | 563.7 | 563.7 | 346.3 | 431.4 | 77 | 36 | 490.8 | 329.8 | 367.2 | 75.3 | 86 | -1.7 | 2025 | 2033 | 8 |  | 490.8 | 563.7 | 540.2 | CRAIGHEAD BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CRAIGHEADB | 540 | 6MCGUIRE | 538 | 6HARRISB | 1 | 538 | 6HARRISB 230.00 | 540 | 6MCGUIRE 230.00 | 3 | 538-540-3 | 617.5 | 617.5 | 389.9 | 472.8 | 76.9 | 42 | 529.8 | 371.4 | 413.6 | 78.5 | 354 | 1.6 | 2025 | 2031 | 6 |  | 529.8 | 617.5 | 553.7 | MECKLENBURG BL | 230 kV Line | 556.9073 | 617.458 | 556.9073 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20347 | ABRDN RD 230.00 | 20348 | RKH 230.00 | 1 | 20347-20348-1 | 539 | 539 | 365 | 394.1 | 76.3 | 8 | 539 | 334.2 | 421.5 | 76.7 | 199 | 0.4 | 2025 | 2025 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20157 | HOMESTED 230.00 | 20160 | PINE LK 230.00 | 1 | 20157-20160-1 | 423 | 423 | 225 | 302.7 | 76.1 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2025 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 282.2 | 364 | 75.9 | 36 | 478 | 313.5 | 402.6 | 84.9 | 168 | 9 | 2025 | 2020 | -5 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 300.9 | 384.5 | 80.7 | -20.5 | -4.8
| DUTCHOVERB | 543 | 6RIVRBEN | 441 | 6LINCOLN | 1 | 441 | 6LINCOLN 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 441-543-2 | 597.5 | 597.5 | 271.3 | 462 | 75.6 | 2 | 597.5 | 284.3 | 481.1 | 79.3 | 41 | 3.7 | 2026 | 2023 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 597.5 | 285.3 | 500.9 | 82.2 | -38.9 | -6.6
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20145 | NEUSE 115.00 | 20185 | FALLS 115.00 | 1 | 20145-20185-1 | 201 | 201 | 130.1 | 136 | 75.3 | 3 | 201 | 117.9 | 147.4 | 75.7 | 128 | 0.4 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 1 | 712-719-1 | 840 | 840 | 346.6 | 629.4 | 74.9 | 2 | 840 | 415.6 | 754.3 | 89.8 | 41 | 14.9 | 2026 | 2017 | -9 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 381.2 | 692.7 | 82.5 | -63.3 | -7.6
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 848 | 6PL GRDN 230.00 | 1 | 713-848-1 | 478 | 478 | 133.1 | 347.2 | 74.8 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | 436.9351 | 477.96 | 436.9351 | FAGO | 230 kV Line | 458.045 | 506.6376 | 458.045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 713 | 6BECKRDT 230.00 | 848 | 6PL GRDN 230.00 | 2 | 713-848-2 | 478 | 478 | 133.1 | 347.2 | 74.8 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | 436.9351 | 477.96 | 436.9351 | FAGO | 230 kV Line | 458.045 | 506.6376 | 458.045 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20024 | ROX 1-4F 230.00 | 20182 | FALLS 230.00 | 1 | 20024-20182-1 | 539 | 539 | 298.2 | 377.1 | 74.6 | 10 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CPL1AOR | 20015 | MAYO 1F | 20054 | DURHAM | 1 | 20079 | OXF S T 230.00 | 20085 | OXFORD N 230.00 | 1 | 20079-20085-1 | 539 | 539 | 339.1 | 388.3 | 74.6 | 11 | 539 | 334.1 | 394.5 | 74.5 | 387 | -0.1 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20162 | MILBURNE 230.00 | 20182 | FALLS 230.00 | 1 | 20162-20182-1 | 423 | 423 | 242.2 | 288.1 | 74.4 | 9 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2026 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20091 | BRIERCK 230.00 | 20159 | RTP 23KV 230.00 | 1 | 20091-20159-1 | 539 | 539 | 328.6 | 366.5 | 74.3 | 11 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2027 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230.00 | 544 | 6WINECOF 230.00 | 1 | 443-544-1 | 478 | 478 | 319.4 | 351.2 | 74.1 | 34 | 478 | 327 | 368.6 | 76.1 | 189 | 2 | 2027 | 2025 | -2 |  | 459.7 | 478 | 478 | DOOLEY | 230 kV Line | 556.9 | 617.5 | 556.9 | 478 | 313 | 342.8 | 70 | 8.4 | 4.1
| PISGHBK2 | 108 | 6PISGAH | 2666 | PISGA 2 | 2 | 209 | 3MILLSRV 115.00 | 20800 | ASHEVIL 115.00 | 1 | 209-20800-1 | 207 | 207 | 140.7 | 154.9 | 73.8 | 13 | 207 | 131 | 163.4 | 78.8 | 95 | 5 | 2027 | 2024 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20265 | E15-STED 115.00 | 20401 | VANDER 115.00 | 1 | 20265-20401-1 | 163 | 163 | 117.5 | 117.5 | 73.5 | 2 | 163 | 103.6 | 126.5 | 79 | 204 | 5.5 | 2027 | 2023 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 112 | 8BAD CRK 500.00 | 113 | 8JOCASSE 500.00 | 1 | 112-113-1 | 1790.9 | 1790.9 | 1396.3 | 1396.3 | 73.2 | 2 | 1732 | 1396.9 | 1396.9 | 75.9 | 84 | 2.7 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | 1397.7 | 1397.7 | 73 | -1.4 | 0.2
| LONDONCREEK | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230.00 | 265 | 6RIVERVW 230.00 | 2 | 236-265-2 | 452.5 | 452.5 | 225.5 | 334.1 | 72.9 | 21 | 452.5 | 287.6 | 425.5 | 93.6 | 52 | 20.7 | 2027 | 2015 | -12 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 277.7 | 420.8 | 91.4 | -86.7 | -18.5
| FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 105 | 6SHADYTW 230.00 | 109 | 6SHADY G 230.00 | 2 | 105-109-2 | 478 | 478 | 215.7 | 346 | 72.6 | 3 | 478 | 244.5 | 391.9 | 83.3 | 44 | 10.7 | 2028 | 2021 | -7 |  | 477.96 | 477.96 | 477.96 | SHADY GROVE | 230 kV Line | 859.9297 | 1008.8939 | 859.9297 | 478 | 214.7 | 346.1 | 73.3 | -0.1 | -0.7
| BASE CASE | 0 |  | 0 |  |  | 20378 | RICHMOND 230.00 | 20977 | RICH CC1 18.000 | 1 | 20378-20977-1 | 660 | 660 | 476 | 476 | 72.1 | 1 | 660 | 510 | 516 | 78.2 | 1433 | 6.1 | 2028 | 2024 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230.00 | 540 | 6MCGUIRE 230.00 | 1 | 443-540-1 | 478 | 478 | 167 | 348.5 | 71.9 | 2 | 478 | 291.8 | 453 | 92.8 | 39 | 20.9 | 2028 | 2015 | -13 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | -39.5 | -7.1
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 443 | 6MARSHAL 230.00 | 540 | 6MCGUIRE 230.00 | 2 | 443-540-2 | 478 | 478 | 167 | 348.5 | 71.9 | 2 | 478 | 291.8 | 453 | 92.8 | 40 | 20.9 | 2028 | 2015 | -13 |  | 459.7 | 478 | 478 | WESTPORT | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 250.2 | 388 | 79 | -39.5 | -7.1
| BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115.00 | 20890 | TILL #3 13.800 | 1 | 20004-20890-1 | 31 | 31 | 22.3 | 22.3 | 71.9 | 2 | 31 | 22 | 22 | 71 | 130 | -0.9 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20004 | TIL 1-4H 115.00 | 20891 | TILL #4 13.800 | 1 | 20004-20891-1 | 31 | 31 | 22.3 | 22.3 | 71.9 | 2 | 31 | 22 | 22 | 71 | 130 | -0.9 | 2028 | 2029 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20053 | CAPE 5&6 115.00 | 20878 | CAPE #5 13.800 | 1 | 20053-20878-1 | 200 | 200 | 143.2 | 143.2 | 71.6 | 2 | 200 | 144.3 | 155.5 | 77.8 | 335 | 6.2 | 2028 | 2024 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20309 | BISCOE W 230.00 | 20347 | ABRDN RD 230.00 | 1 | 20309-20347-1 | 539 | 539 | 331.7 | 357.8 | 71.3 | 8 | 539 | 302.8 | 385.6 | 72 | 34 | 0.7 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20348 | RKH 230.00 | 20638 | WDSB T 230.00 | 1 | 20348-20638-1 | 539 | 539 | 348.3 | 368.6 | 71.3 | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20519 | M-TARAWA 230.00 | 20524 | JACKSONV 230.00 | 1 | 20519-20524-1 | 478 | 478 | 316 | 322.2 | 71.2 | 3 | 478 | 321.1 | 424.7 | 92.7 | 1264 | 21.5 | 2029 | 2015 | -14 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| PLSNTGDN_XFR | 850 | 8PL GRDN | 848 | 6PL GRDN | 5 | 845 | 6E.DURHM 230.00 | 847 | 6PARKWOD 230.00 | 1 | 845-847-1 | 478 | 478 | 234.3 | 324.2 | 70.6 | 16 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | 477.96 | 477.96 | 477.96 | MICHIE | 230 kV Line | 575.9418 | 718.1349 | 575.9418 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| GUARDNORTH | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 20047 | WSP BUS 115.00 | 20406 | ST PAULS 115.00 | 1 | 20047-20406-1 | 119 | 119 | 74.8 | 80.6 | 70.5 | 2 | 119 | 72.6 | 94.7 | 79.6 | 207 | 9.1 | 2029 | 2023 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| CLINGMANB | 712 | 6ANTIOCH | 716 | 6MITCH R | 1 | 712 | 6ANTIOCH 230.00 | 716 | 6MITCH R 230.00 | 2 | 712-716-2 | 717 | 717 | 308.5 | 513.5 | 70.4 | 3 | 717 | 383.7 | 638.6 | 87.8 | 39 | 17.4 | 2029 | 2018 | -11 |  | 717 | 717 | 717 | CLINGMAN | 230 kV Line | 946.7591 | 1176.1799 | 946.7591 | 717 | 351.1 | 584.7 | 79.2 | -71.2 | -8.8
| HODGBK1SHORT | 5 | 6HODGES | 3 | 6ANDERSN | 1 | 1 | 3CLARK H 115.00 | 22 | CLARK HL 100.00 | 4 | 1-22-4 | 96 | 96 | 55.6 | 67.3 | 70.1 | 13 | 96 | 65.4 | 77 | 80.2 | 347 | 10.1 | 2029 | 2023 | -6 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | 58.2 | 69.2 | 72.1 | -1.9 | -2
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20676 | KINGST N 230.00 | 20677 | KINGSTRE 230.00 | 1 | 20676-20677-1 | 557 | 557 | 342.3 | 382.1 | 70.1 | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2029 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| BASE CASE | 0 |  | 0 |  |  | 20182 | FALLS 230.00 | 20185 | FALLS 115.00 | 1 | 20182-20185-1 | 300 | 300 | 209.9 | 209.9 | 70 | 6 | 300 | 214.6 | 311.1 | 103.7 | 1807 | 33.7 | 2030 | 2011 | -19 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
| RICHMOND | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 20674 | OLANTA 230.00 | 20675 | LAKE CTY 230.00 | 1 | 20674-20675-1 | 478 | 478 | 286.7 | 325.1 | 70 | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2030 | #N/A | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 7 | > 5% worse
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening
[25 empty] | 8 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent
STUDYL | THRP | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1517.1 | 112.4 | 42 | 1350 | - | 1123.1 | 83.2 | 910 | -29.2 | 2011 | 2021 | 10 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1871.9 | 98.3 | 42 | 1904.3 | - | 1909.2 | 100.3 | 910 | 2 | 2012 | 2011 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1541.1 | 80.9 | 330.8 | 17.4
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 82.8 | 87.1 | 42 | 95 | - | 88.1 | 92.7 | 910 | 5.6 | 2018 | 2015 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 337 | 86.4 | 21 | 390 | - | 349.5 | 89.6 | 455 | 3.2 | 2019 | 2017 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 95.6 | 86.1 | 42 | 111 | - | 85.1 | 76.6 | 910 | -9.5 | 2019 | 2025 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 890.3 | 83.4 | 42 | 1067 | - | 985.6 | 92.4 | 910 | 9 | 2021 | 2015 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG2 | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 881.1 | 82.6 | 42 | 1067 | - | 982.5 | 92.1 | 910 | 9.5 | 2021 | 2016 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 193.2 | 82.2 | 42 | 235 | - | 192.2 | 81.8 | 910 | -0.4 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 50.7 | 81.8 | 42 | 62 | - | 54.2 | 87.4 | 910 | 5.6 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 50.7 | 81.8 | 42 | 62 | - | 54.2 | 87.4 | 910 | 5.6 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | MCG1 | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 458 | 458 | - | 372.6 | 81.3 | 42 | 458 | - | 364 | 79.5 | 910 | -1.8 | 2022 | 2023 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 458 | - | 347.6 | 75.9 | 25 | 5.4
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 85.7 | 80.9 | 42 | 106 | - | 82.3 | 77.7 | 910 | -3.2 | 2022 | 2024 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 538 | 6HARRISB | 542 | 6OAKBORO | 1 | 538-542-1 | 437 | 437 | - | 353.1 | 80.8 | 42 | 437 | - | 270.3 | 61.9 | 854 | -18.9 | 2022 | 2036 | 14 |  | 437 | 482 | 437 | HARRISBURG | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 235.4 | 53.9 | 117.7 | 26.9
STUDYL | BEL1 | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 697.4 | 79.4 | 42 | 878 | - | 735.9 | 83.8 | 910 | 4.4 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 849-850-1 | 1385.6 | 1385.6 | - | 1098.6 | 79.3 | 21 | 1385.6 | - | 904.6 | 65.3 | 455 | -14 | 2023 | 2033 | 10 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | 1385.6 | - | 732.8 | 52.9 | 365.8 | 26.4
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 185 | 78.7 | 42 | 235 | - | 187.5 | 79.8 | 910 | 1.1 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 645.3 | 78.5 | 42 | 822 | - | 667.2 | 81.2 | 910 | 2.7 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 260.5 | 78.2 | 42 | 333 | - | 271.7 | 81.6 | 910 | 3.4 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 688.2 | 77.9 | 42 | 883 | - | 727.4 | 82.4 | 910 | 4.5 | 2024 | 2021 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 155.4 | 77.7 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | CLI5 | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 155.4 | 77.7 | 42 | 200 | - | 154.9 | 77.5 | 910 | -0.2 | 2024 | 2024 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 682.1 | 77.2 | 42 | 883 | - | 729.3 | 82.6 | 910 | 5.4 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 702 | 76.6 | 42 | 917 | - | 752.8 | 82.1 | 910 | 5.5 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 368.5 | 76.3 | 42 | 483 | - | 394.7 | 81.7 | 910 | 5.4 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | THRP | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 362 | 75.7 | 42 | 478 | - | 353.9 | 74.1 | 872 | -1.6 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 62.1 | 12.9
STUDYL | THRP | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 362 | 75.7 | 42 | 478 | - | 353.9 | 74.1 | 872 | -1.6 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 299.9 | 62.8 | 62.1 | 12.9
STUDYL | BEL1 | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1300 | 1300 | - | 975.8 | 75.1 | 21 | 1300 | - | 979.5 | 75.3 | 455 | 0.2 | 2026 | 2026 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 398.5 | 74.8 | 42 | 533 | - | 427.6 | 80.2 | 910 | 5.4 | 2026 | 2023 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO3 | - | - | - | - | - | 112 | 8BAD CRK | 113 | 8JOCASSE | 1 | 112-113-1 | 1790.9 | 1790.9 | - | 1314.1 | 73.4 | 21 | 1790.9 | - | 1319 | 73.7 | 454 | 0.3 | 2027 | 2027 | 0 |  | 1732 | 2218.7 | 1790.9 | WHITEWATER | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1790.9 | - | 1308.4 | 73.1 | 5.7 | 0.3
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 22.8 | 73.4 | 42 | 31 | - | 23.1 | 74.6 | 910 | 1.2 | 2027 | 2026 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 22.8 | 73.4 | 42 | 31 | - | 23.1 | 74.6 | 910 | 1.2 | 2027 | 2026 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 443 | 6MARSHAL | 713 | 6BECKRDT | 1 | 443-713-1 | 437 | 437 | - | 313.9 | 71.8 | 80 | 437 | - | 349.7 | 80 | 1436 | 8.2 | 2028 | 2023 | -5 |  | 437 | 478 | 437 | MARSHALL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 437 | - | 306.2 | 70.1 | 7.7 | 1.7
STUDYL | CAT1 | - | - | - | - | - | 209 | 3MILLSRV | 20800 | ASHEVIL | 1 | 209-20800-1 | 207 | 207 | - | 147.5 | 71.2 | 42 | 207 | - | 139.4 | 67.3 | 910 | -3.9 | 2029 | 2031 | 2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20888 | TILL #1 | 1 | 20004-20888-1 | 31 | 31 | - | 21.9 | 70.8 | 42 | 31 | - | 22.1 | 71.2 | 910 | 0.4 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BEL1 | - | - | - | - | - | 20004 | TIL 1-4H | 20889 | TILL #2 | 1 | 20004-20889-1 | 31 | 31 | - | 21.9 | 70.8 | 42 | 31 | - | 22.1 | 71.2 | 910 | 0.4 | 2029 | 2029 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | OCO1 | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 67.2 | 70 | 21 | 96 | - | 77.7 | 80.9 | 455 | 10.9 | 2030 | 2022 | -8 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 69.7 | 72.6 | -2.5 | -2.6
2 | % Yearly Load Growth |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [6 empty] | Directory: | P:\Bdm\NC PWG\Model\Thermal Screening\PECTRM\
2011 | Study Year |  | Thermal Screening | [6 empty] | File: | Thermal Screening duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM Revised.xls
2011 | Implementation Year
2011 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Loading Exceeds
[25 empty] | 5 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM | [5 empty] | 2011 Summer Screening - 600ImportCPLE_Duke | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2007 Summer Screening |  |  |  | Difference |  | 2011 Summer Screening - duk11s_PEC_FinalNP_Rkh-WE_Fxd_E-W_Fixed_HarDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc
STUDYL | BADX | - | - | - | - | - | 337 | 8NEWPORT | 20377 | RICHMOND | 1 | 337-20377-1 | 1350 | 1350 | - | 1359.1 | 100.7 | 2 | 1350 | - | 966.8 | 71.6 | 42 | -29.1 | 2011 | 2028 | 17 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20615 | BARNARD | 20616 | BARNARD | 1 | 20615-20616-1 | 150 | 150 | - | 140.8 | 93.9 | 1 | 150 | - | 142.5 | 95 | 21 | 1.1 | 2015 | 2014 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 142.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20106 | WAKEFORE | 20107 | E18-WEMC | 1 | 20106-20107-1 | 40 | 40 | - | 37.3 | 93.4 | 2 | 40 | - | 36.8 | 92.1 | 42 | -1.3 | 2015 | 2016 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 35.7 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20885 | WSP #3 | 1 | 20047-20885-1 | 95 | 95 | - | 82.4 | 86.7 | 2 | 95 | - | 88.1 | 92.7 | 42 | 6 | 2019 | 2015 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 81.7 | #N/A | 82.8
STUDYL | BADX | - | - | - | - | - | 20378 | RICHMOND | 20976 | RICH EMC | 1 | 20378-20976-1 | 325 | 325 | - | 280.5 | 86.3 | 2 | 325 | - | 293 | 90.2 | 42 | 3.9 | 2019 | 2017 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 291.3 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20875 | LEE #1 | 1 | 20030-20875-1 | 111 | 111 | - | 95.2 | 85.8 | 2 | 111 | - | 84.1 | 75.8 | 42 | -10 | 2019 | 2025 | 6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 100.1 | #N/A | 95.6
STUDYL | BADX | - | - | - | - | - | 20041 | CF 5-6 F | 20053 | CAPE 5&6 | 1 | 20041-20053-1 | 350 | 350 | - | 299 | 85.4 | 1 | 350 | - | 316.1 | 90.3 | 21 | 4.9 | 2019 | 2017 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 295.4 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20985 | ANSON | 20986 | LILESEMC | 1 | 20985-20986-1 | 390 | 390 | - | 331.3 | 85 | 1 | 390 | - | 344.7 | 88.4 | 21 | 3.4 | 2020 | 2018 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 347.6 | #N/A | 337
STUDYL | BADX | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1609.7 | 84.5 | 2 | 1904.3 | - | 1636.2 | 85.9 | 42 | 1.4 | 2020 | 2019 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1279.9 | 67.2 | 329.8 | 17.3 | 1940.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20020 | BRUN 2 N | 20863 | BRUN #2 | 1 | 20020-20863-1 | 1067 | 1067 | - | 891 | 83.5 | 2 | 1067 | - | 985.7 | 92.4 | 42 | 8.9 | 2021 | 2015 | -6 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 870.9 | #N/A | 890.3
STUDYL | BADX | - | - | - | - | - | 20329 | RAMSEUR | 20330 | I-RAMTEX | 1 | 20329-20330-1 | 19 | 19 | - | 15.8 | 83.4 | 2 | 19 | - | 15.6 | 81.9 | 42 | -1.5 | 2021 | 2022 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20022 | BRUN 1 N | 20862 | BRUN #1 | 1 | 20022-20862-1 | 1067 | 1067 | - | 885.1 | 82.9 | 2 | 1067 | - | 982.6 | 92.1 | 42 | 9.2 | 2021 | 2016 | -5 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 876.8 | #N/A | 881.1
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20851 | ASHVL #1 | 1 | 20800-20851-1 | 235 | 235 | - | 192 | 81.7 | 2 | 235 | - | 192.4 | 81.9 | 42 | 0.2 | 2022 | 2022 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 190.7 | #N/A | 193.2
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20883 | WSP #1 | 1 | 20047-20883-1 | 62 | 62 | - | 50.5 | 81.4 | 2 | 62 | - | 54.2 | 87.4 | 42 | 6 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.5 | #N/A | 50.7
STUDYL | BADX | - | - | - | - | - | 20047 | WSP BUS | 20884 | WSP #2 | 1 | 20047-20884-1 | 62 | 62 | - | 50.5 | 81.4 | 2 | 62 | - | 54.2 | 87.4 | 42 | 6 | 2022 | 2018 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 49.5 | #N/A | 50.7
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20876 | LEE #2 | 1 | 20030-20876-1 | 106 | 106 | - | 85.4 | 80.6 | 2 | 106 | - | 81.3 | 76.7 | 42 | -3.9 | 2022 | 2025 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 88.1 | #N/A | 85.7
STUDYL | BADX | - | - | - | - | - | 837 | 6ROWANG | 840 | 6ROWANT | 1 | 837-840-1 | 1200 | 1200 | - | 957.7 | 79.8 | 1 | 1200 | - | 955.1 | 79.6 | 21 | -0.2 | 2023 | 2023 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | - | 622.5 | 51.9 | 335.2 | 27.9 | 976.9 | #N/A | 975.8
STUDYL | BADX | - | - | - | - | - | 20018 | ROB 2 N | 20864 | ROB #2 | 1 | 20018-20864-1 | 878 | 878 | - | 697.9 | 79.5 | 2 | 878 | - | 736.3 | 83.9 | 42 | 4.4 | 2023 | 2020 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 706.9 | #N/A | 697.4
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20852 | ASHVL #2 | 1 | 20800-20852-1 | 235 | 235 | - | 183.5 | 78.1 | 2 | 235 | - | 186.8 | 79.5 | 42 | 1.4 | 2024 | 2023 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 181.8 | #N/A | 185
STUDYL | BADX | - | - | - | - | - | 20030 | LEE 1-3F | 20877 | LEE #3 | 1 | 20030-20877-1 | 333 | 333 | - | 259.7 | 78 | 2 | 333 | - | 268.8 | 80.7 | 42 | 2.7 | 2024 | 2022 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 263.2 | #N/A | 260.5
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20858 | ASHVCT#1 | 1 | 20800-20858-1 | 200 | 200 | - | 154.4 | 77.2 | 2 | 200 | - | 155 | 77.5 | 42 | 0.3 | 2025 | 2024 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 157 | #N/A | 155.4
STUDYL | BADX | - | - | - | - | - | 20800 | ASHEVIL | 20859 | ASHVCT#2 | 1 | 20800-20859-1 | 200 | 200 | - | 154.4 | 77.2 | 2 | 200 | - | 155 | 77.5 | 42 | 0.3 | 2025 | 2024 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 157 | #N/A | 155.4
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20871 | ROX #3 | 1 | 20024-20871-1 | 883 | 883 | - | 680.7 | 77.1 | 2 | 883 | - | 712.3 | 80.7 | 42 | 3.6 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 702.2 | #N/A | 682.1
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20872 | ROX #4 | 1 | 20024-20872-1 | 883 | 883 | - | 677.8 | 76.8 | 2 | 883 | - | 712.6 | 80.7 | 42 | 3.9 | 2025 | 2022 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 712.6 | #N/A | 688.2
STUDYL | BADX | - | - | - | - | - | 20015 | MAYO 1F | 20873 | MAYO #1 | 1 | 20015-20873-1 | 917 | 917 | - | 700.9 | 76.4 | 2 | 917 | - | 753.5 | 82.2 | 42 | 5.8 | 2025 | 2021 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 712.5 | #N/A | 702
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20869 | ROX #1 | 1 | 20024-20869-1 | 483 | 483 | - | 368.6 | 76.3 | 2 | 483 | - | 385.5 | 79.8 | 42 | 3.5 | 2025 | 2023 | -2 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 380.5 | #N/A | 368.5
STUDYL | BADX | - | - | - | - | - | 20024 | ROX 1-4F | 20870 | ROX #2 | 1 | 20024-20870-1 | 822 | 822 | - | 622.5 | 75.7 | 2 | 822 | - | 661.7 | 80.5 | 42 | 4.8 | 2026 | 2022 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 708.6 | #N/A | 645.3
STUDYL | BADX | - | - | - | - | - | 20066 | FALLS23 | 20097 | CG-ROX | 1 | 20066-20097-1 | 423 | 423 | - | 318.2 | 75.2 | 2 | 423 | - | 272.8 | 64.5 | 42 | -10.7 | 2026 | 2034 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 390.7 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 714 | 6BELEWS | 841 | 6BOBWH B | 1 | 714-841-1 | 478 | 478 | - | 357 | 74.7 | 2 | 478 | - | 349.9 | 73.2 | 42 | -1.5 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 60.3 | 12.6 | 467.7 | #N/A | 362
STUDYL | BADX | - | - | - | - | - | 714 | 6BELEWS | 842 | 6BOBWH W | 2 | 714-842-2 | 478 | 478 | - | 357 | 74.7 | 2 | 478 | - | 349.9 | 73.2 | 42 | -1.5 | 2026 | 2027 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | - | 296.7 | 62.1 | 60.3 | 12.6 | 467.7 | #N/A | 362
STUDYL | BADX | - | - | - | - | - | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 849-850-1 | 1385.6 | 1385.6 | - | 1033.2 | 74.6 | 1 | 1385.6 | - | 843.3 | 60.9 | 21 | -13.7 | 2026 | 2037 | 11 |  | 1385.6 | 1385.6 | 1385.6 | PARKWOOD | 500 kV Line | 3739.388 | 3739.388 | 3739.388 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1338.7 | #N/A | 1098.6
STUDYL | BADX | - | - | - | - | - | 1 | 3CLARK H | 22 | CLARK HL | 4 | 1-22-4 | 96 | 96 | - | 71.3 | 74.3 | 1 | 96 | - | 81.3 | 84.7 | 21 | 10.4 | 2027 | 2020 | -7 |  | 96 | 96 | 96 | CLARK HILL TIE 04 | 115/100 kV Transformer | 159.7 | 173.3 | 173.3 | 96 | - | 73.5 | 76.6 | -2.2 | -2.3 | 67.3 | #N/A | 67.2
STUDYL | BADX | - | - | - | - | - | 20039 | SUT 3 F | 20868 | SUT #3 | 1 | 20039-20868-1 | 533 | 533 | - | 391.2 | 73.4 | 2 | 533 | - | 427.8 | 80.3 | 42 | 6.9 | 2027 | 2023 | -4 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 477.2 | #N/A | 398.5
STUDYL | BADX | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 478 | 478 | - | 346.7 | 72.5 | 2 | 478 | - | 344 | 72 | 42 | -0.5 | 2028 | 2028 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | - | 328.3 | 68.7 | 18.4 | 3.8 | 412.3 | #N/A | 372.6
STUDYL | BADX | - | - | - | - | - | 20182 | FALLS | 20185 | FALLS | 1 | 20182-20185-1 | 300 | 300 | - | 213.8 | 71.3 | 1 | 300 | - | 215 | 71.7 | 21 | 0.4 | 2029 | 2028 | -1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 209.9 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20387 | P1-FAY 0 | 20388 | P3-FAYRR | 1 | 20387-20388-1 | 637 | 637 | - | 454 | 71.3 | 1 | 637 | - | 382.3 | 60 | 21 | -11.3 | 2029 | 2037 | 8 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 471.5 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20632 | MARION | 20654 | DILLON T | 1 | 20632-20654-1 | 97 | 97 | - | 69 | 71.1 | 1 | 97 | - | 53.3 | 54.9 | 21 | -16.2 | 2029 | 2042 | 13 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 78.7 | #N/A | #N/A
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20890 | TILL #3 | 1 | 20004-20890-1 | 31 | 31 | - | 21.9 | 70.5 | 2 | 31 | - | 23.2 | 74.8 | 42 | 4.3 | 2029 | 2026 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.3 | #N/A | 22.8
STUDYL | BADX | - | - | - | - | - | 20004 | TIL 1-4H | 20891 | TILL #4 | 1 | 20004-20891-1 | 31 | 31 | - | 21.9 | 70.5 | 2 | 31 | - | 23.2 | 74.8 | 42 | 4.3 | 2029 | 2026 | -3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 22.3 | #N/A | 22.8
STUDYL | BADX | - | - | - | - | - | 209 | 3MILLSRV | 20800 | ASHEVIL | 1 | 209-20800-1 | 207 | 207 | - | 145.1 | 70.1 | 2 | 207 | - | 136.6 | 66 | 42 | -4.1 | 2029 | 2032 | 3 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 154.9 | #N/A | 147.5
STUDYL | BADX | - | - | - | - | - | 20398 | M-FBWOOD | 20399 | FB WOODR | 1 | 20398-20399-1 | 150 | 150 | - | 105.2 | 70.1 | 2 | 150 | - | 103 | 68.7 | 42 | -1.4 | 2029 | 2030 | 1 |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Populate Summary Worksheet