NC Transmission Planning Collaborative

Planning Working Group (PWG)

Meeting Minutes

September 19, 2006

Aberdeen, NC

10:00 AM – 3:00 PM Eastern

Attendees:

Bryan Guy, Chair					Progress Energy

Lee Adams						Progress Energy

Mark Byrd						Progress Energy

James Manning, Vice Chair				NCEMC

Denise Roeder					ElectriCities

Frank Gaffney					ElectriCities

Bob Pierce						Duke Energy

Brian Moss						Duke Energy

Rich Wodyka						Gestalt

Pam Kozlowski					Gestalt

- ADMINISTRATIVE

- Mr. Guy called the meeting to order at approximately 10:00 AM and provided an overview of the meeting facilities for the day.

- The group reviewed the August 15, 2006 PWG meeting minutes.  The minutes were approved as modified at the meeting.

- OSC MEETING AND TAG MEETING REPORTS

  - A report on OSC meeting and on the TAG meeting, both held on September 7, 2006, was given by those who had participated in the meetings.

- RELIABILITY PLANNING STUDIES

- Mr. Guy presented the results of PEC’s thermal screenings of the 1,200 MW import case from Duke with the following potential solutions to the Raleigh / Durham area overloads implemented:

  - Added Parkwood-Durham 500 kV line (15 miles).

  - Added Pleasant Garden-Harris 500 kV (65 miles).  Mr. Guy reported that continuing the 500 kV line from Harris to Wake or to Cumberland did not improve the results.

  - Added Durham-Harris 230 kV line (30 miles).

ACTION ITEM:	PEC to review the results of the 1,200 MW import cases both with and without potential solutions and determine if the conductor or ancillary equipment is limiting.  By October 3rd, PEC to provide the rating of the conductor and of the limiting element, if different from the conductor.  Once PEC has identified the limiting elements, PWG to have teleconference to brainstorm solutions.

- Based on the results of the thermal screenings of the potential solutions listed above, the group brainstormed another potential solution to the Raleigh / Durham area overloads:  Add Parkwood-Durham 500 kV line (15 miles) with a third 500/230 kV transformer bank at Wake.  The group also discussed performing the thermal screenings on the 1,200 MW import case from Duke with different dispatches of Anson and Yadkin.

ACTION ITEM:	PEC and Duke to add the Parkwood-Durham 500 kV line with a third 500/230 kV transformer bank at Wake in the 1,200 MW import case from Duke and perform thermal screening.

ACTION ITEM:	PEC and Duke to create the three modified dispatches listed below in the 1,200 MW import case from Duke and perform thermal screenings:

- Anson down;

- Yadkin full on; and

- Yadkin full on and Anson down.

ACTION ITEM: PEC to document each operating procedure cited as a solution to an overload and indicate the threshold where the operating procedure is no longer acceptable to rely upon as a solution to the overload.

ACTION ITEM: PEC and Duke to develop 2010/2011 winter case with a 20 MW import from AEP to Waynesville and perform thermal screening.

- DRAFT RELIABILITY PLAN

- The group developed a draft outline for the report on the results of the studies and recommended solutions for the final plan.

ACTION ITEM:	Gestalt to develop first draft of report for the next PWG meeting.

- OTHER ITEMS

- The meeting was adjourned at approximately 2:00 PM.