Supplemental Report on the

NCTPC

2006

Collaborative

Transmission

Plan

DRAFT 03/07/07

Table of Contents

I.	Executive Summary	3

II.	Introduction	5

III.	1,200 MW Resource Supply Option Study – Increased Imports from Duke to Progress East	5

III.A.	Case Development	5

III.B.	Assessment, Problem Identification and Solution Development	5

III.C.	Selection of Preferred Reliability Solutions	6

IV.	Updated 2006 Collaborative Transmission Plan	7

Appendix 1:	Updated Collaborative Transmission Plan Major Project Listing

Appendix 2:	New and Modified Major Project Descriptions

Appendix 3:	Projects Investigated for Duke to Progress East Resource Supply Options Studied

# Executive Summary

The purpose of this supplemental report to the 2006 North Carolina Transmission Planning Collaborative (“NCTPC”) Collaborative Transmission Plan is two-fold:

- to report on results of additional analyses performed to study transfers of 1,200 MW from Duke Energy Carolinas (“Duke”) to Progress Energy Carolinas, Inc. (“Progress”); and

- to update the preferred solutions presented in the Collaborative Transmission Plan based on additional analysis performed over the last two months.

The NCTPC was established to:

- provide the Participants (Duke, Progress, North Carolina Electric Membership Corporation and ElectriCities of North Carolina) and other stakeholders an opportunity to participate in the electric transmission planning process for the Participants in the State of North Carolina;

- preserve the integrity of the current reliability and least-cost planning processes;

- expand the transmission planning process to include analysis of increasing transmission access to supply resources inside and outside the control areas of Duke and Progress; and

- develop a single coordinated transmission plan for the Participants in North Carolina that includes reliability and enhanced transmission access considerations while appropriately balancing costs, benefits and risks associated with the use of transmission and generation resources.

The report documenting the first single Collaborative Transmission Plan for the Participants in North Carolina was published in January 2007.  While the overall NCTPC Process includes both a Reliability Planning Process and an Enhanced Transmission Access Planning Process, the 2006 NCTPC Process focused exclusively on the Reliability Planning Process because stakeholders did not request any Enhanced Transmission Access scenarios for the 2006 Study.

The Scope of the Reliability Planning Study included a base reliability analysis as well as analysis of potential resource supply options.  The purpose of the base reliability study was to evaluate the transmission system’s ability to meet load growth projected for 2011 through 2016 with the Participants’ planned Designated Network Resources (“DNRs”).  The purpose of the resource supply analysis was to evaluate transmission system impacts for various resource supply options to meet future native load requirements.

The resource supply analysis included evaluating independently an import of 600 MW:

- from each neighboring Control Area into Duke and/or Progress East;

- from Duke into Progress East; and

- from Progress East into Duke.

In August 2006, one additional resource supply scenario study was added to evaluate a 1,200 MW import from Duke to Progress East.  The results of the analysis of this 1,200 MW import case are provided in this supplemental report on the 2006 Collaborative Transmission Plan.

The Planning Working Group (“PWG”) developed a number of potential alternatives to solve problems identified in the 1,200 MW import case from Duke to Progress East.  These potential alternatives were simulated in:

- the base reliability case;

- the 600 MW import case from Duke to Progress East; and

- the 1,200 MW import case from Duke to Progress East.

As a result of the analysis, the PWG identified [and the Oversight Steering Committee (“OSC”) approved] a preferred solution that modifies the 2006 Collaborative Transmission Plan as follows:

- Added project:

  - Pleasant Garden to Asheboro 230 kV line, including replacing the Asheboro 230/115 kV transformers.

- Modified project:

  - Harris to Durham 230 kV line has been modified in the Plan.  The Harris to RTP 230 kV section of the line is included in the Plan.  However, the RTP to Durham 230 kV section of the line is deferred, since this section of the line is not needed within the 10 year planning horizon.

- Deferred project:

  - Third Wake 500/230 kV transformer to beyond the 10 year planning horizon

- Deleted projects:

  - Buck to Asheboro 230 kV line

  - Cape Fear to Siler City 230 kV line

The updated major project listing for the 2006 Collaborative Transmission Plan reflecting these modifications is Appendix 1 to this report.

# Introduction

The report documenting the first single Collaborative Transmission Plan for the Participants in North Carolina was published in January 2007.  The report included results from the base reliability analysis as well as analysis of potential resource supply options.  The resource supply analysis included evaluating independently an import of 600 MW:

- from each neighboring Control Area into Duke and/or Progress East;

- from Duke into Progress East; and

- from Progress East into Duke.

In August 2006, one additional resource supply scenario study was added to evaluate a 1,200 MW import case from Duke to Progress East.  The results of the analysis of this 1,200 MW import case are provided in this supplemental report on the 2006 Collaborative Transmission Plan.

# 1,200 MW Resource Supply Option Study – Increased Imports from Duke to Progress East

## Case Development

Using the 2011 resource supply option case with a 600 MW import from Duke to Progress East, the PWG created a 1,200 MW import case from Duke to Progress East.  The 1,200 MW import represents the following resource supply options from Duke into Progress East:

- 500 MW for Fayetteville;

- 400 MW for Progress; and

- 200 MW for NCEMC.

### A 100 MW redirect OASIS request by NCEMC for changing the source from AEP to Duke was also added to the models thus creating a 1,200 MW Duke to Progress East import case.

## Assessment, Problem Identification and Solution Development

The PWG performed an assessment of the 1,200 MW Duke to Progress import case in accordance with the methodology and criteria discussed in Section III of the Report on the NCTPC 2006 Collaborative Transmission Plan.  The reliability problems resulting from their assessments of this resource supply option scenario were documented and discussed among the PWG.

The PWG developed the potential alternatives, listed in Table 1, to solve the problems identified in the analysis of the 1,200 MW Duke to Progress import case.  These potential alternatives were simulated in:

- the base reliability case;

- the 600 MW import case from Duke to Progress East; and

- the 1,200 MW import case from Duke to Progress East.

Duke and Progress developed rough planning cost estimates and construction schedules for the alternatives.

Table 1

Potential Alternatives

| Alternative | Description |
| --- | --- |
| 1 | Parkwood to Durham 500 kV line Pleasant Garden to Asheboro 230 kV line |
| 2 | Harris to Durham 230 kV line Buck to Asheboro 230 kV line |
| 3 | Harris to Durham 230 kV line Pleasant Garden to Asheboro 230 kV line |
| 4 | Bynum 500 kV substation Harris to RTP 230 kV line |
| 5 | Bynum 500 kV substation Harris to RTP 230 kV line Parkwood to Durham 500 kV line |
| 6 | Harris to RTP 230 kV line Pleasant Garden to Asheboro 230 kV line |

## Selection of Preferred Reliability Solutions

Using the results of the analysis described in Section III.B., the PWG compared the potential alternatives and selected the preferred solution, balancing cost, benefit and risk.  The PWG identified the following preferred solution for both the 600 MW and the 1,200 MW Duke to Progress East resource supply option scenarios:

- Adding the Harris to RTP 230 kV line; and

- Adding the Pleasant Garden to Asheboro 230 kV line, including replacing the Asheboro 230/115 kV transformers

Implementation of this solution:

- Defers the need for:

  - the third Wake 500/230 kV transformer beyond the 10 year planning horizon; and

  - the RTP to Durham 230 kV line section of the Harris to Durham 230 kV line beyond the 10 year planning horizon.

- Deletes the need for:

  - the Buck to Asheboro 230 kV line; and

  - the Cape Fear to Siler City 230 kV line.

These deferred and deleted projects were previously identified in Appendix D to the Report on the NCTPC 2006 Collaborative Transmission Plan.

The issues identified and preferred solutions investigated for the 600 MW and 1,200 MW import cases from Duke to Progress East are listed in Appendix 3.  The table in Appendix 3 is intended to give an estimate of the cost and schedule impact in order to accommodate a new request to increase imports into Progress East from Duke by 600 MW and by 1,200 MW in 2011.  The cost estimates provided reflect either the total cost of new projects needed solely for the import or the acceleration of an existing project already identified.  The need date and lead time determine the estimated year the request could be accommodated.

As indicated in Appendix 3, the Pleasant Garden to Asheboro 230 kV line is needed by 2011 to support an additional 1,200 MW import from Duke to Progress East.  With a lead time of 5 years the likelihood of achieving a 2011 in service date for the Pleasant Garden to Asheboro 230 kV line presents a significant challenge.  A tight lead time is also an issue for the Buck to Asheboro 230 kV line solution presented in the Collaborative Transmission Plan published in January 2007.  However, the Pleasant Garden alternative is projected to be a more feasible solution since Pleasant Garden is much closer to Asheboro than Buck (a 20 mile 230 kV line versus a 40 mile 230 kV line).

In addition, the Pleasant Garden alternative reduces loadings on impacted facilities to a greater degree than the Buck alternative.  Analyses showed that flows on the Progress ties with Duke in the Raleigh/Durham area and Rockingham/Oakboro area as well as on the ties with Yadkin at Badin are several percent lower with the Pleasant Garden alternative than with the Buck alternative.  Loading in the Asheboro/Biscoe/Tillery corridor is also lower with the Pleasant Garden alternative.  A significant benefit of the Pleasant Garden to Asheboro 230 kV solution with an estimated cost of $19M is the potential to replace the Cape Fear to Siler City 230 kV project also with an estimated cost of $19M.  The Pleasant Garden alternative solves the same voltage issues in the Asheboro area as the Buck alternative.

# Updated 2006 Collaborative Transmission Plan

Now that the reliability and all of the resource supply options studies have been completed as part of the 2006 Study, the PWG has re-evaluated the results to determine if any modifications should be incorporated into the 2006 Collaborative Transmission Plan.  The PWG recommended [and the OSC approved] the following modifications to the 2006 Collaborative Transmission Plan that were identified from the supplemental resource supply option studies documented in this report.  The new projects added to the Plan were not identified in the base reliability studies; however, based on the additional analysis performed by the PWG, the projects will have positive financial and power flow benefits on base reliability projects and will address issues that had not been addressed in the 6 to 10 year time horizon of the reliability studies.  The projects will also be beneficial toward creating additional import capability as identified in the resource supply option studies.  The new projects are listed below:

- Harris to RTP 230 kV line; and

- Pleasant Garden to Asheboro 230 kV line, including replacing the Asheboro 230/115 kV transformers.

Addition of these new projects to the Plan,

- Defers the need for:

  - the third Wake 500/230 kV transformer beyond the 10 year planning horizon; and

  - the RTP to Durham 230 kV line section of the Harris to Durham 230 kV line beyond the 10 year planning horizon.

- Deletes the need for:

  - the Buck to Asheboro 230 kV line; and

  - the Cape Fear to Siler City 230 kV line.

The updated 2006 Collaborative Transmission Plan is comprised of 14 major projects with an estimated cost of $10 million or more each.  These projects are listed in Appendix 1.  The list will continue to be modified on an ongoing basis as new improvements are identified through the NCTPC Process and projects are completed or eliminated from the list.  The list provides the following information for each project:

- Reliability Project:  Description of the project.

- Issue Resolved:  Specific driver for project.

- Status:  Status of development of the project as described below:

  - Underway – Projects with this status range from the Transmission Owner having some money in its current year budget for the project to the Transmission Owner having completed some construction activities for the project.

  - Planned – Projects with this status do not have money in the Transmission Owner’s current year budget; and the project is subject to change.

- Transmission Owner:  Responsible equipment owner designated to design and implement the project.

- Planned In-Service Date:  The date the project is expected to be placed in service.

- Estimated Cost:  Best estimate of the cost available.  The estimate accuracy may vary dependent on the maturity of the project.

- Estimated Time to Complete:  Number of years needed to complete project.

A detailed description of the major projects which are either new or modified, based on this supplemental analysis and report, is provided in Appendix 2.