## Sheet1
Resource Supply Option Duke>PEC 2010 600 MW and 1200 MW Comparison
| Primary Solution Alternative | Issue Identified | Owner | Lead Time | Duke>PEC 600 MW Need | Nominal Cost ($Millions) | Duke 600 | Duke>PEC 1200 MW Need | Nominal Cost ($Millions)
1 | Pleasant Garden-Asheboro 230 kV line, Construct 20 mile line (2011 TAP Project, $25 M) | Biscoe-Tillery 115 kV Biscoe-Asheboro East 115 kV Cape Fear-Siler City 230 kV Badin-Tillery 115 kV | PEC/DUKE | 5 | 2011 |  |  | 2011
2 | Asheboro 230kV Sub, Replace 2-200 MVA with 2-300 MVA 230/115 kV Banks (2011 TAP Project, $4.3M) | Asheboro 230/115 kV Banks | PEC | 2 | 2011 |  |  | 2011
3 | Fay-Ft. Bragg Woodruff St 230kV Line, Replace line switch (2012 TAP project-$250,000) | Fay-Ft. Bragg Woodruff St 230kV Line | PEC | 3 | 2012 | 0.03 |  | 2012 | 0.03
4 | Wake 500 kV Sub, Install #3-500/230 kV bank (2017 -problem outside horizon, $21 M) | Wake 500/230 kV banks | PEC | 4 | 2014 | 21 |  | 2013 | 21
5 | Fay-Fay East 230kV Line, Replace CB, wavetrap, line switches (2016 TAP project-$425,000) | Fay-Fay East 230kV Line | PEC | 3 | 2014 | 0.09 |  | 2014 | 0.09
6 | Durham-RTP 230 kV , Reconductor line section (not needed in base case , $5 M) | Durham-RTP 230 kV | PEC | 4 | 2015 | 5 |  | 2014 | 5
7 | Asheboro-Asheboro East 115 kV #3 , Construct new line (2015 TAP Project, $5 M) | Asheboro East-Asheboro South 115 kV Asheboro East-Asheboro North 115 kV | PEC | 5 | 2014 | 0.5 |  | 2013 | 1
8 | Person-Milburnie 230 kV line, Uprate Rox Cog-Falls section ( 2017 problem outside horizon, $2.5 M) | Person-Milburnie 230 kV line | PEC | 3 | 2016 | 2.5 |  | 2015 | 2.5
9 | West End 230 kV Sub, Install 230 kV reactor on Cape Fear terminal (problem outside horizon, $5 M) | Cape Fear - West End 230 kV Rockingham - West End 230 kV | PEC | 3 | 2016 | 5 |  | 2016 | 5
10 | Rockinghan-Anson 230 kV Line #3, Construct new line (problem outside horizon, $17.7 M) | Rockinghan-Anson 230 kV Blk & Wht | PEC | 5 | 2015 | 17.7 |  | 2011 | 17.7
11 | Harrisburg-Oakboro 230 kV line 1/2 , Bundle line | Harrisburg-Oakboro 230 kV 1/2 | DUKE | 3 | - | - |  | 2014 | 3
12 | Antioch 500/230 kV Transformers replacement | Antioch 500/230 kV Transformer - overload of existing banks | DUKE | 5 | 2013 | 30 |  | 2013 | 30
14 | Pleasant Garden 500/230 kV transformer - install additional capacity | Pleasant Garden 500/230 kV transformer - overload of existing bank | DUKE | 5 | 2015 | 16 |  | 2015 | 16
|  | TOTAL (Nominal Cost $Millions) |  |  |  | 97.82 |  |  | 101.32
1 | The tables in Appendix D reflect the date the project is needed in order to implement the resource supply option studied.
2 | The tables in Appendix D contain the estimated incremental costs of the transmission upgrades required to import an additional 600 MW or 1200 MW into the Progress East and/or Duke systems. The costs are incremental to the total transmission capital plans of Progress and Duke. Project costs represent either: (i) the estimated acceleration cost of an existing project within the 10-year planning horizon; or (ii) the estimated total cost of a new project that would be needed in the 10-year planning horizon to support the increased import. The costs are expressed in nominal dollars. Also, the projects required to increase the transfer capability over each of the interfaces were determined independently. Therefore, the projects and cost estimates in the tables in Appendix D do not reflect the requirements for simultaneously increasing transfer capability over two or more of the interfaces.
3 | The project date is based on Progress TRM case study results. Results based on Duke planning criteria result in a later project date.