## 2012 Hr&BR1DnTRM Summary
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 8:33
2012 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK12S/2006 VST11S/2012 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2012\duk12s_PEC_Final-HrDnTRM_CommitLincoln.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Largest Loading% | HrDn Loading% | Br1Dn Loading% | Project Yr Need | Contingency
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 136.1 | 86.8 | 108 | 126 | 126 | 121.1 | 2001 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 128.5 | 72.9 | 108 | 119 | 119 | 115.8 | 2004 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 103.8 | 55.4 | 95 | 109.2 | 109.2 | 104.3 | 2008 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 633.1 | 235.5 | 590 | 107.3 | 107.3 | 102.4 | 2009 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304632 MARION 115 304654 DILLON T 115 1 | LN | 91.5 | 68.7 | 97 | 102.6 | 94.3 | 102.6 | 2010 | 304663 LATTA 230 304682 DILLMP T 230 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 161 | 27.7 | 158 | 101.9 | 101.9 | 101.5 | 2011 | 304145 NEUSE 115 304185 FALLS 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 585.6 | 188.6 | 590 | 99.2 | 99.2 | 94.4 | 2013 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 94 | 46.2 | 95 | 99 | 99 | 94.1 | 2013 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 104.4 | 49.4 | 108 | 96.7 | 96.7 | 93.5 | 2014 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 520.6 | 327.1 | 539 | 96.6 | 96.6 |  | 2014 | 304348 RKH 230 304361 WEST END 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 157.7 | 67.5 | 170 | 95.7 | 92.8 | 95.7 | 2014 | 304089 HENDERSN 115 304105 FRANKLIN 115 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 202.2 | 93.4 | 220 | 96.2 | 91.9 | 96.2 | 2014 | JAX-TARAWA230_&_JAX-NORTHWDS115
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 200.1 | 111 | 221 | 95.5 | 90.5 | 95.5 | 2014 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304182 FALLS 230 304185 FALLS 115 1 | TR | 309.3 | 208.8 | 300 | 103.1 | 103.1 | 103 | 2015 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 589.2 | 326.1 | 637 | 92.5 | 92.5 |  | 2015 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 540.3 | 143.4 | 590 | 91.6 | 91.6 | 86.8 | 2016 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 433.9 | 135.5 | 478 | 90.8 | 90.8 |  | 2016 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 161.3 | 122.6 | 179 | 90.1 | 90.1 |  | 2016 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304020 BRUN 2 N 230 304604 E1-STHPT 230 1 | LN | 424 | 207.2 | 478 | 88.7 |  | 88.7 | 2017 | 304020 BRUN 2 N 230 304615 BARCRK E 230 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 196.5 | 83.3 | 221 | 88.9 |  | 88.9 | 2017 | JAX-TARAWA230_&_JAX-NORTHWDS115
304630 MULLINS 115 304632 MARION 115 1 | LN | 156.6 | 107.2 | 179 | 87.5 |  | 87.5 | 2017 | 304581 WHITEVIL 115 304600 WHITEVIL 230 1
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 453.8 | 260.7 | 507 | 89.5 | 89.5 |  | 2017 | 304348 RKH 230 304361 WEST END 230 1
304312 ASHEB E 115 304331 ASHEB 115 1 | LN | 178.2 | 109.4 | 201 | 89.8 | 88.7 | 89.8 | 2017 | 304319 ASHEB N 115 304331 ASHEB 115 1
304183 WAKE 500 B$0823 WAKE#1 1.00 1 | TR | 946.7 | 612.4 | 1000 | 94.7 | 94.7 | 90.5 | 2018 | 3Wnd: OPEN B$0824 WAKE#2 2
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 188.2 | 159.7 | 200 | 94.1 | 94.1 | 90 | 2018 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 512.6 | 115.8 | 590 | 86.9 | 86.9 |  | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 412.1 | 320 | 478 | 86.2 | 86.2 |  | 2018 | 304465 NEW BERN 230 304471 CCWDCG T 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 162.9 | 50.7 | 190 | 85.8 | 85.8 | 85.5 | 2018 | 304137 METHOD 115 304150 I-NCSU S 115 1
304035 SUT 1-2F 115 304545 CASTLE H 115 2 | LN | 111.9 | 52.9 | 131 | 85.4 | 85.4 |  | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 408.2 | 307.1 | 478 | 85.4 | 85.4 |  | 2018 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 128.2 | 128.2 | 150 | 85.4 | 85.4 | 85.4 | 2018 | ** Base Case **
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 431.3 | 238.5 | 507 | 85.1 | 85.1 |  | 2018 | 304348 RKH 230 304361 WEST END 230 1
304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 170.8 | 125.4 | 201 | 86.4 | 85 | 86.4 | 2018 | 304111 E18-WK F 115 304185 FALLS 115 1
304265 E15-STED 115 304401 VANDER 115 1 | LN | 138.6 | 116.4 | 163 | 85 |  | 85 | 2018 | 304196 ERWIN 230 304197 DUNN 230 1
304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 187.4 | 103.4 | 200 | 93.7 | 93.7 | 91.5 | 2019 | 304421 LAURINBG 115 304424 LAURINBG 230 2
304421 LAURINBG 115 304424 LAURINBG 230 2 | TR | 187.2 | 102.7 | 200 | 93.6 | 93.6 | 91.4 | 2019 | 304421 LAURINBG 115 304424 LAURINBG 230 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on J12: PTI: Contingency Description

## 2012 HrDnTRM
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 8:33
2012 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK12S/2006 VST11S/2012 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2012\duk12s_PEC_Final-HrDnTRM_CommitLincoln.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 50.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 136.1 | 86.8 | 108 | 126 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 128.5 | 72.9 | 108 | 119 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 103.8 | 55.4 | 95 | 109.2 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 633.1 | 235.5 | 590 | 107.3 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304182 FALLS 230 304185 FALLS 115 1 | TR | 309.3 | 208.8 | 300 | 103.1 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 161 | 27.7 | 158 | 101.9 | 304145 NEUSE 115 304185 FALLS 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 585.6 | 188.6 | 590 | 99.2 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 94 | 46.2 | 95 | 99 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 104.4 | 49.4 | 108 | 96.7 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 520.6 | 327.1 | 539 | 96.6 | 304348 RKH 230 304361 WEST END 230 1
304183 WAKE 500 B$0823 WAKE#1 1.00 1 | TR | 946.7 | 612.4 | 1000 | 94.7 | 3Wnd: OPEN B$0824 WAKE#2 2
304632 MARION 115 304654 DILLON T 115 1 | LN | 91.5 | 68.7 | 97 | 94.3 | 304663 LATTA 230 304682 DILLMP T 230 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 188.2 | 159.7 | 200 | 94.1 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 187.4 | 103.4 | 200 | 93.7 | 304421 LAURINBG 115 304424 LAURINBG 230 2
304421 LAURINBG 115 304424 LAURINBG 230 2 | TR | 187.2 | 102.7 | 200 | 93.6 | 304421 LAURINBG 115 304424 LAURINBG 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 157.7 | 67.5 | 170 | 92.8 | 304089 HENDERSN 115 304105 FRANKLIN 115 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 589.2 | 326.1 | 637 | 92.5 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 202.2 | 93.4 | 220 | 91.9 | JAX-TARAWA230_&_JAX-NORTHWDS115
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 540.3 | 143.4 | 590 | 91.6 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 433.9 | 135.5 | 478 | 90.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 200.1 | 111 | 221 | 90.5 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 161.3 | 122.6 | 179 | 90.1 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 453.8 | 260.7 | 507 | 89.5 | 304348 RKH 230 304361 WEST END 230 1
304312 ASHEB E 115 304331 ASHEB 115 1 | LN | 178.2 | 109.4 | 201 | 88.7 | 304319 ASHEB N 115 304331 ASHEB 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 512.6 | 115.8 | 590 | 86.9 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 412.1 | 320 | 478 | 86.2 | 304465 NEW BERN 230 304471 CCWDCG T 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 162.9 | 50.7 | 190 | 85.8 | 304137 METHOD 115 304150 I-NCSU S 115 1
304035 SUT 1-2F 115 304545 CASTLE H 115 2 | LN | 111.9 | 52.9 | 131 | 85.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 408.2 | 307.1 | 478 | 85.4 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 128.2 | 128.2 | 150 | 85.4 | ** Base Case **
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 431.3 | 238.5 | 507 | 85.1 | 304348 RKH 230 304361 WEST END 230 1
304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 170.8 | 125.4 | 201 | 85 | 304111 E18-WK F 115 304185 FALLS 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating

## 2012 Br1DnTRM
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 8:20
2012 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK12S/2006 VST11S/2012 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2012\duk12s_PEC_Final-Br1DnTRM_CommitLincoln.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 131.5 | 82.9 | 108 | 121.8 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 125.1 | 72 | 108 | 115.8 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 99.1 | 51.4 | 95 | 104.3 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304182 FALLS 230 304185 FALLS 115 1 | TR | 309.1 | 210.7 | 300 | 103 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304632 MARION 115 304654 DILLON T 115 1 | LN | 99.5 | 73.4 | 97 | 102.6 | 304663 LATTA 230 304682 DILLMP T 230 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 604.4 | 300.8 | 590 | 102.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 160.4 | 26.1 | 158 | 101.5 | 304145 NEUSE 115 304185 FALLS 115 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 211.7 | 98.5 | 220 | 96.2 | JAX-TARAWA230_&_JAX-NORTHWDS115
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 162.6 | 73.2 | 170 | 95.7 | 304089 HENDERSN 115 304105 FRANKLIN 115 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 211 | 117.4 | 221 | 95.5 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 557.1 | 254.1 | 590 | 94.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 89.4 | 42.3 | 95 | 94.1 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 101 | 48.5 | 108 | 93.5 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 182.9 | 101 | 200 | 91.5 | 304421 LAURINBG 115 304424 LAURINBG 230 2
304421 LAURINBG 115 304424 LAURINBG 230 2 | TR | 182.7 | 100.3 | 200 | 91.4 | 304421 LAURINBG 115 304424 LAURINBG 230 1
304183 WAKE 500 B$0823 WAKE#1 1.00 1 | TR | 905.3 | 585.3 | 1000 | 90.5 | 3Wnd: OPEN B$0824 WAKE#2 2
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 180.1 | 154.8 | 200 | 90 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
304312 ASHEB E 115 304331 ASHEB 115 1 | LN | 180.4 | 111.2 | 201 | 89.8 | 304319 ASHEB N 115 304331 ASHEB 115 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 196.5 | 83.3 | 221 | 88.9 | JAX-TARAWA230_&_JAX-NORTHWDS115
304020 BRUN 2 N 230 304604 E1-STHPT 230 1 | LN | 424 | 207.2 | 478 | 88.7 | 304020 BRUN 2 N 230 304615 BARCRK E 230 1
304630 MULLINS 115 304632 MARION 115 1 | LN | 156.6 | 107.2 | 179 | 87.5 | 304581 WHITEVIL 115 304600 WHITEVIL 230 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 512.1 | 209.5 | 590 | 86.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 173.6 | 124.3 | 201 | 86.4 | 304111 E18-WK F 115 304185 FALLS 115 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 162.4 | 39.5 | 190 | 85.5 | 304137 METHOD 115 304150 I-NCSU S 115 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 128.2 | 128.2 | 150 | 85.4 | ** Base Case **
304265 E15-STED 115 304401 VANDER 115 1 | LN | 138.6 | 116.4 | 163 | 85 | 304196 ERWIN 230 304197 DUNN 230 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on F12: PTI: Loading in %
Note on G12: PTI: Contingency Description