## 2016 Hr&Br1Dn Summary
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 9:00
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016\duk16s_PEC_Final-HrDnTRM_CommitLincoln_v2.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 50.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Largest Loading% | Hr Loading% | Br1 Loading% | Project Yr Need | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 694.7 | 281.7 | 590 | 117.7 | 117.7 | 112.9 | 2008 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304632 MARION 115 304654 DILLON T 115 1 | LN | 108.7 | 81.9 | 97 | 115.5 | 112.1 | 115.5 | 2009 | 304663 LATTA 230 304682 DILLMP T 230 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 121.5 | 75 | 108 | 112.5 | 112.5 | 108.1 | 2011 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 177.7 | 36.8 | 158 | 112.4 | 112.4 | 111.5 | 2011 | 304145 NEUSE 115 304185 FALLS 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 643.8 | 232.3 | 590 | 109.1 | 109.1 | 104.3 | 2012 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 230.1 | 105.8 | 220 | 108.9 | 104.6 | 108.9 | 2012 | JAX-TARAWA230_&_JAX-NORTHWDS115
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 116.7 | 68.6 | 108 | 108.1 | 108.1 | 104.8 | 2012 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 516.4 | 194.1 | 478 | 108 | 108 | 85.4 | 2012 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 226.9 | 125.7 | 221 | 107.5 | 102.7 | 107.5 | 2013 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 561.9 | 352.3 | 539 | 104.3 | 104.3 | 91.4 | 2014 | 304348 RKH 230 304361 WEST END 230 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 212.9 | 88.7 | 221 | 100.7 | 96.3 | 100.7 | 2015 | JAX-TARAWA230_&_JAX-NORTHWDS115
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 594.1 | 184 | 590 | 100.7 | 100.7 | 95.8 | 2015 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 999.7 | 647.6 | 1000 | 100 | 100 | 95.6 | 2020 | 3Wnd: OPEN B$0832 WAKE#2 2
304630 MULLINS 115 304632 MARION 115 1 | LN | 174.7 | 123.8 | 179 | 97.6 |  | 97.6 | 2017 | 304587 E1-CHADP 230 304631 MARION 230 1
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 489.3 | 280.2 | 507 | 96.5 | 96.5 |  | 2018 | 304348 RKH 230 304361 WEST END 230 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 91.5 | 47.8 | 95 | 96.3 | 96.3 | 91.4 | 2018 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 160.9 | 77.8 | 170 | 96 | 94.6 | 96 | 2018 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 562.7 | 153.6 | 590 | 95.4 | 95.4 | 90.5 | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 169.4 | 129.7 | 179 | 94.6 | 94.6 |  | 2019 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178.8 | 68.8 | 190 | 94.1 | 94.1 | 93.7 | 2019 | 304137 METHOD 115 304150 I-NCSU S 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 100.9 | 53.7 | 118 | 93.3 | 85.5 | 93.3 | 2019 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.5 | 139.5 | 150 | 93 | 93 | 93 | 2019 | ** Base Case **
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 174.6 | 107.4 | 190 | 91.9 | 91.9 | 91.3 | 2020 | 304163 MILBURNE 115 304168 YONKERS 115 1
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 464.9 | 256.2 | 507 | 91.7 | 91.7 |  | 2020 | 304348 RKH 230 304361 WEST END 230 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 98.4 | 13.5 | 108 | 91.1 | 91.1 | 90.5 | 2020 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 431.7 | 324.1 | 478 | 90.3 | 90.3 |  | 2020 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 178.1 | 79.9 | 201 | 89.8 | 88.6 | 89.8 | 2021 | 304312 ASHEB E 115 304331 ASHEB 115 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 158.2 | 118.7 | 179 | 88.4 | 88.4 |  | 2021 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 176 | 110.9 | 200 | 88 |  | 88 | 2025 | 304631 MARION 230 304632 MARION 115 2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.8 | 38.6 | 138 | 87.6 | 87.6 | 87.2 | 2021 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 442 | 342.3 | 507 | 87.2 | 87.2 |  | 2022 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 137.8 | 37.6 | 158 | 87.2 | 87.2 | 86.3 | 2022 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137.9 | 70.1 | 159 | 86.7 | 86.7 | 86.2 | 2022 | 304163 MILBURNE 115 304168 YONKERS 115 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 410.8 | 312.7 | 478 | 85.9 | 85.9 |  | 2022 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 92.6 | 45.1 | 108 | 85.7 | 85.7 |  | 2022 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 101 | 82.9 | 118 | 85.6 | 85.6 |  | 2022 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 605.9 | 326.3 | 709 | 85.5 | 85.5 |  | 2022 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 81.1 | 39.4 | 95 | 85.4 | 85.4 |  | 2022 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 171.5 | 133.9 | 201 | 85.3 | 85.3 |  | 2022 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 170.1 | 144.1 | 200 | 85 | 85 |  | 2026 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on G12: PTI: Loading in %
Note on J12: PTI: Contingency Description

## 2016 HrDn TRM
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 9:00
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016\duk16s_PEC_Final-HrDnTRM_CommitLincoln_v2.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 50.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 694.7 | 281.7 | 590 | 117.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 121.5 | 75 | 108 | 112.5 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 177.7 | 36.8 | 158 | 112.4 | 304145 NEUSE 115 304185 FALLS 115 1
304632 MARION 115 304654 DILLON T 115 1 | LN | 108.7 | 81.9 | 97 | 112.1 | 304663 LATTA 230 304682 DILLMP T 230 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 643.8 | 232.3 | 590 | 109.1 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 116.7 | 68.6 | 108 | 108.1 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 516.4 | 194.1 | 478 | 108 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 230.1 | 105.8 | 220 | 104.6 | JAX-TARAWA230_&_JAX-NORTHWDS115
304348 RKH 230 304638 WDSB T 230 1 | LN | 561.9 | 352.3 | 539 | 104.3 | 304348 RKH 230 304361 WEST END 230 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 226.9 | 125.7 | 221 | 102.7 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 594.1 | 184 | 590 | 100.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 999.7 | 647.6 | 1000 | 100 | 3Wnd: OPEN B$0832 WAKE#2 2
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 489.3 | 280.2 | 507 | 96.5 | 304348 RKH 230 304361 WEST END 230 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 212.9 | 88.7 | 221 | 96.3 | JAX-TARAWA230_&_JAX-NORTHWDS115
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 91.5 | 47.8 | 95 | 96.3 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 562.7 | 153.6 | 590 | 95.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 160.9 | 77.8 | 170 | 94.6 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 169.4 | 129.7 | 179 | 94.6 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178.8 | 68.8 | 190 | 94.1 | 304137 METHOD 115 304150 I-NCSU S 115 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.5 | 139.5 | 150 | 93 | ** Base Case **
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 174.6 | 107.4 | 190 | 91.9 | 304163 MILBURNE 115 304168 YONKERS 115 1
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 464.9 | 256.2 | 507 | 91.7 | 304348 RKH 230 304361 WEST END 230 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 98.4 | 13.5 | 108 | 91.1 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 431.7 | 324.1 | 478 | 90.3 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 178.1 | 79.9 | 201 | 88.6 | 304312 ASHEB E 115 304331 ASHEB 115 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 158.2 | 118.7 | 179 | 88.4 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.8 | 38.6 | 138 | 87.6 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 442 | 342.3 | 507 | 87.2 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 137.8 | 37.6 | 158 | 87.2 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137.9 | 70.1 | 159 | 86.7 | 304163 MILBURNE 115 304168 YONKERS 115 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 410.8 | 312.7 | 478 | 85.9 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 92.6 | 45.1 | 108 | 85.7 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 101 | 82.9 | 118 | 85.6 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 100.9 | 53.7 | 118 | 85.5 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 605.9 | 326.3 | 709 | 85.5 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 81.1 | 39.4 | 95 | 85.4 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 171.5 | 133.9 | 201 | 85.3 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 170.1 | 144.1 | 200 | 85 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on F12: PTI: Loading in %
Note on G12: PTI: Contingency Description

## 2016 BR1Dn TRM
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- THU, MAY 03 2007 8:46
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016\duk16s_PEC_Final-Br1DnTRM_CommitLincoln_v2.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 666.2 | 343.9 | 590 | 112.9 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 408.3 | 172.7 | 478 | 85.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 163.2 | 82.4 | 170 | 96 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 173.4 | 116.9 | 190 | 91.3 | 304163 MILBURNE 115 304168 YONKERS 115 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 97.8 | 17.1 | 108 | 90.5 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137 | 80 | 159 | 86.2 | 304163 MILBURNE 115 304168 YONKERS 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 176.1 | 35.7 | 158 | 111.5 | 304145 NEUSE 115 304185 FALLS 115 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178 | 57.9 | 190 | 93.7 | 304137 METHOD 115 304150 I-NCSU S 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 110.1 | 66.4 | 118 | 93.3 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 956 | 619.6 | 1000 | 95.6 | 3Wnd: OPEN B$0832 WAKE#2 2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.4 | 41.3 | 138 | 87.2 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 180.6 | 80.7 | 201 | 89.8 | 304312 ASHEB E 115 304331 ASHEB 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 492.9 | 313.1 | 539 | 91.4 | 304348 RKH 230 304361 WEST END 230 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 239.6 | 110.8 | 220 | 108.9 | JAX-TARAWA230_&_JAX-NORTHWDS115
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 222.5 | 93.9 | 221 | 100.7 | JAX-TARAWA230_&_JAX-NORTHWDS115
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 237.5 | 132 | 221 | 107.5 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 136.4 | 34.5 | 158 | 86.3 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 534 | 216.7 | 590 | 90.5 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 615.2 | 294.7 | 590 | 104.3 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 565.5 | 246.9 | 590 | 95.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.5 | 139.5 | 150 | 93 | ** Base Case **
304630 MULLINS 115 304632 MARION 115 1 | LN | 174.7 | 123.8 | 179 | 97.6 | 304587 E1-CHADP 230 304631 MARION 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 176 | 110.9 | 200 | 88 | 304631 MARION 230 304632 MARION 115 2
304632 MARION 115 304654 DILLON T 115 1 | LN | 112.1 | 83.7 | 97 | 115.5 | 304663 LATTA 230 304682 DILLMP T 230 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 113.2 | 67.7 | 108 | 104.8 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 116.8 | 70.9 | 108 | 108.1 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 86.9 | 44 | 95 | 91.4 | 304716 CAM TAP 115 304725 CAMDEN 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on F12: PTI: Loading in %
Note on G12: PTI: Contingency Description