## 2016-TRM+DK600-RSO SUMMARY
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 9:40
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_Duke600CPLE-HrDnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Worst Loading | Hr Loading% | Br1 Loading% | Yr Needed | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 704.6 | 285.6 | 590 | 117.4 | 117.4 | 111.6 | 2009 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 179.5 | 33.2 | 158 | 113.6 | 113.6 | 112.5 | 2010 | 304145 NEUSE 115 304185 FALLS 115 1
304632 MARION 115 304654 DILLON T 115 1 | LN | 107 | 81 | 97 | 113.1 | 110.3 | 113.1 | 2010 | 304663 LATTA 230 304682 DILLMP T 230 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 535.8 | 207.5 | 478 | 111.1 | 111.1 | 88.7 | 2011 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 229.2 | 105.4 | 220 | 108.5 | 104.2 | 108.5 | 2012 | JAX-TARAWA230_&_JAX-NORTHWDS115
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 654.4 | 236.2 | 590 | 108.9 | 108.9 | 103.2 | 2012 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304348 RKH 230 304638 WDSB T 230 1 | LN | 569.2 | 356.9 | 539 | 105.6 | 105.6 | 92.5 | 2013 | 304348 RKH 230 304361 WEST END 230 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 226 | 125.2 | 221 | 107.1 | 102.3 | 107.1 | 2013 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 115.2 | 68.9 | 108 | 106.6 | 106.6 | 102 | 2013 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 112.5 | 68.3 | 108 | 104.2 | 104.2 | 100.8 | 2014 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 211.9 | 88.2 | 221 | 100.3 | 95.9 | 100.3 | 2015 | JAX-TARAWA230_&_JAX-NORTHWDS115
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 605.7 | 187.9 | 590 | 100.6 | 100.6 | 94.9 | 2015 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 496.4 | 284.4 | 507 | 97.9 | 97.9 |  | 2017 | 304348 RKH 230 304361 WEST END 230 1
304630 MULLINS 115 304632 MARION 115 1 | LN | 174.6 | 123.7 | 179 | 97.5 |  | 97.5 | 2017 | 304587 E1-CHADP 230 304631 MARION 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 162.8 | 76.5 | 170 | 97 | 95.7 | 97 | 2018 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 180.5 | 64.9 | 190 | 95 | 95 | 94.2 | 2018 | 304137 METHOD 115 304150 I-NCSU S 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 100.4 | 55.5 | 118 | 95.3 | 85.1 | 95.3 | 2018 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1053.7 | 682 | 1000 | 105.4 | 105.4 | 100.8 | 2018 | 3Wnd: OPEN B$0832 WAKE#2 2
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 171 | 132.5 | 179 | 95.5 | 95.5 |  | 2018 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 575.1 | 157.6 | 590 | 95.3 | 95.3 | 89.7 | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 176 | 112.2 | 190 | 92.6 | 92.6 | 91.8 | 2019 | 304163 MILBURNE 115 304168 YONKERS 115 1
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 471.9 | 260.3 | 507 | 93.1 | 93.1 |  | 2019 | 304348 RKH 230 304361 WEST END 230 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.6 | 139.6 | 150 | 93 | 93 | 93 | 2019 | ** Base Case **
304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 486.9 | 338.4 | 539 | 90.3 | 90.3 |  | 2020 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 99.3 | 16.3 | 108 | 92 | 92 | 91 | 2020 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 181.7 | 81.4 | 201 | 91.5 | 90.4 | 91.5 | 2020 | 304312 ASHEB E 115 304331 ASHEB 115 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 436.6 | 330.7 | 478 | 91.3 | 91.3 | 85.4 | 2020 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 122.2 | 40.6 | 138 | 88.6 | 88.6 | 87.1 | 2021 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 455.3 | 350 | 507 | 89.8 | 89.8 |  | 2021 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 627.1 | 344.5 | 709 | 88.4 | 88.4 |  | 2021 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 139.1 | 37.7 | 158 | 88 | 88 | 87.2 | 2021 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 160 | 121.5 | 179 | 89.4 | 89.4 |  | 2021 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 423.9 | 321.8 | 478 | 88.7 | 88.7 |  | 2021 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 84.9 | 41.5 | 95 | 89.3 | 89.3 |  | 2021 | 304716 CAM TAP 115 304725 CAMDEN 115 1
42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 234.4 | 153.2 | 273 | 85.9 |  | 85.9 | 2022 | 42002 6WATEREE 230 304700 SUMTER 230 1
304047 WSP BUS 115 304406 ST PAULS 115 1 | LN | 101.4 | 75 | 119 | 85.2 | 85.2 |  | 2022 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
304145 NEUSE 115 304185 FALLS 115 1 | LN | 173 | 138.9 | 201 | 86.1 | 86.1 | 85.3 | 2022 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 139 | 74.7 | 159 | 87.4 | 87.4 | 86.6 | 2022 | 304163 MILBURNE 115 304168 YONKERS 115 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 100.6 | 80.6 | 118 | 85.2 | 85.2 |  | 2022 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 442.6 | 337.4 | 507 | 87.3 | 87.3 |  | 2022 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 162.2 | 98.5 | 190 | 85.4 | 85.4 |  | 2022 | 304378 RICHMOND 230 304415 RAEFORD 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 177.1 | 111.6 | 200 | 88.5 |  | 88.5 | 2025 | 304631 MARION 230 304632 MARION 115 2
304631 MARION 230 304632 MARION 115 2 | TR | 173.3 | 105.5 | 200 | 86.7 |  | 86.7 | 2025 | 304631 MARION 230 304632 MARION 115 1
304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 863.5 | 628.3 | 1000 | 86.4 |  | 86.4 | 2026 | 304183 WAKE 500 304391 CUMBERLD 500 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating

## Duke & Yadkin Overloads
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 8:22
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_Duke600CPLE-Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Br1 Loading% | Hr Loading% | Contingency
2512 HIGH RCK 100 2513 TUCKERTN 100 1 | LN | 96.8 | 81.3 | 102 | 94.9 | 99.7 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
2511 BADIN 100 2513 TUCKERTN 100 1 | LN | 101.8 | 83.7 | 116 |  | 87.8 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
836 8WOODLF 500 850 8PL GRDN 500 1 | LN | 2053.6 | 1784.2 | 1904.3 | 107.8 | 110.1 | 337 8NEWPORT 500 304377 RICHMOND 500 1
714 6BELEWS 230 842 6BOBWH W 230 2 | LN | 408.1 | 388.2 | 478 | 85.4 | 86.7 | 337 8NEWPORT 500 304377 RICHMOND 500 1
714 6BELEWS 230 841 6BOBWH B 230 1 | LN | 408.1 | 388.2 | 478 | 85.4 | 86.7 | 337 8NEWPORT 500 304377 RICHMOND 500 1
713 6BECKRDT 230 726 BECKRDIT 100 3 | TR | 229 | 229 | 251.9 | 90.9 | 90.9 | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 2 | TR | 228.8 | 228.8 | 252.8 | 90.5 | 90.5 | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 1 | TR | 223.4 | 223.4 | 260.3 | 85.8 | 85.8 | ** Base Case **
536 6BUCK 230 561 BUCK TIE 100 A4 | TR | 491.7 | 491.7 | 509 | 96.6 | 96.6 | ** Base Case **
333 6NEWPORT 230 541 6MORN ST 230 1 | LN | 476.1 | 412.5 | 478 | 99.6 | 99.9 | 337 8NEWPORT 500 304377 RICHMOND 500 1
333 6NEWPORT 230 541 6MORN ST 230 1 | LN | 412.5 | 412.5 | 436.9 | 94.4 | 94.9 | ** Base Case **
331 6ALLEN 230 341 ALLEN 100 6 | TR | 222.5 | 222.5 | 230.4 |  | 96.6 | ** Base Case **
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on F12: PTI: Loading in %
Note on G12: PTI: Loading in %
Note on H12: PTI: Contingency Description

## 2016-HrDnTRM+DK600-RSO
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 9:40
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_Duke600CPLE-HrDnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 704.6 | 285.6 | 590 | 117.4 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 535.8 | 207.5 | 478 | 111.1 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304047 WSP BUS 115 304406 ST PAULS 115 1 | LN | 101.4 | 75 | 119 | 85.2 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 486.9 | 338.4 | 539 | 90.3 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 162.8 | 76.5 | 170 | 95.7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 176 | 112.2 | 190 | 92.6 | 304163 MILBURNE 115 304168 YONKERS 115 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 99.3 | 16.3 | 108 | 92 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 173 | 138.9 | 201 | 86.1 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 139 | 74.7 | 159 | 87.4 | 304163 MILBURNE 115 304168 YONKERS 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 179.5 | 33.2 | 158 | 113.6 | 304145 NEUSE 115 304185 FALLS 115 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 180.5 | 64.9 | 190 | 95 | 304137 METHOD 115 304150 I-NCSU S 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 100.4 | 55.5 | 118 | 85.1 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 100.6 | 80.6 | 118 | 85.2 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1053.7 | 682 | 1000 | 105.4 | 3Wnd: OPEN B$0832 WAKE#2 2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 122.2 | 40.6 | 138 | 88.6 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 455.3 | 350 | 507 | 89.8 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 442.6 | 337.4 | 507 | 87.3 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 181.7 | 81.4 | 201 | 90.4 | 304312 ASHEB E 115 304331 ASHEB 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 569.2 | 356.9 | 539 | 105.6 | 304348 RKH 230 304361 WEST END 230 1
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 471.9 | 260.3 | 507 | 93.1 | 304348 RKH 230 304361 WEST END 230 1
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 496.4 | 284.4 | 507 | 97.9 | 304348 RKH 230 304361 WEST END 230 1
304369 FAY E 69.0 304389 P2-FAY E 230 1 | TR | 152 | 76.2 | 150 | 101.3 | 304369 FAY E 69.0 304389 P2-FAY E 230 2
304369 FAY E 69.0 304389 P2-FAY E 230 2 | TR | 152 | 75.7 | 150 | 101.3 | 304369 FAY E 69.0 304389 P2-FAY E 230 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 627.1 | 344.5 | 709 | 88.4 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 162.2 | 98.5 | 190 | 85.4 | 304378 RICHMOND 230 304415 RAEFORD 230 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 229.2 | 105.4 | 220 | 104.2 | JAX-TARAWA230_&_JAX-NORTHWDS115
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 211.9 | 88.2 | 221 | 95.9 | JAX-TARAWA230_&_JAX-NORTHWDS115
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 436.6 | 330.7 | 478 | 91.3 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 226 | 125.2 | 221 | 102.3 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 139.1 | 37.7 | 158 | 88 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 171 | 132.5 | 179 | 95.5 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 160 | 121.5 | 179 | 89.4 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 423.9 | 321.8 | 478 | 88.7 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 575.1 | 157.6 | 590 | 95.3 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 654.4 | 236.2 | 590 | 108.9 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 605.7 | 187.9 | 590 | 100.6 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.6 | 139.6 | 150 | 93 | ** Base Case **
304632 MARION 115 304654 DILLON T 115 1 | LN | 107 | 81 | 97 | 110.3 | 304663 LATTA 230 304682 DILLMP T 230 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 112.5 | 68.3 | 108 | 104.2 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 115.2 | 68.9 | 108 | 106.6 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 84.9 | 41.5 | 95 | 89.3 | 304716 CAM TAP 115 304725 CAMDEN 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating

## 2016-Br1DnTRM+DK600-RSO
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 8:22
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_Duke600CPLE-Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 234.4 | 153.2 | 273 | 85.9 | 42002 6WATEREE 230 304700 SUMTER 230 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 651 | 347.6 | 590 | 111.6 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 415.4 | 185.5 | 478 | 88.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 165 | 80.9 | 170 | 97 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 174.3 | 121.7 | 190 | 91.8 | 304163 MILBURNE 115 304168 YONKERS 115 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 98.3 | 20.4 | 108 | 91 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 171.5 | 138.8 | 201 | 85.3 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137.7 | 84.7 | 159 | 86.6 | 304163 MILBURNE 115 304168 YONKERS 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 177.8 | 31.9 | 158 | 112.5 | 304145 NEUSE 115 304185 FALLS 115 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178.9 | 53.6 | 190 | 94.2 | 304137 METHOD 115 304150 I-NCSU S 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 112.4 | 68.4 | 118 | 95.3 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1008 | 653.4 | 1000 | 100.8 | 3Wnd: OPEN B$0832 WAKE#2 2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.2 | 43.6 | 138 | 87.1 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 183.8 | 82 | 201 | 91.5 | 304312 ASHEB E 115 304331 ASHEB 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 498.5 | 316.4 | 539 | 92.5 | 304348 RKH 230 304361 WEST END 230 1
304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 863.5 | 628.3 | 1000 | 86.4 | 304183 WAKE 500 304391 CUMBERLD 500 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 238.8 | 110.4 | 220 | 108.5 | JAX-TARAWA230_&_JAX-NORTHWDS115
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 221.7 | 93.4 | 221 | 100.3 | JAX-TARAWA230_&_JAX-NORTHWDS115
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 408.1 | 268 | 478 | 85.4 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 236.6 | 131.4 | 221 | 107.1 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 137.7 | 34 | 158 | 87.2 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 529.8 | 220.4 | 590 | 89.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 603.6 | 298.4 | 590 | 103.2 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 558.2 | 250.6 | 590 | 94.9 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.6 | 139.6 | 150 | 93 | ** Base Case **
304630 MULLINS 115 304632 MARION 115 1 | LN | 174.6 | 123.7 | 179 | 97.5 | 304587 E1-CHADP 230 304631 MARION 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 177.1 | 111.6 | 200 | 88.5 | 304631 MARION 230 304632 MARION 115 2
304631 MARION 230 304632 MARION 115 2 | TR | 173.3 | 105.5 | 200 | 86.7 | 304631 MARION 230 304632 MARION 115 1
304632 MARION 115 304654 DILLON T 115 1 | LN | 109.7 | 82.3 | 97 | 113.1 | 304663 LATTA 230 304682 DILLMP T 230 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 108.8 | 67.3 | 108 | 100.8 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 110.2 | 64.6 | 108 | 102 | 304716 CAM TAP 115 304725 CAMDEN 115 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating