## AC Branch Violations
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- MON, MAY 07 2007 16:44
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_PJM200_Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Worst Loading | Br1 Loading% | Har Loading% | Year Needed | Ncon | Contingency
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 654.8 | 343.8 | 590 | 117.3 | 111 | 117.3 | 2009 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304632 MARION 115 304654 DILLON T 115 1 | LN | 109.6 | 82 | 97 | 113 | 113 | 108.3 | 2010 | 881 | 304663 LATTA 230 304682 DILLMP T 230 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 117.9 | 71.4 | 108 | 113 | 109.2 | 113 | 2010 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 176.9 | 34.3 | 158 | 112.5 | 112 | 112.5 | 2011 | 289 | 304145 NEUSE 115 304185 FALLS 115 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 239.7 | 110.9 | 220 | 108.9 | 108.9 | 104.7 | 2012 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 114.4 | 68.6 | 108 | 108.9 | 106 | 108.9 | 2012 | 938 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 606 | 294.7 | 590 | 108.7 | 102.7 | 108.7 | 2012 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 237.6 | 132 | 221 | 107.5 | 107.5 | 102.8 | 2013 | 724 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 407.9 | 172.9 | 478 | 107.3 | 85.3 | 107.3 | 2013 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304348 RKH 230 304638 WDSB T 230 1 | LN | 487 | 309.6 | 539 | 102.7 | 90.3 | 102.7 | 2014 | 534 | 304348 RKH 230 304361 WEST END 230 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 976.6 | 632.8 | 1000 | 101.5 | 97.7 | 101.5 | 2019 | 335 | 3Wnd: OPEN B$0832 WAKE#2 2
304183 WAKE 500 B$0832 WAKE#2 1.00 2 | TR | 976.3 | 632.4 | 1000 | 101.4 | 97.6 | 101.4 | 2020 | 334 | 3Wnd: OPEN B$0831 WAKE#1 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 222.6 | 94 | 221 | 100.7 | 100.7 | 96.5 | 2015 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 558.9 | 246.8 | 590 | 100.3 | 94.7 | 100.3 | 2015 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304190 WAKE 230 B$0831 WAKE#1 1.00 1 | TR | 951.6 | 622.7 | 1000 | 98.8 | 95.2 | 98.8 | 2021 | 335 | 3Wnd: OPEN B$0832 WAKE#2 2
304190 WAKE 230 B$0832 WAKE#2 1.00 2 | TR | 951.3 | 622.3 | 1000 | 98.8 | 95.1 | 98.8 | 2021 | 334 | 3Wnd: OPEN B$0831 WAKE#1 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 87.8 | 44.2 | 95 | 96.7 | 92.4 | 96.7 | 2018 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304630 MULLINS 115 304632 MARION 115 1 | LN | 172 | 122.1 | 179 | 96.1 | 96.1 |  | 2018 | 820 | 304587 E1-CHADP 230 304631 MARION 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 163.2 | 81.1 | 170 | 96 | 96 | 94.5 | 2018 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 529.3 | 216.6 | 590 | 95 | 89.7 | 95 | 2018 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 481.2 | 275.6 | 507 | 94.9 |  | 94.9 | 2019 | 534 | 304348 RKH 230 304361 WEST END 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178.2 | 57.1 | 190 | 94.2 | 93.8 | 94.2 | 2019 | 276 | 304137 METHOD 115 304150 I-NCSU S 115 1
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 168.4 | 129 | 179 | 94.1 |  | 94.1 | 2019 | 776 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 110.8 | 66.6 | 118 | 93.9 | 93.9 | 85.8 | 2019 | 300 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 173.6 | 117.8 | 190 | 92 | 91.4 | 92 | 2020 | 311 | 304163 MILBURNE 115 304168 YONKERS 115 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 97.9 | 17.8 | 108 | 91.2 | 90.6 | 91.2 | 2020 | 322 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 182.8 | 81.6 | 201 | 90.9 | 90.9 | 89.7 | 2020 | 489 | 304312 ASHEB E 115 304331 ASHEB 115 1
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 456.9 | 251.6 | 507 | 90.1 |  | 90.1 | 2020 | 534 | 304348 RKH 230 304361 WEST END 230 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 430.5 | 321.9 | 478 | 90.1 |  | 90.1 | 2020 | 680 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 157.2 | 118 | 179 | 87.8 |  | 87.8 | 2021 | 776 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 175.6 | 110.7 | 200 | 87.8 | 87.8 |  | 2025 | 845 | 304631 MARION 230 304632 MARION 115 2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.6 | 43.2 | 138 | 87.7 | 87.4 | 87.7 | 2021 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 469.5 | 331.7 | 539 | 87.1 |  | 87.1 | 2022 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 136.4 | 34.4 | 158 | 87.1 | 86.3 | 87.1 | 2022 | 770 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137.1 | 80.8 | 159 | 86.8 | 86.3 | 86.8 | 2022 | 311 | 304163 MILBURNE 115 304168 YONKERS 115 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 93.4 | 46 | 108 | 86.5 |  | 86.5 | 2022 | 938 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304631 MARION 230 304632 MARION 115 2 | TR | 172 | 104.6 | 200 | 86 | 86 |  | 2026 | 844 | 304631 MARION 230 304632 MARION 115 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 101.1 | 82.5 | 118 | 85.7 |  | 85.7 | 2022 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 81.4 | 38.9 | 95 | 85.7 |  | 85.7 | 2022 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 170.9 | 135.7 | 201 | 85.4 | 85 | 85.4 | 2022 | 298 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 407.6 | 310.1 | 478 | 85.3 |  | 85.3 | 2022 | 88 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
YADKIN & DUKE
2512 HIGH RCK 100 2513 TUCKERTN 100 1 | LN | 81.3 | 81.3 | 102 | 81.5 | 79.7 | 81.5 | 2024 |  | ** Base Case **
2511 BADIN 100 2513 TUCKERTN 100 1 | LN | 81.3 | 81.3 | 116 | 71.7 | 70.1 | 71.7 | 2028 |  | ** Base Case **
836 8WOODLF 500 850 8PL GRDN 500 1 | LN | 1965.5 | 1718 | 1904.3 | 105.2 | 103.2 | 105.2 | 2013 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
333 6NEWPORT 230 541 6MORN ST 230 1 | LN | 468.7 | 411.1 | 478 | 98.2 | 98.1 | 98.2 | 2017 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
536 6BUCK 230 561 BUCK TIE 100 A4 | TR | 490.2 | 490.2 | 509 | 96.3 | 96.3 | 96.3 | 2018 |  | ** Base Case **
331 6ALLEN 230 341 ALLEN 100 6 | TR | 219.1 | 219.1 | 230.4 | 95.1 | 95.1 | 94.9 | 2018 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 3 | TR | 227.5 | 227.5 | 251.9 | 90.3 | 90.3 | 90.3 | 2020 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 2 | TR | 227.3 | 227.3 | 252.8 | 89.9 | 89.9 | 89.9 | 2021 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 1 | TR | 222 | 222 | 260.3 | 85.3 | 85.3 | 85.2 | 2022 |  | ** Base Case **
Note on A13: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C13: PTI: Contingency MVA for Tran and Amp for Lines
Note on D13: PTI: Base Case Flow
Note on E13: PTI: Branch Rating
Note on G13: PTI: Loading in %
Note on H13: PTI: Loading in %
Note on J13: PTI: Contingency index
Note on K13: PTI: Contingency Description