## AC Branch Violations
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 13:14
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2_sc400_HarDnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Worst Loading | Br1 Loading% | Har Loading% | Year Needed | Ncon | Contingency
304632 MARION 115 304654 DILLON T 115 1 | LN | 117.7 | 88.4 | 97 | 126.4 | 126.4 | 121.4 | 2005 | 881 | 304663 LATTA 230 304682 DILLMP T 230 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 134.3 | 83.7 | 108 | 124.4 | 120.5 | 124.4 | 2006 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 712.5 | 285.2 | 590 | 120.8 | 114 | 120.8 | 2007 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 128.2 | 74.6 | 108 | 118.7 | 115.9 | 118.7 | 2008 | 938 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 541.6 | 209 | 478 | 113.3 | 89.2 | 113.3 | 2010 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 178.3 | 34.7 | 158 | 112.9 | 112.3 | 112.9 | 2010 | 289 | 304145 NEUSE 115 304185 FALLS 115 1
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 661.6 | 235.8 | 590 | 112.1 | 105.3 | 112.1 | 2011 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 104.2 | 56.1 | 95 | 109.7 | 105.4 | 109.7 | 2012 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 229.2 | 105.1 | 220 | 108.3 | 108.3 | 104.2 | 2012 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 225.5 | 124.9 | 221 | 106.9 | 106.9 | 102 | 2013 | 724 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 570.2 | 356.7 | 539 | 105.8 | 93.2 | 105.8 | 2013 | 534 | 304348 RKH 230 304361 WEST END 230 1
304630 MULLINS 115 304632 MARION 115 1 | LN | 154.4 | 110.4 | 179 | 104.6 | 104.6 | 86.3 | 2014 | 820 | 304587 E1-CHADP 230 304631 MARION 230 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 612.2 | 187.6 | 590 | 103.8 | 96.9 | 103.8 | 2014 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1034.2 | 669.8 | 1000 | 103.4 | 99.3 | 103.4 | 2019 | 335 | 3Wnd: OPEN B$0832 WAKE#2 2
304183 WAKE 500 B$0832 WAKE#2 1.00 2 | TR | 1033.8 | 669.4 | 1000 | 103.4 | 99.3 | 103.4 | 2019 | 334 | 3Wnd: OPEN B$0831 WAKE#1 1
304190 WAKE 230 B$0831 WAKE#1 1.00 1 | TR | 1006 | 658.7 | 1000 | 100.6 | 96.7 | 100.6 | 2020 | 335 | 3Wnd: OPEN B$0832 WAKE#2 2
304190 WAKE 230 B$0832 WAKE#2 1.00 2 | TR | 1005.7 | 658.3 | 1000 | 100.6 | 96.7 | 100.6 | 2020 | 334 | 3Wnd: OPEN B$0831 WAKE#1 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 211.9 | 88 | 221 | 100.1 | 100.1 | 95.9 | 2015 | 42 | JAX-TARAWA230_&_JAX-NORTHWDS115
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 93.7 | 47 | 95 | 98.6 | 94.4 | 98.6 | 2017 | 929 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 581.1 | 157.2 | 590 | 98.5 | 91.6 | 98.5 | 2017 | 41 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 497.3 | 284.4 | 507 | 98.1 |  | 98.1 | 2017 | 534 | 304348 RKH 230 304361 WEST END 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 162.3 | 77 | 170 | 96.7 | 96.7 | 95.5 | 2018 | 7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 104.1 | 51.1 | 108 | 96.4 | 93.6 | 96.4 | 2018 | 938 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 103 | 54.9 | 118 | 94.9 | 94.9 | 87.3 | 2019 | 300 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 179.5 | 66.4 | 190 | 94.5 | 94 | 94.5 | 2019 | 276 | 304137 METHOD 115 304150 I-NCSU S 115 1
304663 LATTA 230 304682 DILLMP T 230 1 | LN | 473.7 | 358.1 | 507 | 93.4 | 93.4 |  | 2019 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 472.7 | 260.4 | 507 | 93.2 |  | 93.2 | 2019 | 534 | 304348 RKH 230 304361 WEST END 230 1
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 175.3 | 110.1 | 190 | 92.2 | 91.6 | 92.2 | 2020 | 311 | 304163 MILBURNE 115 304168 YONKERS 115 1
304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 419.2 | 316.9 | 478 | 91.5 | 91.5 | 87.7 | 2020 | 39 | MARION-MARION(SCPSA)230_1&2
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 98.8 | 15 | 108 | 91.4 | 90.8 | 91.4 | 2020 | 322 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 182.6 | 158.6 | 200 | 91.3 | 87.7 | 91.3 | 2024 | 137 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 435.9 | 331.3 | 478 | 91.2 | 85.3 | 91.2 | 2020 | 680 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304631 MARION 230 304632 MARION 115 1 | TR | 174 | 109.6 | 200 | 91 | 91 | 87 | 2024 | 845 | 304631 MARION 230 304632 MARION 115 2
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 179.8 | 80.6 | 201 | 90.7 | 90.7 | 89.5 | 2020 | 489 | 304312 ASHEB E 115 304331 ASHEB 115 1
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 161.6 | 121.6 | 179 | 90.3 |  | 90.3 | 2020 | 776 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 426.4 | 311.2 | 478 | 89.2 | 89.2 |  | 2021 | 40 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 452.3 | 350.5 | 507 | 89.2 |  | 89.2 | 2021 | 578 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 631.7 | 345.1 | 709 | 89.1 |  | 89.1 | 2021 | 596 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304631 MARION 230 304632 MARION 115 2 | TR | 170.4 | 103.7 | 200 | 89.1 | 89.1 | 85.2 | 2024 | 844 | 304631 MARION 230 304632 MARION 115 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 425.5 | 323 | 478 | 89 |  | 89 | 2021 | 88 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304047 WSP BUS 115 304406 ST PAULS 115 1 | LN | 105.3 | 79.2 | 119 | 88.5 |  | 88.5 | 2021 | 28 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
304671 SARDIS 230 304674 OLANTA 230 1 | LN | 423.2 | 309.6 | 478 | 88.5 | 88.5 |  | 2021 | 39 | MARION-MARION(SCPSA)230_1&2
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 121.6 | 39.6 | 138 | 88.1 | 87.7 | 88.1 | 2021 | 22 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304629 NICHOLS 115 304630 MULLINS 115 1 | LN | 157.7 | 102.7 | 179 | 88.1 | 88.1 |  | 2021 | 820 | 304587 E1-CHADP 230 304631 MARION 230 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 138.5 | 38.5 | 158 | 87.7 | 86.9 | 87.7 | 2021 | 770 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 85 | 53.1 | 97 | 87.6 | 87.6 |  | 2021 | 881 | 304663 LATTA 230 304682 DILLMP T 230 1
304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 469.9 | 328.5 | 539 | 87.2 |  | 87.2 | 2022 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 138.4 | 72.7 | 159 | 87 | 86.5 | 87 | 2022 | 311 | 304163 MILBURNE 115 304168 YONKERS 115 1
304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 165.1 | 102.8 | 190 | 86.9 | 86.9 | 86.9 | 2022 | 581 | 304378 RICHMOND 230 304415 RAEFORD 230 1
304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 439.8 | 338.1 | 507 | 86.7 |  | 86.7 | 2022 | 578 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304676 KINGST N 230 304677 KINGSTRE 230 1 | LN | 482.3 | 367.9 | 557 | 86.6 | 86.6 |  | 2022 | 39 | MARION-MARION(SCPSA)230_1&2
304145 NEUSE 115 304185 FALLS 115 1 | LN | 172.1 | 136.5 | 201 | 85.6 | 85.2 | 85.6 | 2022 | 298 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 100.6 | 81.5 | 118 | 85.2 |  | 85.2 | 2022 | 11 | METHOD-PRISONF230_&_METHOD-BLUERDG230
YADKIN & DUKE
2512 HIGH RCK 100 2513 TUCKERTN 100 1 | LN | 101 | 84.2 | 102 | 99 | 95.8 | 99 | 2017 | 54 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
2511 BADIN 100 2513 TUCKERTN 100 1 | LN | 101.1 | 84.2 | 116 | 87.1 |  | 87.1 | 2022 | 54 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
836 8WOODLF 500 850 8PL GRDN 500 1 | LN | 2037.5 | 1790.6 | 1904.3 | 107 | 104.8 | 107 | 2013 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
333 6NEWPORT 230 541 6MORN ST 230 1 | LN | 474.2 | 415.5 | 478 | 99.2 | 98.8 | 99.2 | 2017 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
536 6BUCK 230 561 BUCK TIE 100 A4 | TR | 489.6 | 489.6 | 509 | 96.3 | 96.3 | 96.2 | 2018 |  | ** Base Case **
331 6ALLEN 230 341 ALLEN 100 6 | TR | 218.1 | 218.1 | 230.4 | 94.8 | 94.8 | 94.6 | 2019 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 3 | TR | 227.9 | 227.9 | 251.9 | 90.5 | 90.4 | 90.5 | 2020 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 2 | TR | 227.7 | 227.7 | 252.8 | 90.1 |  | 90.1 | 2020 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 1 | TR | 222.3 | 222.3 | 260.3 | 85.4 |  | 85.4 | 2022 |  | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 3 | TR | 230.6 | 227.9 | 271 | 85.1 |  | 85.1 | 2022 | 979 | 848 6PL GRDN 230 304332 ASHEB 230 1
714 6BELEWS 230 841 6BOBWH B 230 1 | LN | 406.9 | 387.7 | 478 | 85.1 |  | 85.1 | 2022 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
714 6BELEWS 230 842 6BOBWH W 230 2 | LN | 406.9 | 387.7 | 478 | 85.1 |  | 85.1 | 2022 | 970 | 337 8NEWPORT 500 304377 RICHMOND 500 1
Note on A13: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C13: PTI: Contingency MVA for Tran and Amp for Lines
Note on D13: PTI: Base Case Flow
Note on E13: PTI: Branch Rating
Note on G13: PTI: Loading in %
Note on H13: PTI: Loading in %
Note on J13: PTI: Contingency index
Note on K13: PTI: Contingency Description