## 2016-TRM+SCEG600 RSO Summary
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 11:41
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2-SCEG600Calpine-HrDnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Worst Loading | Hr Loading% | Br1 Loading% | Yr Needed | Contingency
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 138.8 | 86 | 108 | 128.5 | 128.5 | 124.5 | 2004 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 132.9 | 77.9 | 108 | 123.1 | 123.1 | 120.2 | 2006 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304632 MARION 115 304654 DILLON T 115 1 | LN | 116.1 | 87.2 | 97 | 124.3 | 119.7 | 124.3 | 2006 | 304663 LATTA 230 304682 DILLMP T 230 1
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 704 | 286.6 | 590 | 118.1 | 118.1 | 112.7 | 2008 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 108.5 | 57.9 | 95 | 114.2 | 114.2 | 109.9 | 2010 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 179.4 | 33.8 | 158 | 113.5 | 113.5 | 112.5 | 2010 | 304145 NEUSE 115 304185 FALLS 115 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 541 | 212.9 | 478 | 112.7 | 112.7 | 90.6 | 2010 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 654.3 | 237.1 | 590 | 109.6 | 109.6 | 104.2 | 2012 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 229 | 105.1 | 220 | 108.5 | 104.1 | 108.5 | 2012 | JAX-TARAWA230_&_JAX-NORTHWDS115
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 225.4 | 124.8 | 221 | 106.8 | 102 | 106.8 | 2013 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 573 | 359.1 | 539 | 106.3 | 106.3 | 93.7 | 2013 | 304348 RKH 230 304361 WEST END 230 1
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 97.8 | 48.7 | 95 | 103 | 103 | 98.7 | 2014 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304630 MULLINS 115 304632 MARION 115 1 | LN | 153.3 | 109.8 | 179 | 103.6 | 85.6 | 103.6 | 2014 | 304587 E1-CHADP 230 304631 MARION 230 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 108.8 | 54.3 | 108 | 100.8 | 100.8 | 97.8 | 2015 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 606.2 | 188.9 | 590 | 101.3 | 101.3 | 95.9 | 2015 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 211.7 | 87.9 | 221 | 100.2 | 95.8 | 100.2 | 2015 | JAX-TARAWA230_&_JAX-NORTHWDS115
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 500.1 | 286.7 | 507 | 98.6 | 98.6 | 85.3 | 2017 | 304348 RKH 230 304361 WEST END 230 1
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 576 | 158.6 | 590 | 96 | 96 | 90.7 | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 172.7 | 133.7 | 179 | 96.5 | 96.5 |  | 2018 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1052.5 | 681.2 | 1000 | 105.3 | 105.3 | 100.9 | 2018 | 3Wnd: OPEN B$0832 WAKE#2 2
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 101 | 55.6 | 118 | 95.6 | 85.6 | 95.6 | 2018 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 162.3 | 76.7 | 170 | 96.9 | 95.5 | 96.9 | 2018 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.6 | 139.6 | 150 | 93 | 93 | 93 | 2019 | ** Base Case **
304360 ELLERBE 230 304361 WEST END 230 1 | LN | 475.6 | 262.5 | 507 | 93.8 | 93.8 |  | 2019 | 304348 RKH 230 304361 WEST END 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 180.4 | 65.5 | 190 | 94.9 | 94.9 | 94.2 | 2019 | 304137 METHOD 115 304150 I-NCSU S 115 1
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 176.1 | 111.6 | 190 | 92.7 | 92.7 | 91.8 | 2019 | 304163 MILBURNE 115 304168 YONKERS 115 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 183.5 | 164 | 200 | 91.8 | 91.8 | 89.2 | 2020 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
304663 LATTA 230 304682 DILLMP T 230 1 | LN | 466.1 | 351.2 | 507 | 91.9 |  | 91.9 | 2020 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 161.7 | 122.6 | 179 | 90.3 | 90.3 |  | 2020 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 438.1 | 333.6 | 478 | 91.7 | 91.7 | 85.9 | 2020 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 180.6 | 81 | 201 | 90.9 | 89.8 | 90.9 | 2020 | 304312 ASHEB E 115 304331 ASHEB 115 1
304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 459.1 | 354.6 | 507 | 90.5 | 90.5 |  | 2020 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304265 E15-STED 115 304401 VANDER 115 1 | LN | 147.8 | 117.9 | 163 | 90.6 |  | 90.6 | 2020 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 99.3 | 15.8 | 108 | 91.9 | 91.9 | 91 | 2020 | 304174 I-PERSTP 115 304181 GARNER E 115 1
42003 3EASTOVE 115 304696 SHAW TAP 115 1 | LN | 105.4 | 39.6 | 118 | 91.5 | 89.3 | 91.5 | 2020 | SUMT-SUMMRTN230_&_SUMT-WATEREE230
42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 242.3 | 137.6 | 273 | 90.6 | 88.8 | 90.6 | 2020 | 42002 6WATEREE 230 304700 SUMTER 230 1
304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 429.3 | 326 | 478 | 89.8 | 89.8 |  | 2021 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 139.4 | 38.2 | 158 | 88.2 | 88.2 | 87.5 | 2021 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 635.1 | 349 | 709 | 89.6 | 89.6 |  | 2021 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 446.5 | 342.1 | 507 | 88.1 | 88.1 |  | 2021 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 122.1 | 39.7 | 138 | 88.5 | 88.5 | 87.1 | 2021 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 139.1 | 74.1 | 159 | 87.5 | 87.5 | 86.6 | 2021 | 304163 MILBURNE 115 304168 YONKERS 115 1
304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 478.6 | 333.2 | 539 | 88.8 | 88.8 |  | 2021 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304047 WSP BUS 115 304406 ST PAULS 115 1 | LN | 105.1 | 78.7 | 119 | 88.3 | 88.3 |  | 2021 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
42002 6WATEREE 230 304700 SUMTER 230 1 | LN | 438.7 | 373 | 500 | 89.7 | 87.7 | 89.7 | 2021 | 304018 ROB 2 N 230 304864 ROB #2 22.0 1
304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 418.7 | 304.3 | 478 | 87.6 |  | 87.6 | 2021 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304685 ALCOLU 115 304686 SUMTER 115 1 | LN | 103.1 | 20.3 | 119 | 86.6 |  | 86.6 | 2022 | 43008 6KNGSTRE 230 304677 KINGSTRE 230 1
304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 413.5 | 302.3 | 478 | 86.5 |  | 86.5 | 2022 | MARION-MARION(SCPSA)230_1&2
304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 82.8 | 51.6 | 97 | 85.4 |  | 85.4 | 2022 | 304663 LATTA 230 304682 DILLMP T 230 1
304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 165.7 | 102.8 | 190 | 87.3 | 87.2 | 87.3 | 2022 | 304378 RICHMOND 230 304415 RAEFORD 230 1
304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 100.7 | 81.2 | 118 | 85.4 | 85.4 |  | 2022 | METHOD-PRISONF230_&_METHOD-BLUERDG230
304145 NEUSE 115 304185 FALLS 115 1 | LN | 172.8 | 138.2 | 201 | 86 | 86 | 85.3 | 2022 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304631 MARION 230 304632 MARION 115 1 | TR | 172.7 | 108.8 | 200 | 90.3 | 86.3 | 90.3 | 2024 | 304631 MARION 230 304632 MARION 115 2
304631 MARION 230 304632 MARION 115 2 | TR | 172.7 | 108.8 | 200 | 88.4 |  | 88.4 | 2025 | 304631 MARION 230 304632 MARION 115 2
304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 851.3 | 609.7 | 1000 | 85.1 |  | 85.1 | 2026 | 304183 WAKE 500 304391 CUMBERLD 500 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on G12: PTI: Loading in %
Note on H12: PTI: Loading in %
Note on J12: PTI: Contingency Description

## Duke & Yadkin Overloads
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 9:54
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2-SCEG600Calpine-Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Br1 Loading% | Hr Loading% | Contingency
2512 HIGH RCK 100 2513 TUCKERTN 100 1 | LN | 97.4 | 82.2 | 102 | 95.5 | 99.5 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
2511 BADIN 100 2513 TUCKERTN 100 1 | LN | 101.7 | 84.5 | 116 |  | 87.7 | 304004 TIL 1-4H 115 304302 E14-TROY 115 1
836 8WOODLF 500 850 8PL GRDN 500 1 | LN | 2024.4 | 1765.9 | 1904.3 | 106.3 | 108.4 | 337 8NEWPORT 500 304377 RICHMOND 500 1
714 6BELEWS 230 842 6BOBWH W 230 2 | LN | 414.7 | 384.6 | 478 | 86.8 | 85.6 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
714 6BELEWS 230 841 6BOBWH B 230 1 | LN | 414.7 | 384.6 | 478 | 86.8 | 85.6 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
713 6BECKRDT 230 726 BECKRDIT 100 3 | TR | 228.1 | 228.1 | 251.9 | 90.6 | 90.5 | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 2 | TR | 227.9 | 227.9 | 252.8 | 90.2 | 90.1 | ** Base Case **
713 6BECKRDT 230 726 BECKRDIT 100 1 | TR | 222.6 | 222.6 | 260.3 | 85.5 | 85.5 | ** Base Case **
536 6BUCK 230 561 BUCK TIE 100 A4 | TR | 490.6 | 490.6 | 509 | 96.4 | 96.4 | ** Base Case **
333 6NEWPORT 230 541 6MORN ST 230 1 | LN | 480 | 419.1 | 478 | 100.4 | 100.6 | 337 8NEWPORT 500 304377 RICHMOND 500 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating
Note on G12: PTI: Loading in %

## 2016-Br1DnTRM+SCEG600 RSO
AC Branch Violations
PSS(tm)MUST 8.3.1 -- Managing and Utilizing System Transmission -- TUE, MAY 08 2007 9:54
2016 NCPWG SUMMER PEAK BASE CASE 04-03-07
2007 DUK16S/2006 VST16S/2016 PEC_TPU/2006 NCTPC/PG-ASHEBORO
Case.File J:\NC Stakeholders\PWG2007-2012-2016Study\Cases\2016 RSO\duk16s_PEC_Final_v2-SCEG600Calpine-Br1DnTRM.sav
Subsys.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC_subsystem.sub
Monit.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Duke+PEC+Yadkin_monitor.mon
Contin.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\PEC-East_contingencies.con
Exclud.File J:\NC Stakeholders\PWG2007-2012-2016Study\Files\ACCC Files\Eastern System--renumbered-East&West.EXC
Branches with MVA flow more than 85.0 % of nominal rating
** From bus ** ** To bus ** CKT | Type | ContMVA | BaseFlow | Rating | Loading% | Contingency
304732 ELGIN T 115 304734 WATRE 115 1 | LN | 93.8 | 45.7 | 95 | 98.7 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 104.4 | 54.6 | 95 | 109.9 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 134.5 | 82.4 | 108 | 124.5 | 304716 CAM TAP 115 304725 CAMDEN 115 1
304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 178.3 | 159.5 | 200 | 89.2 | 43014 6S BETH 230 304057 DARL CO 230 1
304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 129.8 | 77 | 108 | 120.2 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 105.7 | 53.5 | 108 | 97.8 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
304685 ALCOLU 115 304686 SUMTER 115 1 | LN | 103.1 | 20.3 | 119 | 86.6 | 43008 6KNGSTRE 230 304677 KINGSTRE 230 1
304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 413.5 | 302.3 | 478 | 86.5 | MARION-MARION(SCPSA)230_1&2
304663 LATTA 230 304682 DILLMP T 230 1 | LN | 466.1 | 351.2 | 507 | 91.9 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304632 MARION 115 304654 DILLON T 115 1 | LN | 120.5 | 89.7 | 97 | 124.3 | 304663 LATTA 230 304682 DILLMP T 230 1
304631 MARION 230 304632 MARION 115 2 | TR | 176.7 | 107.6 | 200 | 88.4 | 304631 MARION 230 304632 MARION 115 1
304631 MARION 230 304632 MARION 115 1 | TR | 180.5 | 113.8 | 200 | 90.3 | 304631 MARION 230 304632 MARION 115 2
304630 MULLINS 115 304632 MARION 115 1 | LN | 186.5 | 131 | 179 | 104.2 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304629 NICHOLS 115 304630 MULLINS 115 1 | LN | 156.6 | 101.9 | 179 | 87.5 | 304587 E1-CHADP 230 304631 MARION 230 1
304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 139.6 | 139.6 | 150 | 93 | ** Base Case **
304587 E1-CHADP 230 304631 MARION 230 1 | LN | 613.4 | 411.3 | 637 | 96.3 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304587 E1-CHADP 230 304600 WHITEVIL 230 1 | LN | 562.2 | 373.8 | 637 | 88.3 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 584.5 | 251.9 | 590 | 95.9 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 635.6 | 299.7 | 590 | 104.2 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 552.2 | 221.7 | 590 | 90.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 138.3 | 34.1 | 158 | 87.5 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 236.1 | 131.1 | 221 | 106.8 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 410.4 | 271.1 | 478 | 85.9 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 221.5 | 93.1 | 221 | 100.2 | JAX-TARAWA230_&_JAX-NORTHWDS115
304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 238.6 | 110.1 | 220 | 108.5 | JAX-TARAWA230_&_JAX-NORTHWDS115
304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 82.8 | 51.6 | 97 | 85.4 | 304663 LATTA 230 304682 DILLMP T 230 1
304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 165.9 | 99.7 | 190 | 87.3 | 304378 RICHMOND 230 304415 RAEFORD 230 1
304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 851.3 | 609.7 | 1000 | 85.1 | 304183 WAKE 500 304391 CUMBERLD 500 1
304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 432.3 | 248.1 | 507 | 85.3 | 304348 RKH 230 304361 WEST END 230 1
304348 RKH 230 304638 WDSB T 230 1 | LN | 504.8 | 320.1 | 539 | 93.7 | 304348 RKH 230 304361 WEST END 230 1
304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 182.7 | 81.6 | 201 | 90.9 | 304312 ASHEB E 115 304331 ASHEB 115 1
304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 120.2 | 42.5 | 138 | 87.1 | BISCOEW-BISCOESUB115_&_BISCOEW-SPRINGT_115
304265 E15-STED 115 304401 VANDER 115 1 | LN | 147.8 | 117.9 | 163 | 90.6 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1009.4 | 654.3 | 1000 | 100.9 | 3Wnd: OPEN B$0832 WAKE#2 2
304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 112.9 | 68.5 | 118 | 95.6 | 304156 ROL/SQ T 230 304190 WAKE 230 1
304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 178.9 | 54.2 | 190 | 94.2 | 304137 METHOD 115 304150 I-NCSU S 115 1
304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 177.8 | 32.4 | 158 | 112.5 | 304145 NEUSE 115 304185 FALLS 115 1
304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 137.7 | 84.2 | 159 | 86.6 | 304163 MILBURNE 115 304168 YONKERS 115 1
304145 NEUSE 115 304185 FALLS 115 1 | LN | 171.5 | 138.3 | 201 | 85.3 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
304137 METHOD 115 304153 TRYON HL 115 1 | LN | 98.3 | 19.8 | 108 | 91 | 304174 I-PERSTP 115 304181 GARNER E 115 1
304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 174.3 | 121.2 | 190 | 91.8 | 304163 MILBURNE 115 304168 YONKERS 115 1
304111 E18-WK F 115 304185 FALLS 115 1 | LN | 164.8 | 81 | 170 | 96.9 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 418.7 | 304.3 | 478 | 87.6 | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
304046 WSPN BUS 230 304582 DELCO 230 1 | LN | 425 | 239.2 | 478 | 88.9 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 435.6 | 191.7 | 478 | 90.6 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 688 | 349 | 590 | 112.7 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
42003 3EASTOVE 115 304696 SHAW TAP 115 1 | LN | 108 | 40.6 | 118 | 91.5 | SUMT-SUMMRTN230_&_SUMT-WATEREE230
42002 6WATEREE 230 304700 SUMTER 230 1 | LN | 448.7 | 383 | 500 | 89.7 | 304018 ROB 2 N 230 304864 ROB #2 22.0 1
42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 247.4 | 140 | 273 | 90.6 | 42002 6WATEREE 230 304700 SUMTER 230 1
Note on A12: PTI: ** From bus ** ** To bus ** Circuit Type
Note on C12: PTI: Contingency MVA for Tran and Amp for Lines
Note on D12: PTI: Base Case Flow
Note on E12: PTI: Branch Rating