## PEC Reliability&RSO-Reduced
| 2007-08-07 |  |  |  |  | Base TRM |  |  |  | Import - 2016 RSO | [19 empty] | Generation - 2016 RSO
[6 empty] | 2012 |  | 2016 |  | Dk-1200MW |  | Dk-1200MW+Imprt Prjcts+3DkPrjcts |  | Dk-1200MW+ Bynum500+ 3DkPrjcts |  | Dk-1200MW+ Erwin500+ 3DkPrjcts |  | PJM-200MW |  |  | SC- 400MW |  |  | Dk-600MW |  |  | SG-Calpine 600MW |  |  | Laurinburg 450MW |  |  | Cumbrlnd/Fay 450MW |  |  | Wilson 450MW |  |  | Selma 450MW |  |  | Wspn 600MW
Item # | NOTES | LINE / ELEMENT | ** From bus ** ** To bus ** CKT | Type | Rating | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | Contingency
1 | SCEG ONLY | SUMTER - SCE&G CANADYS 230KV | 42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 273 |  |  |  |  | 95.2 | 2018 | 93.9 | 2019 | 93.5 | 2019 | 94.3 | 2019 | [6 empty] | 85.9 | 2022 | 85.9 | 90.6 | 2020 | 90.6 | [15 empty] | 42002 6WATEREE 230 304700 SUMTER 230 1
2 | SCEG ONLY | SUMTER - SCE&G EASTOVER 115KV | 42003 3EASTOVE 115 304696 SHAW TAP 115 1 | LN | 118 |  |  |  |  | 88.9 | 2021 |  |  | 87.1 | 2022 | 87.9 | 2021 | [9 empty] | 91.5 | 2020 | 91.5 | [15 empty] | SUMT-SUMMRTN230_&_SUMT-WATEREE230
3 | 1200MW +BYNUM 500 Only- Can Uprate to 1077MVA | HARRIS-SILER CITY 230kV | 304009 HARRIS1N 230 304337 BYNUM T 230 1 | LN | 793 | [8 empty] | 96.8 | 2018 | [29 empty] | PARKWOOD-BYNUM 500 KV LINE
4 | LOCAL | BR #2 - DELCO 230KV WEST | 304020 BRUN 2 N 230 304604 E1-STHPT 230 1 | LN | 478 | 88.7 | 2017 | [37 empty] | 304020 BRUN 2 N 230 304615 BARCRK E 230 1
5 | LOCAL-Project 2017 | SUTTON-CASTLE HAYNE 115KV LINE #2 | 304035 SUT 1-2F 115 304545 CASTLE H 115 2 | LN | 131 | 85.4 | 2018 | [37 empty] | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
6 | LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 590 | 107.3 | 2009 | 117.7 | 2008 | 117.9 | 2008 | 117.5 | 2009 | 120 | 2008 | 118.2 | 2008 | 117.3 | 2009 | -0.4 | 120.8 | 2007 | 3.1 | 117.4 | 2009 | -0.3 | 118.1 | 2008 | 0.4 | 118 | 2008 | 0.3 | 119.6 | 2008 | 1.9 | 116.3 | 2009 | -1.4 | 116.6 | 2009 | -1.1 | 119.5 | 2008 | 1.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
7 | LOCAL OP PROCEDURE | SUTTON PLANT - DELCO 230KV | 304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 478 | 90.8 | 2016 | 108 | 2012 | 111.7 | 2011 | 110.2 | 2011 | 115.5 | 2009 | 107.7 | 2012 | 107.3 | 2013 | -0.7 | 113.3 | 2010 | 5.3 | 111.1 | 2011 | 3.1 | 112.7 | 2010 | 4.7 | 111.9 | 2011 | 3.9 | 112.4 | 2011 | 4.4 | 106 | 2013 | -2 | 105.7 | 2013 | -2.3 | 114.1 | 2010 | 6.1 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
8 | WSPN GEN ONLY | WEATHERSPOON 230/115kV | 304046 WSPN BUS 230 304047 WSP BUS 115 1 | TR | 200 | [36 empty] | 91.5 | 2023 | 91.5 | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1
9 | WSPN GEN ONLY | WSPN PLANT - FAYETTEVILLE 230KV | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1 | LN | 478 | [36 empty] | 85.9 | 2022 | 85.9 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
10 | SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 478 | [15 empty] | 89.2 | 2021 |  |  |  |  | 87.6 | 2021 | 87.6 | [15 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
11 | WSPN GEN ONLY | WSPN PLANT - RAEFORD 230KV SUB 115KV | 304047 WSP BUS 115 304432 PA-LMB#2 115 1 | LN | 133 | [36 empty] | 89.2 | 2021 | 89.2 | 304378 RICHMOND 230 304415 RAEFORD 230 1
12 | 1200MW ONLY- OP PROC | CAPE FEAR PLANT-ERWIN 115KV | 304052 CAPE F F 115 304220 LILINGTN 115 1 | LN | 86 |  |  |  |  | 89.7 | 2021 | 88.7 | 2021 | 95.8 | 2018 | [29 empty] | 304009 HARRIS1N 230 304204 DUNCAN 230 1
13 | 1200MW ONLY | DURHAM-FALLS 230KV | 304078 WD VALLY 230 304117 DURHAM 230 1 | LN | 541 | [39 empty] | ROX-FALLS230_&_FALLS23-CGROX230
14 | PROJECT IN 2014 | FRANKLINTON - HENDERSON 115KV | 304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 201 | 86.4 | 2018 | [37 empty] | 304111 E18-WK F 115 304185 FALLS 115 1
15 | OUTSIDE HORIZON | CARY REGENCY PARK - DURHAM 230KV | 304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 539 |  |  |  |  | 95.6 | 2018 |  |  | 75 | 2026 | 83 | 2023 | 87.1 | 2022 | 87.1 | 87.2 | 2022 | 87.2 | 90.3 | 2020 | 90.3 | 88.8 | 2021 | 88.8 | 86.4 | 2022 | 86.4 | 85.6 | 2022 | 85.6 | 87.3 | 2022 | 87.3 |  |  |  | 85.6 | 2022 | 85.6 | METHOD-PRISONF230_&_METHOD-BLUERDG230
16 | SELMA GEN ONLY | SELMA 230/115kV Bank #1 & 2 (exact same) | 304177 SELMA 115 304192 SELMA 230 1 | TR | 200 | [33 empty] | 91.1 | 2024 | 91.1 |  |  |  | 304177 SELMA 115 304192 SELMA 230 2
17 | PROJECT IN 2013 | FALLS 230/115kV Bank #1 | 304182 FALLS 230 304185 FALLS 115 1 | TR | 300 | 103.1 | 2015 | [37 empty] | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
18 | PROJECT | WAKE 500/230 KV BANKS | 304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1000 | 94.7 | 2018 | 100 | 2020 | 107.9 | 2017 |  |  | 104 | 2018 | 87.3 | 2025 | 101.5 | 2019 | 1.5 | 103.4 | 2019 | 3.4 | 105.4 | 2018 |  | 105.3 | 2018 | 5.3 | 103.5 | 2019 | 3.5 | 104.4 | 2018 | 4.4 | 96.6 | 2021 | -3.4 | 94.9 | 2022 | -5.1 | 103 | 2019 | 3 | 3Wnd: OPEN B$0832 WAKE#2 2
19 | OP. PROC. | CLINTON - VANDER 115KV | 304265 E15-STED 115 304401 VANDER 115 1 | LN | 163 | 85 | 2018 |  |  | 86.3 | 2022 |  |  | 86.1 | 2022 | 85.6 | 2022 | [9 empty] | 90.6 | 2020 | 90.6 | 86.2 | 2022 | 86.2 | 87.5 | 2021 | 87.5 | [6 empty] | 86.7 | 2022 | 86.7 | 304196 ERWIN 230 304197 DUNN 230.0 1
20 | OUTSIDE HORIZON | ASHEBORO EAST - BISCOE 230KV SUB 115KV | 304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 138 |  |  | 87.6 | 2021 | 88.2 | 2021 | 87.7 | 2021 | 87.2 | 2022 | 87.6 | 2021 | 87.7 | 2021 | 0.1 | 88.1 | 2021 | 0.5 | 88.6 | 2021 | 1 | 88.5 | 2021 | 0.9 | 87.7 | 2021 | 0.1 | 87.7 | 2021 | 0.1 | 87.5 | 2021 | -0.1 | 87.5 | 2021 | -0.1 | 87.9 | 2021 | 0.3 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
21 | 1200MW +BYNUM 500 Only | CAPE FEAR-BISCOE 115kV | 304305 SPRING T 115 304428 BISCOE W 115 1 | LN | 198 | [6 empty] | 86.1 | 2022 | 88.1 | 2021 | 85.3 | 2022 | [27 empty] | 304009 HARRIS1N 230 304337 BYNUM T 230 1
22 | PROJECT IN PLACE | ASHEBORO-ASHEBORO EAST NORTH 115kV LINE | 304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 201 | [8 empty] | 93.4 | 2019 | 91.6 | 2020 | [27 empty] | 304312 ASHEB E 115 304331 ASHEB 115 1
23 | REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 507 |  |  | 87.2 | 2022 | 91.9 | 2020 | 90.8 | 2020 |  |  | 89.3 | 2021 |  |  |  | 89.2 | 2021 | 2 | 89.8 | 2021 | 2.6 | 90.5 | 2020 | 3.3 | 91.6 | 2020 | 4.4 | 86 | 2022 | -1.2 | [6 empty] | 88.7 | 2021 | 1.5 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
24 | REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 507 | [6 empty] | 88.3 | 2021 |  |  | 86.8 | 2022 |  |  |  | 86.7 | 2022 | 86.7 | 87.3 | 2022 | 87.3 | 88.1 | 2021 | 88.1 | 89.1 | 2021 | 89.1 | [9 empty] | 86.2 | 2022 | 86.2 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
25 | OUTSIDE HORIZON | FAYETTEVILLE-ROCKINGHAM 230kV | 304348 RKH 230 304355 HAMLET 230 1 | LN | 507 |  |  |  |  | 87.4 | 2022 | 88.5 | 2021 | 85.9 | 2022 | 87.5 | 2021 | [27 empty] | 304377 RICHMOND 500 304391 CUMBERLD 500 1
26 | LAURNBRG GEN ONLY | RICHMOND - ROCKINGHAM 230KV | 304348 RKH 230 304378 RICHMOND 230 1 | LN | 1014 | [24 empty] | 86.5 | 2022 | 86.5 | [12 empty] | 304348 RKH 230 304378 RICHMOND 230 2
27 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304348 RKH 230 304638 WDSB T 230 1 | LN | 539 | 96.6 | 2014 | 104.3 | 2014 | 106.4 | 2013 | 105 | 2014 | 100.4 | 2015 | 101.9 | 2015 | 102.7 | 2014 | -1.6 | 105.8 | 2013 | 1.5 | 105.6 | 2013 | 1.3 | 106.3 | 2013 | 2 | 106.8 | 2013 | 2.5 | 104.3 | 2014 | 0 | 101.9 | 2015 | -2.4 | 101.5 | 2015 | -2.8 | 105.4 | 2013 | 1.1 | 304348 RKH 230 304361 WEST END 230 1
28 | 1200MW +BYNUM 500 Only | LILESVILLE-RKH BLK/WHT | 304350 PH SH 1B 230 304985 LILES SS 230 1 | LN | 398 |  |  |  |  | 89.9 | 2021 |  |  | 85.6 | 2022 | 91.6 | 2020 | [27 empty] | 337 8NEWPORT 500 304377 RICHMOND 500 1
29 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304361 WEST END 230 1 | LN | 507 | 85.1 | 2018 | 91.7 | 2020 | 93.7 | 2019 | 92.5 | 2019 | 87.7 | 2021 | 89.2 | 2021 | 90.1 | 2020 | -1.6 | 93.2 | 2019 | 1.5 | 93.1 | 2019 | 1.4 | 93.8 | 2019 | 2.1 | 94.4 | 2019 | 2.7 | 91.8 | 2020 | 0.1 | 89.3 | 2021 | -2.4 | 88.8 | 2021 | -2.9 | 92.9 | 2019 | 1.2 | 304348 RKH 230 304361 WEST END 230 1
30 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 507 | 89.5 | 2017 | 96.5 | 2018 | 98.6 | 2017 | 97.3 | 2018 | 92.5 | 2019 | 94 | 2019 | 94.9 | 2019 | -1.6 | 98.1 | 2017 | 1.6 | 97.9 | 2017 | 1.4 | 98.6 | 2017 | 2.1 | 99.2 | 2017 | 2.7 | 96.6 | 2018 | 0.1 | 94.1 | 2019 | -2.4 | 93.6 | 2019 | -2.9 | 97.7 | 2017 | 1.2 | 304348 RKH 230 304361 WEST END 230 1
31 | CUMB/WSPN GEN ONLY | FAYETTEVILLE - FT. BRG WODRUFF ST. 230KV | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1 | LN | 793 | [27 empty] | 87.9 | 2021 | 87.9 | [6 empty] | 86.6 | 2022 | 86.6 | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1
32 | PROJECT NEEDED | FAYETTEVILLE - FAYETTEVILLE EAST 230KV | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 709 | 92.5 | 2015 | 85.5 | 2022 | 99.1 | 2017 | 95.6 | 2018 | 92.1 | 2020 | 80 | 2024 |  |  |  | 89.1 | 2021 | 3.6 | 88.4 | 2021 | 2.9 | 89.6 | 2021 | 4.1 | 93.8 | 2019 | 8.3 | 97.7 | 2017 | 12.2 | 87.6 | 2021 | 2.1 | 85.4 | 2022 | -0.1 | 96 | 2018 | 10.5 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
33 | OUTSIDE HORIZON | CUMBERLAND 500/230kV BANK | 304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 1000 |  |  |  |  | 91.2 | 2024 | 91.1 | 2024 | 89.4 | 2024 | 90.1 | 2024 | [6 empty] | 86.4 | 2026 | 86.4 | 85.1 | 2026 | 85.1 | [15 empty] | 304183 WAKE 500 304391 CUMBERLD 500 1
34 | CUMB/WSPN GEN ONLY | FAYETTEVILLE - VANDER 115KV SOUTH | 304392 FAY 115 304401 VANDER 115 1 | LN | 163 | [27 empty] | 85.7 | 2022 | 85.7 | [6 empty] | 85 | 2022 | 85 | 304392 FAY 115 304402 E15-VAND 115 1
35 | WSPN GEN ONLY | WSPN PL. - FAY'VILLE DUP. SW. ST. 115KV | 304406 ST PAULS 115 304412 F DUP SW 115 1 | LN | 119 | [36 empty] | 87 | 2022 | 87 | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1
36 | LAURNBRG GEN ONLY | RAEFORD 230KV SUB - WAGRAM 115KV | 304411 RAEFORD 115 304416 MAXAPT T 115 1 | LN | 190 | [24 empty] | 87.2 | 2022 | 87.2 | [12 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
37 | OUTSIDE HORIZON | RAEFORD 230KV SUB - WAGRAM 115KV | 304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 190 |  |  |  |  | 86.5 | 2022 | 86.4 | 2022 | [7 empty] | 86.9 | 2022 | 86.9 | 85.4 | 2022 | 85.4 | 87.3 | 2022 | 87.3 | 100.3 | 2015 | 100.3 | [9 empty] | 85.3 | 2022 | 85.3 | 304378 RICHMOND 230 304415 RAEFORD 230 1
38 | LAURNBRG GEN ONLY | LAURINBURG - WAGRAM 115KV | 304419 WAGRAMSW 115 304421 LAURINBG 115 1 | LN | 201 | [24 empty] | 95.8 | 2018 | 95.8 | [12 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
39 | PROJECT IN 2013 | LAURINBURG 230/115kV BANK #1 & 2 (same) | 304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 200 | 93.7 | 2019 | [37 empty] | 304421 LAURINBG 115 304424 LAURINBG 230 2
40 | OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 97 | [15 empty] | 87.6 | 2021 | 87.6 |  |  |  | 85.4 | 2022 | 85.4 | [15 empty] | 304663 LATTA 230 304682 DILLMP T 230 1
41 | WSPN GEN ONLY | CASTLE HAYNE-JACSONVILLE 230KV | 304556 TOPSL T 230 304564 SCOTT T 230 1 | LN | 478 | [36 empty] | 85.2 | 2022 | 85.2 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
42 | SC-ONLY | MARION - WHITEVILLE 115KV | 304629 NICHOLS 115 304630 MULLINS 115 1 | LN | 179 | [15 empty] | 88.1 | 2021 | 88.1 | [21 empty] | 304587 E1-CHADP 230 304631 MARION 230 1
43 | SCPSA JOINT STUDY | MARION - WHITEVILLE 115KV | 304630 MULLINS 115 304632 MARION 115 1 | LN | 179 | 87.5 | 2017 | 97.6 | 2017 | 97 | 2018 |  |  | 95.6 | 2018 |  |  | 96.1 | 2018 | -1.5 | 104.6 | 2014 | 7 | 97.5 |  | -0.1 | 103.6 | 2014 | 6 | 100.9 | 2015 | 3.3 | 94.2 | 2019 | -3.4 | 95.7 | 2018 | -1.9 | 95.4 | 2018 | -2.2 | 99.1 | 2017 | 1.5 | 304587 E1-CHADP 230 304631 MARION 230 1
44 | OUTSIDE HORIZON | MARION 230/115 BANK #1 & 2 (same) | 304631 MARION 230 304632 MARION 115 1 | TR | 200 |  |  | 88 | 2025 | 89.2 | 2021 |  |  | 88.7 | 2025 | 88.5 | 2025 | 87.8 | 2025 | -0.2 | 91 | 2024 | 3 | 88.5 | 2025 | 0.5 | 90.3 | 2024 | 2.3 | 90.4 | 2024 | 2.4 | 87.3 | 2025 | -0.7 | 87.7 | 2025 | -0.3 | 87.6 | 2025 | -0.4 | 87.6 | 2025 | -0.4 | 304631 MARION 230 304632 MARION 115 2
45 | OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304632 MARION 115 304654 DILLON T 115 1 | LN | 97 | 102.6 | 2010 | 115.5 | 2009 | 112.1 | 2011 |  |  | 109.3 | 2012 |  |  | 113 | 2010 | -2.5 | 126.4 | 2005 |  | 113.1 | 2010 | -2.4 | 124.3 | 2006 | 8.8 | 113.4 | 2010 | -2.1 | 110.6 | 2011 | -4.9 | 112.7 | 2010 | -2.8 | 112 | 2011 | -3.5 | 102.3 | 2015 | -13.2 | 304663 LATTA 230 304682 DILLMP T 230 1
46 | SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304663 LATTA 230 304682 DILLMP T 230 1 | LN | 507 | [15 empty] | 93.4 | 2019 |  |  |  |  | 91.9 | 2020 | 91.9 | [15 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
47 | SC ONLY | FLORENCE - KINGSTREE 230KV | 304671 SARDIS 230 304674 OLANTA 230 1 | LN | 478 | [15 empty] | 88.5 | 2021 | 88.5 | [21 empty] | MARION-MARION(SCPSA)230_1&2
48 | SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 478 |  |  |  |  | 87.5 | 2021 |  |  | 86.3 | 2022 | [5 empty] | 91.5 | 2020 | 91.5 |  |  |  | 86.5 | 2022 | 86.5 | [15 empty] | MARION-MARION(SCPSA)230_1&2
49 | SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304676 KINGST N 230 304677 KINGSTRE 230 1 | LN | 557 | [15 empty] | 86.6 | 2022 | 86.6 | [21 empty] | MARION-MARION(SCPSA)230_1&2
50 | SCEG ONLY | KINGSTREE - SUMTER 115KV | 304685 ALCOLU 115 304686 SUMTER 115 1 | LN | 119 | [21 empty] | 86.6 | 2022 | 86.6 | [15 empty] | 43008 6KNGSTRE 230 304677 KINGSTRE 230 1
51 | OP. PROC. - DUKE (DK1) | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 108 | 96.7 | 2014 | 85.7 | 2022 | [8 empty] | 86.5 | 2022 | 0.8 | 96.4 | 2018 | 10.7 |  |  |  | 100.8 | 2015 | 15.1 | 87.9 | 2021 | 2.2 | 86.8 | 2022 | 1.1 | 86.2 | 2022 | 0.5 | 86.3 | 2022 | 0.6 | 88.1 | 2021 | 2.4 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
52 | OP. PROC. - DUKE (DK1) | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 108 | 119 | 2004 | 108.1 | 2012 | 99.5 | 2017 | 97 | 2018 | 97.3 | 2018 | 96.5 | 2018 | 108.9 | 2012 | 0.8 | 118.7 | 2008 | 10.6 | 104.2 | 2014 | -3.9 | 123.1 | 2006 | 15 | 110.3 | 2011 | 2.2 | 109.2 | 2012 | 1.1 | 108.6 | 2012 | 0.5 | 108.7 | 2012 | 0.6 | 110.5 | 2011 | 2.4 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
53 | OP. PROC. - DUKE (DK1) | CAMDEN 230/115kV BANK | 304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 200 | 94.1 | 2018 | 85 | 2026 | [11 empty] | 91.3 | 2024 | 6.3 |  |  |  | 91.8 | 2020 | 6.8 | 86.8 | 2022 | 1.8 | 85.1 | 2022 | 0.1 | 89.7 | 2021 | 4.7 |  |  |  | 86.9 | 2025 | 1.9 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
54 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 108 | 126 | 2001 | 112.5 | 2011 | 99.5 | 2017 | 96.6 | 2018 |  |  | 95.8 | 2018 | 113 | 2010 | 0.5 | 124.4 | 2006 | 11.9 | 106.6 | 2013 | -5.9 | 128.5 | 2004 | 16 | 115.1 | 2009 | 2.6 | 113.5 | 2010 | 1 | 112.7 | 2010 | 0.2 | 112.8 | 2010 | 0.3 | 115.4 | 2009 | 2.9 | 304716 CAM TAP 115 304725 CAMDEN 115 1
55 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 95 | 109.2 | 2008 | 96.3 | 2018 | [8 empty] | 96.7 | 2018 | 0.4 | 109.7 | 2012 | 13.4 | 89.3 | 2021 | -7 | 114.2 | 2010 | 17.9 | 99.1 | 2017 | 2.8 | 97.3 | 2018 | 1 | 96.3 | 2018 | 0 | 96.5 | 2018 | 0.2 | 99.4 | 2017 | 3.1 | 304716 CAM TAP 115 304725 CAMDEN 115 1
56 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304732 ELGIN T 115 304734 WATRE 115 1 | LN | 95 |  |  | 85.4 | 2022 | [8 empty] | 85.7 | 2022 | 0.3 | 98.6 | 2017 | 13.2 |  |  |  | 103 | 2014 | 17.6 | 88.1 | 2021 | 2.7 | 86.3 | 2022 | 0.9 | 85.3 | 2022 | -0.1 | 85.5 | 2022 | 0.1 | 88.3 | 2021 | 2.9 | 304716 CAM TAP 115 304725 CAMDEN 115 1
Note on B43: OPEN 115kV LINE
Note on B48: OPEN LINE
Note on F3: PTI: Branch Rating
Note on AT3: PTI: Contingency Description

## PWG- PEC LOCAL ISSUES 2012&2016
| 2007-07-24 |  |  |  |  | Base TRM |  |  |  | Import - 2016 RSO
[6 empty] | 2012 |  | 2016 |  | Dk-1200MW
Item # | NOTE | LINE / ELEMENT | ** From bus ** ** To bus ** CKT | Type | Rating | % | Yr | % | Yr | % | Yr | Contingency | NOTES
1 | OUTSIDE HORIZON | CARY REGENCY PARK - DURHAM 230KV | 304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 539 |  |  |  |  | 95.6 | 2018 | METHOD-PRISONF230_&_METHOD-BLUERDG230 | COULD BE 2018
2 | PROJECT | WAKE 500/230 KV BANKS | 304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1000 | 94.7 | 2018 | 100 | 2020 | 107.9 | 2017 | 3Wnd: OPEN B$0832 WAKE#2 2 | COULD BE 2017 FOR 1200MW IMPORTS
3 | PROJECT IN 2013 | LAURINBURG 230/115kV BANK #1 & 2 (same) | 304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 200 | 93.7 | 2019 | [5 empty] | Could Delay till 2019
4 | SCEG ONLY | SUMTER - SCE&G CANADYS 230KV | 42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 273 |  |  |  |  | 95.2 | 2018 | 42002 6WATEREE 230 304700 SUMTER 230 1 | Limited to 154 Degrees on SCEG Side- 403MVA on PEC side
5 | LOCAL- PROJECT NEEDED | Currently FALLS - FRANKLINTON 115KV | 304111 E18-WK F 115 304185 FALLS 115 1 | LN | 170 | 95.7 | 2014 | 96 | 2018 | 97.9 | 2017 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115 | 180 Degree rating Gnd Clearance
6 | LOCAL- PROJECT NEEDED | CHESTNUT HILLS - MILBURNIE 115KV | 304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 158 | 101.9 | 2011 | 112.4 | 2011 | 113.6 | 2010 | 304145 NEUSE 115 304185 FALLS 115 1 | 170 Degree rating Gnd Clearance
7 | LOCAL- PROJECT NEEDED | MILBURNIE - MORDECAI 115KV | 304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 190 | 85.8 | 2018 | 94.1 | 2019 | 95 | 2018 | 304137 METHOD 115 304150 I-NCSU S 115 1 | Mv Sullivan Load
| LOCAL- PROJECT NEEDED | METHOD - RALEIGH 115KV | 304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 190 |  |  | 91.9 | 2020 | 92.5 | 2019 | 304163 MILBURNE 115 304168 YONKERS 115 1 | Mv Sullivan Load
8 | ?OP. PROC.? | CLINTON - VANDER 115KV | 304265 E15-STED 115 304401 VANDER 115 1 | LN | 163 | 85 | 2018 |  |  | 86.3 | 2022 | 304196 ERWIN 230 304197 DUNN 230.0 1 | Gnd Clearance + Sensitive to Generation
9 | REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 507 |  |  | 87.2 | 2022 | 91.9 | 2020 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
10 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304348 RKH 230 304638 WDSB T 230 1 | LN | 539 | 96.6 | 2014 | 104.3 | 2014 | 106.4 | 2013 | 304348 RKH 230 304361 WEST END 230 1
| OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304361 WEST END 230 1 | LN | 507 | 85.1 | 2018 | 91.7 | 2020 | 93.7 | 2019 | 304348 RKH 230 304361 WEST END 230 1
| OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 507 | 89.5 | 2017 | 96.5 | 2018 | 98.6 | 2017 | 304348 RKH 230 304361 WEST END 230 1
11 | 1200MW +BYNUM 500 Only | LILESVILLE-RKH BLK/WHT | 304350 PH SH 1B 230 304985 LILES SS 230 1 | LN | 398 |  |  |  |  | 89.9 | 2021 | 337 8NEWPORT 500 304377 RICHMOND 500 1 | Outside
12 | PROJECT NEEDED | FAYETTEVILLE - FAYETTEVILLE EAST 230KV | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 709 | 92.5 | 2015 | 85.5 | 2022 | 99.1 | 2017 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
13 | LOCAL- PROJECT NEEDED | JACKSONVLLE - JACKSONVLLE CITY 115KV WEST | 304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 220 | 96.2 | 2014 | 108.9 | 2012 | 108.4 | 2012 | JAX-TARAWA230_&_JAX-NORTHWDS115 | Investigate 230/115kV Sub Solution
| LOCAL- PROJECT NEEDED | JACKSONVLLE - JACKSONVLLE CITY 115KV WEST | 304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 221 | 88.9 | 2017 | 100.7 | 2015 | 100.2 | 2015 | JAX-TARAWA230_&_JAX-NORTHWDS115
| LOCAL- PROJECT NEEDED | JACKSONVILLE - JACKSONVILLE CITY 115KV EAST | 304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 221 | 95.5 | 2014 | 107.5 | 2013 | 107.6 | 2012 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
14 | LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 158 |  |  | 87.2 | 2022 | 88 | 2021 | 304544 HOLLY RG 115 304545 CASTLE H 115 1 | Investigate 230/115kV Sub Solution near Folkstone
| LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 179 | 90.1 | 2016 | 94.6 | 2019 | 95.7 | 2018 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
15 | SCPSA JOINT STUDY | MARION - WHITEVILLE 115KV | 304630 MULLINS 115 304632 MARION 115 1 | LN | 179 | 87.5 | 2017 | 97.6 | 2017 | 97 | 2018 | 304587 E1-CHADP 230 304631 MARION 230 1 | Reactors
16 | OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304632 MARION 115 304654 DILLON T 115 1 | LN | 97 | 102.6 | 2010 | 115.5 | 2009 | 112.1 | 2011 | 304663 LATTA 230 304682 DILLMP T 230 1 | Operating Procedure/Reactor
| LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 590 | 107.3 | 2009 | 117.7 | 2008 | 117.9 | 2008 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng) | JENKINS
| LOCAL OP PROCEDURE | SUTTON PLANT - DELCO 230KV | 304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 478 | 90.8 | 2016 | 108 | 2012 | 111.7 | 2011 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng) | JENKINS
| LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 590 | 86.9 | 2018 | 95.4 | 2018 | 95.3 | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng) | JENKINS
| LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 590 | 99.2 | 2013 | 109.1 | 2012 | 108.9 | 2012 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng) | JENKINS
| LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 590 | 91.6 | 2016 | 100.7 | 2015 | 100.5 | 2015 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng) | JENKINS
Note on B25: OPEN LINE
Note on F3: PTI: Branch Rating
Note on M3: PTI: Contingency Description

## PEC Reliability&RSO 2012 & 2016
| 2007-07-05 |  |  |  |  | Base TRM |  |  |  | Import - 2016 RSO | [19 empty] | Generation - 2016 RSO
[6 empty] | 2012 |  | 2016 |  | Dk-1200MW |  | Dk-1200MW+Imprt Prjcts+3DkPrjcts |  | Dk-1200MW+ Bynum500+ 3DkPrjcts |  | Dk-1200MW+ Erwin500+ 3DkPrjcts |  | PJM-200MW |  |  | SC- 400MW |  |  | Dk-600MW |  |  | SG-Calpine 600MW |  |  | Laurinburg 450MW |  |  | Cumbrlnd/Fay 450MW |  |  | Wilson 450MW |  |  | Selma 450MW |  |  | Wspn 600MW
Item # | NOTES | LINE / ELEMENT | ** From bus ** ** To bus ** CKT | Type | Rating | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | % | Yr | D | Contingency
1 | SCEG ONLY | SUMTER - SCE&G CANADYS 230KV | 42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 273 |  |  |  |  | 95.2 | 2018 | 93.9 | 2019 | 93.5 | 2019 | 94.3 | 2019 | [6 empty] | 85.9 | 2022 | 85.9 | 90.6 | 2020 | 90.6 | [15 empty] | 42002 6WATEREE 230 304700 SUMTER 230 1
2 | SCEG ONLY | SUMTER - SCE&G EASTOVER 115KV | 42003 3EASTOVE 115 304696 SHAW TAP 115 1 | LN | 118 |  |  |  |  | 88.9 | 2021 |  |  | 87.1 | 2022 | 87.9 | 2021 | [9 empty] | 91.5 | 2020 | 91.5 | [15 empty] | SUMT-SUMMRTN230_&_SUMT-WATEREE230
| 1200MW +BYNUM 500 Only- Can Uprate to 1077MVA | HARRIS-SILER CITY 230kV | 304009 HARRIS1N 230 304337 BYNUM T 230 1 | LN | 793 | [8 empty] | 96.8 | 2018 | [29 empty] | PARKWOOD-BYNUM 500 KV LINE
3 | LOCAL | BR #2 - DELCO 230KV WEST | 304020 BRUN 2 N 230 304604 E1-STHPT 230 1 | LN | 478 | 88.7 | 2017 | [37 empty] | 304020 BRUN 2 N 230 304615 BARCRK E 230 1
4 | LOCAL-Project 2017 | SUTTON-CASTLE HAYNE 115KV LINE #2 | 304035 SUT 1-2F 115 304545 CASTLE H 115 2 | LN | 131 | 85.4 | 2018 | [37 empty] | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
5 | LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 590 | 107.3 | 2009 | 117.7 | 2008 | 117.9 | 2008 | 117.5 | 2009 | 120 | 2008 | 118.2 | 2008 | 117.3 | 2009 | -0.4 | 120.8 | 2007 | 3.1 | 117.4 | 2009 | -0.3 | 118.1 | 2008 | 0.4 | 118 | 2008 | 0.3 | 119.6 | 2008 | 1.9 | 116.3 | 2009 | -1.4 | 116.6 | 2009 | -1.1 | 119.5 | 2008 | 1.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
6 | LOCAL OP PROCEDURE | SUTTON PLANT - DELCO 230KV | 304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 478 | 90.8 | 2016 | 108 | 2012 | 111.7 | 2011 | 110.2 | 2011 | 115.5 | 2009 | 107.7 | 2012 | 107.3 | 2013 | -0.7 | 113.3 | 2010 | 5.3 | 111.1 | 2011 | 3.1 | 112.7 | 2010 | 4.7 | 111.9 | 2011 | 3.9 | 112.4 | 2011 | 4.4 | 106 | 2013 | -2 | 105.7 | 2013 | -2.3 | 114.1 | 2010 | 6.1 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
7 | WSPN GEN ONLY | WEATHERSPOON 230/115kV | 304046 WSPN BUS 230 304047 WSP BUS 115 1 | TR | 200 | [36 empty] | 91.5 | 2023 | 91.5 | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1
8 | WSPN GEN ONLY | WSPN PLANT - FAYETTEVILLE 230KV | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1 | LN | 478 | [36 empty] | 85.9 | 2022 | 85.9 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
9 | SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 478 | [15 empty] | 89.2 | 2021 |  |  |  |  | 87.6 | 2021 | 87.6 | [15 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
10 | WSPN GEN ONLY | WSPN PLANT - RAEFORD 230KV SUB 115KV | 304047 WSP BUS 115 304432 PA-LMB#2 115 1 | LN | 133 | [36 empty] | 89.2 | 2021 | 89.2 | 304378 RICHMOND 230 304415 RAEFORD 230 1
| 1200MW ONLY | CAPE FEAR PLANT-ERWIN 115KV | 304052 CAPE F F 115 304220 LILINGTN 115 1 | LN | 86 |  |  |  |  | 89.7 | 2021 | 88.7 | 2021 | 95.8 | 2018 | [29 empty] | 304009 HARRIS1N 230 304204 DUNCAN 230 1
| 1200MW ONLY | DURHAM-FALLS 230KV | 304078 WD VALLY 230 304117 DURHAM 230 1 | LN | 541 | [39 empty] | ROX-FALLS230_&_FALLS23-CGROX230
11 | PROJECT IN 2014 | FRANKLINTON - HENDERSON 115KV | 304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 201 | 86.4 | 2018 | [37 empty] | 304111 E18-WK F 115 304185 FALLS 115 1
12 | OUTSIDE HORIZON | CARY REGENCY PARK - DURHAM 230KV | 304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 539 |  |  |  |  | 95.6 | 2018 | [6 empty] | 87.1 | 2022 | 87.1 | 87.2 | 2022 | 87.2 | 90.3 | 2020 | 90.3 | 88.8 | 2021 | 88.8 | 86.4 | 2022 | 86.4 | 85.6 | 2022 | 85.6 | 87.3 | 2022 | 87.3 |  |  |  | 85.6 | 2022 | 85.6 | METHOD-PRISONF230_&_METHOD-BLUERDG230
13 | LOCAL- PROJECT NEEDED | Currently FALLS - FRANKLINTON 115KV | 304111 E18-WK F 115 304185 FALLS 115 1 | LN | 170 | 95.7 | 2014 | 96 | 2018 | 97.9 | 2017 | 96.9 | 2018 | 97.4 | 2018 | 97.3 | 2018 | 96 | 2018 | 0 | 96.7 | 2018 | 0.7 | 97 | 2018 | 1 | 96.9 | 2018 | 0.9 | 96.9 | 2018 | 0.9 | 96.7 | 2018 | 0.7 | 92.4 | 2020 | -3.6 | 96.1 | 2018 | 0.1 | 96.7 | 2018 | 0.7 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
14 | LOCAL | METHOD - RALEIGH 115KV | 304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 190 |  |  | 91.9 | 2020 | 92.5 | 2019 | 86.3 | 2022 | 91.4 | 2020 | 91.3 | 2020 | 92 | 2020 | 0.1 | 92.2 | 2020 | 0.3 | 92.6 | 2019 | 0.7 | 92.7 | 2019 | 0.8 | 91.8 | 2020 | -0.1 | 92 | 2020 | 0.1 | 91.7 | 2020 | -0.2 | 91.7 | 2020 | -0.2 | 92.1 | 2020 | 0.2 | 304163 MILBURNE 115 304168 YONKERS 115 1
15 | LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304137 METHOD 115 304153 TRYON HL 115 1 | LN | 108 |  |  | 91.1 | 2020 | 91.8 | 2020 |  |  | 90.7 | 2020 | 90.6 | 2020 | 91.2 | 2020 | 0.1 | 91.4 | 2020 | 0.3 | 92 | 2020 | 0.9 | 91.9 | 2020 | 0.8 | 91 | 2020 | -0.1 | 91.2 | 2020 | 0.1 | 90.9 | 2020 | -0.2 | 90.9 | 2020 | -0.2 | 91.3 | 2020 | 0.2 | 304174 I-PERSTP 115 304181 GARNER E 115 1
16 | LOCAL | CHESTNUT HILLS - FALLS 115KV | 304145 NEUSE 115 304185 FALLS 115 1 | LN | 201 |  |  | 85.3 | 2022 | 86 | 2022 |  |  | 85.1 | 2022 |  |  | 85.4 | 2022 | 0.1 | 85.6 | 2022 | 0.3 | 86.1 | 2022 | 0.8 | 86 | 2022 | 0.7 | 85.2 | 2022 | -0.1 | 85.4 | 2022 | 0.1 | 85.2 | 2022 | -0.1 | 85.2 | 2022 | -0.1 | 85.5 | 2022 | 0.2 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
17 | LOCAL | METHOD - RALEIGH 115KV | 304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 159 |  |  | 86.7 | 2022 | 87.2 | 2022 |  |  | 86.3 | 2022 | 86.2 | 2022 | 86.8 | 2022 | 0.1 | 87 | 2022 | 0.3 | 87.4 | 2022 | 0.7 | 87.5 | 2021 | 0.8 | 86.6 | 2022 | -0.1 | 86.8 | 2022 | 0.1 | 86.6 | 2022 | -0.1 | 86.5 | 2022 | -0.2 | 86.9 | 2022 | 0.2 | 304163 MILBURNE 115 304168 YONKERS 115 1
18 | LOCAL- PROJECT NEEDED | CHESTNUT HILLS - MILBURNIE 115KV | 304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 158 | 101.9 | 2011 | 112.4 | 2011 | 113.6 | 2010 | 112.1 | 2011 | 112.3 | 2011 | 112.1 | 2011 | 112.5 | 2011 | 0.1 | 112.9 | 2010 | 0.5 | 113.6 | 2010 | 1.2 | 113.5 | 2010 | 1.1 | 112.4 | 2011 | 0 | 112.6 | 2010 | 0.2 | 112.1 | 2011 | -0.3 | 111.7 | 2011 | -0.7 | 112.7 | 2010 | 0.3 | 304145 NEUSE 115 304185 FALLS 115 1
19 | LOCAL- PROJECT NEEDED | MILBURNIE - MORDECAI 115KV | 304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 190 | 85.8 | 2018 | 94.1 | 2019 | 95 | 2018 | 93.9 | 2019 | 94 | 2019 | 93.9 | 2019 | 94.2 | 2019 | 0.1 | 94.5 | 2019 | 0.4 | 95 | 2018 | 0.9 | 94.9 | 2019 | 0.8 | 94.1 | 2019 | 0 | 94.2 | 2019 | 0.1 | 93.8 | 2019 | -0.3 | 93.8 | 2019 | -0.3 | 94.3 | 2019 | 0.2 | 304137 METHOD 115 304150 I-NCSU S 115 1
20 | LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 118 |  |  | 93.3 | 2019 | 93.6 | 2019 |  |  | 99.6 | 2017 |  |  | 93.9 | 2019 | 0.6 | 94.9 | 2019 | 1.6 | 95.3 | 2018 | 2 | 95.6 | 2018 | 2.3 | 96.2 | 2018 | 2.9 | 96.8 | 2018 | 3.5 | 97 | 2018 | 3.7 | 95.6 | 2018 | 2.3 | 96 | 2018 | 2.7 | 304156 ROL/SQ T 230 304190 WAKE 230 1
21 | LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 118 |  |  | 85.6 | 2022 |  |  | 85.6 | 2022 |  |  |  |  | 85.7 | 2022 | 0.1 | 85.2 | 2022 | -0.4 | 85.2 | 2022 | -0.4 | 85.4 | 2022 | -0.2 |  |  |  | 85.3 | 2022 | -0.3 | 86.8 | 2022 | 1.2 | 86.7 | 2022 | 1.1 | 85.2 | 2022 | -0.4 | METHOD-PRISONF230_&_METHOD-BLUERDG230
22 | SELMA GEN ONLY | SELMA 230/115kV Bank #1 & 2 (exact same) | 304177 SELMA 115 304192 SELMA 230 1 | TR | 200 | [33 empty] | 91.1 | 2024 | 91.1 |  |  |  | 304177 SELMA 115 304192 SELMA 230 2
23 | PROJECT IN 2013 | FALLS 230/115kV Bank #1 | 304182 FALLS 230 304185 FALLS 115 1 | TR | 300 | 103.1 | 2015 | [37 empty] | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
24 | PROJECT | WAKE 500/230 KV BANKS | 304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1000 | 94.7 | 2018 | 100 | 2020 | 107.9 | 2017 |  |  | 104 | 2018 | 87.3 | 2025 | 101.5 | 2019 | 1.5 | 103.4 | 2019 | 3.4 | 105.4 | 2018 |  | 105.3 | 2018 | 5.3 | 103.5 | 2019 | 3.5 | 104.4 | 2018 | 4.4 | 96.6 | 2021 | -3.4 | 94.9 | 2022 | -5.1 | 103 | 2019 | 3 | 3Wnd: OPEN B$0832 WAKE#2 2
25 | OP. PROC. | CLINTON - VANDER 115KV | 304265 E15-STED 115 304401 VANDER 115 1 | LN | 163 | 85 | 2018 |  |  | 86.3 | 2022 |  |  | 86.1 | 2022 | 85.6 | 2022 | [9 empty] | 90.6 | 2020 | 90.6 | 86.2 | 2022 | 86.2 | 87.5 | 2021 | 87.5 | [6 empty] | 86.7 | 2022 | 86.7 | 304196 ERWIN 230 304197 DUNN 230.0 1
26 | OUTSIDE HORIZON | ASHEBORO EAST - BISCOE 230KV SUB 115KV | 304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 138 |  |  | 87.6 | 2021 | 88.2 | 2021 | 87.7 | 2021 | 87.2 | 2022 | 87.6 | 2021 | 87.7 | 2021 | 0.1 | 88.1 | 2021 | 0.5 | 88.6 | 2021 | 1 | 88.5 | 2021 | 0.9 | 87.7 | 2021 | 0.1 | 87.7 | 2021 | 0.1 | 87.5 | 2021 | -0.1 | 87.5 | 2021 | -0.1 | 87.9 | 2021 | 0.3 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
| 1200MW +BYNUM 500 Only | CAPE FEAR-BISCOE 115kV | 304305 SPRING T 115 304428 BISCOE W 115 1 | LN | 198 | [6 empty] | 86.1 | 2022 | 88.1 | 2021 | 85.3 | 2022 | [27 empty] | 304009 HARRIS1N 230 304337 BYNUM T 230 1
| PROJECT IN PLACE | ASHEBORO-ASHEBORO EAST NORTH 115kV LINE | 304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 201 | [8 empty] | 93.4 | 2019 | 91.6 | 2020 | [27 empty] | 304312 ASHEB E 115 304331 ASHEB 115 1
27 | REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 507 |  |  | 87.2 | 2022 | 91.9 | 2020 | 90.8 | 2020 |  |  | 89.3 | 2021 |  |  |  | 89.2 | 2021 | 2 | 89.8 | 2021 | 2.6 | 90.5 | 2020 | 3.3 | 91.6 | 2020 | 4.4 | 86 | 2022 | -1.2 | [6 empty] | 88.7 | 2021 | 1.5 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
28 | REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 507 | [6 empty] | 88.3 | 2021 |  |  | 86.8 | 2022 |  |  |  | 86.7 | 2022 | 86.7 | 87.3 | 2022 | 87.3 | 88.1 | 2021 | 88.1 | 89.1 | 2021 | 89.1 | [9 empty] | 86.2 | 2022 | 86.2 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
| OUTSIDE HORIZON | FAYETTEVILLE-ROCKINGHAM 230kV | 304348 RKH 230 304355 HAMLET 230 1 | LN | 507 |  |  |  |  | 87.4 | 2022 | 88.5 | 2021 | 85.9 | 2022 | 87.5 | 2021 | [27 empty] | 304377 RICHMOND 500 304391 CUMBERLD 500 1
29 | LAURNBRG GEN ONLY | RICHMOND - ROCKINGHAM 230KV | 304348 RKH 230 304378 RICHMOND 230 1 | LN | 1014 | [24 empty] | 86.5 | 2022 | 86.5 | [12 empty] | 304348 RKH 230 304378 RICHMOND 230 2
30 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304348 RKH 230 304638 WDSB T 230 1 | LN | 539 | 96.6 | 2014 | 104.3 | 2014 | 106.4 | 2013 | 105 | 2014 | 100.4 | 2015 | 101.9 | 2015 | 102.7 | 2014 | -1.6 | 105.8 | 2013 | 1.5 | 105.6 | 2013 | 1.3 | 106.3 | 2013 | 2 | 106.8 | 2013 | 2.5 | 104.3 | 2014 | 0 | 101.9 | 2015 | -2.4 | 101.5 | 2015 | -2.8 | 105.4 | 2013 | 1.1 | 304348 RKH 230 304361 WEST END 230 1
| 1200MW +BYNUM 500 Only | LILESVILLE-RKH BLK/WHT | 304350 PH SH 1B 230 304985 LILES SS 230 1 | LN | 398 |  |  |  |  | 89.9 | 2021 |  |  | 85.6 | 2022 | 91.6 | 2020 | [27 empty] | 337 8NEWPORT 500 304377 RICHMOND 500 1
31 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304361 WEST END 230 1 | LN | 507 | 85.1 | 2018 | 91.7 | 2020 | 93.7 | 2019 | 92.5 | 2019 | 87.7 | 2021 | 89.2 | 2021 | 90.1 | 2020 | -1.6 | 93.2 | 2019 | 1.5 | 93.1 | 2019 | 1.4 | 93.8 | 2019 | 2.1 | 94.4 | 2019 | 2.7 | 91.8 | 2020 | 0.1 | 89.3 | 2021 | -2.4 | 88.8 | 2021 | -2.9 | 92.9 | 2019 | 1.2 | 304348 RKH 230 304361 WEST END 230 1
32 | OP. PROC. | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 507 | 89.5 | 2017 | 96.5 | 2018 | 98.6 | 2017 | 97.3 | 2018 | 92.5 | 2019 | 94 | 2019 | 94.9 | 2019 | -1.6 | 98.1 | 2017 | 1.6 | 97.9 | 2017 | 1.4 | 98.6 | 2017 | 2.1 | 99.2 | 2017 | 2.7 | 96.6 | 2018 | 0.1 | 94.1 | 2019 | -2.4 | 93.6 | 2019 | -2.9 | 97.7 | 2017 | 1.2 | 304348 RKH 230 304361 WEST END 230 1
33 | CUMB/WSPN GEN ONLY | FAYETTEVILLE - FT. BRG WODRUFF ST. 230KV | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1 | LN | 793 | [27 empty] | 87.9 | 2021 | 87.9 | [6 empty] | 86.6 | 2022 | 86.6 | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1
34 | PROJECT NEEDED | FAYETTEVILLE - FAYETTEVILLE EAST 230KV | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 709 | 92.5 | 2015 | 85.5 | 2022 | 99.1 | 2017 | 95.6 | 2018 | 92.1 | 2020 | [5 empty] | 89.1 | 2021 | 3.6 | 88.4 | 2021 | 2.9 | 89.6 | 2021 | 4.1 | 93.8 | 2019 | 8.3 | 97.7 | 2017 | 12.2 | 87.6 | 2021 | 2.1 | 85.4 | 2022 | -0.1 | 96 | 2018 | 10.5 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
35 | OUTSIDE HORIZON | CUMBERLAND 500/230kV BANK | 304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 1000 |  |  |  |  | 91.2 | 2024 | 91.1 | 2024 | 89.4 | 2024 | 90.1 | 2024 | [6 empty] | 86.4 | 2026 | 86.4 | 85.1 | 2026 | 85.1 | [15 empty] | 304183 WAKE 500 304391 CUMBERLD 500 1
36 | CUMB/WSPN GEN ONLY | FAYETTEVILLE - VANDER 115KV SOUTH | 304392 FAY 115 304401 VANDER 115 1 | LN | 163 | [27 empty] | 85.7 | 2022 | 85.7 | [6 empty] | 85 | 2022 | 85 | 304392 FAY 115 304402 E15-VAND 115 1
37 | WSPN GEN ONLY | WSPN PL. - FAY'VILLE DUP. SW. ST. 115KV | 304406 ST PAULS 115 304412 F DUP SW 115 1 | LN | 119 | [36 empty] | 87 | 2022 | 87 | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1
38 | LAURNBRG GEN ONLY | RAEFORD 230KV SUB - WAGRAM 115KV | 304411 RAEFORD 115 304416 MAXAPT T 115 1 | LN | 190 | [24 empty] | 87.2 | 2022 | 87.2 | [12 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
39 | PROJECT NEEDED | RAEFORD 230KV SUB - WAGRAM 115KV | 304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 190 |  |  |  |  | 86.5 | 2022 | 86.4 | 2022 | [7 empty] | 86.9 | 2022 | 86.9 | 85.4 | 2022 | 85.4 | 87.3 | 2022 | 87.3 | 100.3 | 2015 | 100.3 | [9 empty] | 85.3 | 2022 | 85.3 | 304378 RICHMOND 230 304415 RAEFORD 230 1
40 | LAURNBRG GEN ONLY | LAURINBURG - WAGRAM 115KV | 304419 WAGRAMSW 115 304421 LAURINBG 115 1 | LN | 201 | [24 empty] | 95.8 | 2018 | 95.8 | [12 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
41 | PROJECT IN 2013 | LAURINBURG 230/115kV BANK #1 & 2 (same) | 304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 200 | 93.7 | 2019 | [37 empty] | 304421 LAURINBG 115 304424 LAURINBG 230 2
42 | OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 97 | [15 empty] | 87.6 | 2021 | 87.6 |  |  |  | 85.4 | 2022 | 85.4 | [15 empty] | 304663 LATTA 230 304682 DILLMP T 230 1
43 | LOCAL- PROJECT NEEDED | JACKSONVLLE - JACKSONVLLE CITY 115KV WEST | 304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 220 | 96.2 | 2014 | 108.9 | 2012 | 108.4 | 2012 | 108.8 | 2012 | 108.7 | 2012 | 108.9 | 2012 | 108.9 | 2012 | 0 | 108.3 | 2012 | -0.6 | 108.5 | 2012 | -0.4 | 108.5 | 2012 | -0.4 | 108.1 | 2012 | -0.8 | 107.9 | 2012 | -1 | 108.9 | 2012 | 0 | 108.9 | 2012 | 0 | 107.6 | 2012 | -1.3 | JAX-TARAWA230_&_JAX-NORTHWDS115
44 | LOCAL- PROJECT NEEDED | JACKSONVLLE - JACKSONVLLE CITY 115KV WEST | 304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 221 | 88.9 | 2017 | 100.7 | 2015 | 100.2 | 2015 | 100.6 | 2015 | 100.4 | 2015 | 100.7 | 2015 | 100.7 | 2015 | 0 | 100.1 | 2015 | -0.6 | 100.3 | 2015 | -0.4 | 100.2 | 2015 | -0.5 | 99.9 | 2017 | -0.8 | 99.7 | 2017 | -1 | 100.7 | 2015 | 0 | 100.7 | 2015 | 0 | 99.4 | 2017 | -1.3 | JAX-TARAWA230_&_JAX-NORTHWDS115
45 | LOCAL- PROJECT NEEDED | HAVELOCK - JACKSONVILLE 230KV | 304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 478 | 86.2 | 2018 | 90.3 | 2020 | 91.1 | 2020 | 90.5 | 2020 | 90.6 | 2020 | 90.4 | 2020 | 90.1 | 2020 | -0.2 | 91.2 | 2020 | 0.9 | 91.3 | 2020 | 1 | 91.7 | 2020 | 1.4 | 91.2 | 2020 | 0.9 | 91.2 | 2020 | 0.9 | 89.2 | 2021 | -1.1 | 89.9 | 2021 | -0.4 | 91.6 | 2020 | 1.3 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
46 | LOCAL- PROJECT NEEDED | JACKSONVILLE - JACKSONVILLE CITY 115KV EAST | 304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 221 | 95.5 | 2014 | 107.5 | 2013 | 107.6 | 2012 | 107.3 | 2013 | 107.1 | 2013 | 102.6 | 2014 | 107.5 | 2013 | 0 | 106.9 | 2013 | -0.6 | 107.1 | 2013 | -0.4 | 106.8 | 2013 | -0.7 | 106.5 | 2013 | -1 | 106.4 | 2013 | -1.1 | 103.1 | 2014 | -4.4 | 107.5 | 2013 | 0 | 106 | 2013 | -1.5 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
47 | LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 158 |  |  | 87.2 | 2022 | 88 | 2021 | 87.3 | 2022 | 87.4 | 2022 | 87.2 | 2022 | 87.1 | 2022 | -0.1 | 87.7 | 2021 | 0.5 | 88 | 2021 | 0.8 | 88.2 | 2021 | 1 | 87.5 | 2021 | 0.3 | 87.5 | 2021 | 0.3 | 86.7 | 2022 | -0.5 | 87 | 2022 | -0.2 | 87.7 | 2021 | 0.5 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
48 | LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 179 | 90.1 | 2016 | 94.6 | 2019 | 95.7 | 2018 | 95.7 | 2018 | 94.9 | 2019 | 94.8 | 2019 | 94.1 | 2019 | -0.5 |  |  |  | 95.5 | 2018 | 0.9 | 96.5 | 2018 | 1.9 | 96.3 | 2018 | 1.7 | 96.4 | 2018 | 1.8 | 92.5 | 2019 | -2.1 | 93.2 | 2019 | -1.4 | 97.6 | 2017 | 3 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
49 | LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 179 |  |  | 88.4 | 2021 |  |  | 89.4 | 2021 | 88.8 | 2021 | 88.5 | 2021 | 87.8 | 2021 | -0.6 | 90.3 | 2020 | 1.9 | 89.4 | 2021 | 1 | 90.3 | 2020 | 1.9 | 90.1 | 2020 | 1.7 | 90.2 | 2020 | 1.8 | 86.3 | 2022 | -2.1 | 87 | 2022 | -1.4 | 91.4 | 2020 | 3 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
50 | LOCAL- PROJECT NEEDED | CASTLE HAYNE - JACKSONVILLE 230KV | 304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 478 | 85.4 | 2018 | 85.9 | 2022 |  |  | 86.9 | 2022 | 87.2 | 2022 | 85.8 | 2022 | 85.3 | 2022 | -0.6 | 89 | 2021 | 3.1 | 88.7 | 2021 | 2.8 | 89.8 | 2021 | 3.9 | 89 | 2021 | 3.1 | 89.1 | 2021 | 3.2 | [6 empty] | 90.4 | 2020 | 4.5 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
51 | LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 590 | 86.9 | 2018 | 95.4 | 2018 | 95.3 | 2018 | 96 | 2018 | 92.3 | 2020 | 95.8 | 2018 | 95 | 2018 | -0.4 | 98.5 | 2017 | 3.1 | 95.3 | 2018 | -0.1 | 96 | 2018 | 0.6 | 96.6 | 2018 | 1.2 | 97.1 | 2018 | 1.7 | 94.1 | 2019 | -1.3 | 94.4 | 2019 | -1 | 97.2 | 2018 | 1.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
52 | LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 590 | 99.2 | 2013 | 109.1 | 2012 | 108.9 | 2012 | 109.1 | 2012 | 111.3 | 2011 | 109.5 | 2012 | 108.7 | 2012 | -0.4 | 112.1 | 2011 | 3 | 108.9 | 2012 | -0.2 | 109.6 | 2012 | 0.5 | 109.7 | 2012 | 0.6 | 110.9 | 2011 | 1.8 | 107.7 | 2012 | -1.4 | 108.1 | 2012 | -1 | 110.9 | 2011 | 1.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
53 | LOCAL OP PROCEDURE | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 590 | 91.6 | 2016 | 100.7 | 2015 | 100.5 | 2015 | 101.1 | 2015 |  |  | 101.1 | 2015 | 100.3 | 2015 | -0.4 | 103.8 | 2014 | 3.1 | 100.6 | 2015 | -0.1 | 101.3 | 2015 | 0.6 | 101.7 | 2015 | 1 | 102.4 | 2015 | 1.7 | 99.4 | 2017 | -1.3 | 99.7 | 2017 | -1 | 102.5 | 2015 | 1.8 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
54 | WSPN GEN ONLY | CASTLE HAYNE-JACSONVILLE 230KV | 304556 TOPSL T 230 304564 SCOTT T 230 1 | LN | 478 | [36 empty] | 85.2 | 2022 | 85.2 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
55 | SC-ONLY | MARION - WHITEVILLE 115KV | 304629 NICHOLS 115 304630 MULLINS 115 1 | LN | 179 | [15 empty] | 88.1 | 2021 | 88.1 | [21 empty] | 304587 E1-CHADP 230 304631 MARION 230 1
56 | SCPSA JOINT STUDY | MARION - WHITEVILLE 115KV | 304630 MULLINS 115 304632 MARION 115 1 | LN | 179 | 87.5 | 2017 | 97.6 | 2017 | 97 | 2018 |  |  | 95.6 | 2018 |  |  | 96.1 | 2018 | -1.5 | 104.6 | 2014 | 7 | 97.5 |  | -0.1 | 103.6 | 2014 | 6 | 100.9 | 2015 | 3.3 | 94.2 | 2019 | -3.4 | 95.7 | 2018 | -1.9 | 95.4 | 2018 | -2.2 | 99.1 | 2017 | 1.5 | 304587 E1-CHADP 230 304631 MARION 230 1
57 | OUTSIDE HORIZON | MARION 230/115 BANK #1 & 2 (same) | 304631 MARION 230 304632 MARION 115 1 | TR | 200 |  |  | 88 | 2025 | 89.2 | 2021 |  |  | 88.7 | 2025 | 88.5 | 2025 | 87.8 | 2025 | -0.2 | 91 | 2024 | 3 | 88.5 | 2025 | 0.5 | 90.3 | 2024 | 2.3 | 90.4 | 2024 | 2.4 | 87.3 | 2025 | -0.7 | 87.7 | 2025 | -0.3 | 87.6 | 2025 | -0.4 | 87.6 | 2025 | -0.4 | 304631 MARION 230 304632 MARION 115 2
58 | OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304632 MARION 115 304654 DILLON T 115 1 | LN | 97 | 102.6 | 2010 | 115.5 | 2009 | 112.1 | 2011 |  |  | 109.3 | 2012 |  |  | 113 | 2010 | -2.5 | 126.4 | 2005 |  | 113.1 | 2010 | -2.4 | 124.3 | 2006 | 8.8 | 113.4 | 2010 | -2.1 | 110.6 | 2011 | -4.9 | 112.7 | 2010 | -2.8 | 112 | 2011 | -3.5 | 102.3 | 2015 | -13.2 | 304663 LATTA 230 304682 DILLMP T 230 1
59 | SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304663 LATTA 230 304682 DILLMP T 230 1 | LN | 507 | [15 empty] | 93.4 | 2019 |  |  |  |  | 91.9 | 2020 | 91.9 | [15 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
60 | SC ONLY | FLORENCE - KINGSTREE 230KV | 304671 SARDIS 230 304674 OLANTA 230 1 | LN | 478 | [15 empty] | 88.5 | 2021 | 88.5 | [21 empty] | MARION-MARION(SCPSA)230_1&2
61 | SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 478 |  |  |  |  | 87.5 | 2021 |  |  | 86.3 | 2022 | [5 empty] | 91.5 | 2020 | 91.5 |  |  |  | 86.5 | 2022 | 86.5 | [15 empty] | MARION-MARION(SCPSA)230_1&2
62 | SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304676 KINGST N 230 304677 KINGSTRE 230 1 | LN | 557 | [15 empty] | 86.6 | 2022 | 86.6 | [21 empty] | MARION-MARION(SCPSA)230_1&2
63 | SCEG ONLY | KINGSTREE - SUMTER 115KV | 304685 ALCOLU 115 304686 SUMTER 115 1 | LN | 119 | [21 empty] | 86.6 | 2022 | 86.6 | [15 empty] | 43008 6KNGSTRE 230 304677 KINGSTRE 230 1
64 | OP. PROC. - DUKE (DK1) | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 108 | 96.7 | 2014 | 85.7 | 2022 | [8 empty] | 86.5 | 2022 | 0.8 | 96.4 | 2018 | 10.7 |  |  |  | 100.8 | 2015 | 15.1 | 87.9 | 2021 | 2.2 | 86.8 | 2022 | 1.1 | 86.2 | 2022 | 0.5 | 86.3 | 2022 | 0.6 | 88.1 | 2021 | 2.4 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
65 | OP. PROC. - DUKE (DK1) | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 108 | 119 | 2004 | 108.1 | 2012 | 99.5 | 2017 | 97 | 2018 | 97.3 | 2018 | 96.5 | 2018 | 108.9 | 2012 | 0.8 | 118.7 | 2008 | 10.6 | 104.2 | 2014 | -3.9 | 123.1 | 2006 | 15 | 110.3 | 2011 | 2.2 | 109.2 | 2012 | 1.1 | 108.6 | 2012 | 0.5 | 108.7 | 2012 | 0.6 | 110.5 | 2011 | 2.4 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
66 | OP. PROC. - DUKE (DK1) | CAMDEN 230/115kV BANK | 304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 200 | 94.1 | 2018 | 85 | 2026 | [11 empty] | 91.3 | 2024 | 6.3 |  |  |  | 91.8 | 2020 | 6.8 | 86.8 | 2022 | 1.8 | 85.1 | 2022 | 0.1 | 89.7 | 2021 | 4.7 |  |  |  | 86.9 | 2025 | 1.9 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
67 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 108 | 126 | 2001 | 112.5 | 2011 | 99.5 | 2017 | 96.6 | 2018 |  |  | 95.8 | 2018 | 113 | 2010 | 0.5 | 124.4 | 2006 | 11.9 | 106.6 | 2013 | -5.9 | 128.5 | 2004 | 16 | 115.1 | 2009 | 2.6 | 113.5 | 2010 | 1 | 112.7 | 2010 | 0.2 | 112.8 | 2010 | 0.3 | 115.4 | 2009 | 2.9 | 304716 CAM TAP 115 304725 CAMDEN 115 1
68 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 95 | 109.2 | 2008 | 96.3 | 2018 | [8 empty] | 96.7 | 2018 | 0.4 | 109.7 | 2012 | 13.4 | 89.3 | 2021 | -7 | 114.2 | 2010 | 17.9 | 99.1 | 2017 | 2.8 | 97.3 | 2018 | 1 | 96.3 | 2018 | 0 | 96.5 | 2018 | 0.2 | 99.4 | 2017 | 3.1 | 304716 CAM TAP 115 304725 CAMDEN 115 1
69 | OP. PROC. - DUKE (DK1) | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304732 ELGIN T 115 304734 WATRE 115 1 | LN | 95 |  |  | 85.4 | 2022 | [8 empty] | 85.7 | 2022 | 0.3 | 98.6 | 2017 | 13.2 |  |  |  | 103 | 2014 | 17.6 | 88.1 | 2021 | 2.7 | 86.3 | 2022 | 0.9 | 85.3 | 2022 | -0.1 | 85.5 | 2022 | 0.1 | 88.3 | 2021 | 2.9 | 304716 CAM TAP 115 304725 CAMDEN 115 1
Note on B52: OPEN 115kV LINE
Note on B68: OPEN LINE
Note on F3: PTI: Branch Rating
Note on AT3: PTI: Contingency Description

## Original 2012 & 2016
[5 empty] | Base TRM |  |  |  | Import - 2016 RSO | [7 empty] | Generation - 2016 RSO
[5 empty] | 2012 |  | 2016 |  | PJM-200MW |  | SC- 400MW |  | Dk-600MW |  | SCEG -Calpine 600MW |  | Laurinburg-450MW |  | Cumbrlnd/Fayttvl-450MW |  | Wilson-450MW |  | Selma-450MW |  | Wspn-600MW
NOTES | LINE / ELEMENT | ** From bus ** ** To bus ** CKT | Type | Rating | Loading | Yr | Loading | Yr | Loading | Yr | Loading | Yr | Loading | Yr | Loading | Yr Needed | Loading | Yr | Loading | Yr | Loading | Yr | Loading | Yr | Loading | Yr | Contingency
PROJECT IN 2015 | ASHEBORO - ASHEBORO EAST 115KV NORTH | 304319 ASHEB N 115 304331 ASHEB 115 1 | LN | 201 |  |  | 89.8 | 2021 | 90.9 | 2020 | 90.7 | 2020 | 91.5 | 2020 | 90.9 | 2020 | 90 | 2020 | 89.2 | 2021 | 90.9 | 2020 | 90.8 | 2020 | 90.3 | 2020 | 304312 ASHEB E 115 304331 ASHEB 115 1
PROJECT IN 2013 | ASHEBORO - ASHEBORO EAST 115KV SOUTH | 304312 ASHEB E 115 304331 ASHEB 115 1 | LN | 201 | 89.8 | 2017 | [20 empty] | 304319 ASHEB N 115 304331 ASHEB 115 1
PROJECT NEEDED | ASHEBORO EAST - BISCOE 230KV SUB 115KV | 304290 I-OLVRRB 115 304312 ASHEB E 115 1 | LN | 138 |  |  | 87.6 | 2021 | 87.7 | 2021 | 88.1 | 2021 | 88.6 | 2021 | 88.5 | 2021 | 87.7 | 2021 | 87.7 | 2021 | 87.5 | 2021 | 87.5 | 2021 | 87.9 | 2021 | 304294 BISCOSUB 115 304428 BISCOE W 115 1
LOCAL | BARNARD CREEK 230/115kV BANK #1 | 304615 BARCRK E 230 304616 BARNARD 115 1 | TR | 150 | 85.4 | 2018 | 93 | 2019 | 93 | 2019 |  |  | 93 | 2019 | 93 | 2019 | 93 | 2019 | 93 | 2019 | 93 | 2019 | 93 | 2019 | 93 | 2019 | ** Base Case **
LOCAL | BR #2 - DELCO 230KV WEST | 304020 BRUN 2 N 230 304604 E1-STHPT 230 1 | LN | 478 | 88.7 | 2017 | [20 empty] | 304020 BRUN 2 N 230 304615 BARCRK E 230 1
OP. PROC. - DUKE'S DISPATCH | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304724 CAMCTY01 115 1 | LN | 108 | 96.7 | 2014 | 85.7 | 2022 | 86.5 | 2022 | 96.4 | 2018 |  |  | 100.8 | 2015 | 87.9 | 2021 | 86.8 | 2022 | 86.2 | 2022 | 86.3 | 2022 | 88.1 | 2021 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
OP. PROC. - DUKE'S DISPATCH | CAMDEN - CAMDEN JUNCTION 115KV | 304716 CAM TAP 115 304725 CAMDEN 115 1 | LN | 108 | 119 | 2004 | 108.1 | 2012 | 108.9 | 2012 | 118.7 | 2008 | 104.2 | 2014 | 123.1 | 2006 | 110.3 | 2011 | 109.2 | 2012 | 108.6 | 2012 | 108.7 | 2012 | 110.5 | 2011 | 304725 CAMDEN 115 304731 I-DUP CA 115 1
OP. PROC. | CAMDEN 230/115kV BANK | 304725 CAMDEN 115 304730 CAMDEN 230 1 | TR | 200 | 94.1 | 2018 | 85 | 2026 |  |  | 91.3 | 2024 |  |  | 91.8 | 2020 | 86.8 | 2022 | 85.1 | 2022 | 89.7 | 2021 |  |  | 86.9 | 2025 | 304044 ROB 1 F 115 304721 BETHNE T 115 1
OP. PROC. - DUKE'S DISPATCH | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304725 CAMDEN 115 304731 I-DUP CA 115 1 | LN | 108 | 126 | 2001 | 112.5 | 2011 | 113 | 2010 | 124.4 | 2006 | 106.6 | 2013 | 128.5 | 2004 | 115.1 | 2009 | 113.5 | 2010 | 112.7 | 2010 | 112.8 | 2010 | 115.4 | 2009 | 304716 CAM TAP 115 304725 CAMDEN 115 1
OP. PROC. - DUKE'S DISPATCH | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304731 I-DUP CA 115 304732 ELGIN T 115 1 | LN | 95 | 109.2 | 2008 | 96.3 | 2018 | 96.7 | 2018 | 109.7 | 2012 | 89.3 | 2021 | 114.2 | 2010 | 99.1 | 2017 | 97.3 | 2018 | 96.3 | 2018 | 96.5 | 2018 | 99.4 | 2017 | 304716 CAM TAP 115 304725 CAMDEN 115 1
OP. PROC. - DUKE'S DISPATCH | CAMDEN DUPONT - DPC WATEREE PLANT 115KV | 304732 ELGIN T 115 304734 WATRE 115 1 | LN | 95 |  |  | 85.4 | 2022 | 85.7 | 2022 | 98.6 | 2017 |  |  | 103 | 2014 | 88.1 | 2021 | 86.3 | 2022 | 85.3 | 2022 | 85.5 | 2022 | 88.3 | 2021 | 304716 CAM TAP 115 304725 CAMDEN 115 1
REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304361 WEST END 230 1 | LN | 507 |  |  | 87.2 | 2022 |  |  | 89.2 | 2021 | 89.8 | 2021 | 90.5 | 2020 | 91.6 | 2020 | 86 | 2022 |  |  |  |  | 88.7 | 2021 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
REACTOR/PROJECT | CAPE FEAR PLANT - WEST END 230KV | 304314 E3-CTRCH 230 304373 S GARD T 230 1 | LN | 507 | [6 empty] | 86.7 | 2022 | 87.3 | 2022 | 88.1 | 2021 | 89.1 | 2021 | [6 empty] | 86.2 | 2022 | 304377 RICHMOND 500 304391 CUMBERLD 500 1
PROJECT IN 2014 | CARY REGENCY PARK - DURHAM 230KV | 304091 BRIERCK 230 304117 DURHAM 230 1 | LN | 539 |  |  |  |  | 87.1 | 2022 | 87.2 | 2022 | 90.3 | 2020 | 88.8 | 2021 | 86.4 | 2022 | 85.6 | 2022 | 87.3 | 2022 |  |  | 85.6 | 2022 | METHOD-PRISONF230_&_METHOD-BLUERDG230
PROJECT NEEDED | CASTLE HAYNE - JACKSONVILLE 230KV | 304550 CSTL HYN 230 304564 SCOTT T 230 1 | LN | 478 | 85.4 | 2018 | 85.9 | 2022 | 85.3 | 2022 | 89 | 2021 | 88.7 | 2021 | 89.8 | 2021 | 89 | 2021 | 89.1 | 2021 |  |  |  |  | 90.4 | 2020 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304536 JAX CITY 115 304542 E9-SOW 115 1 | LN | 158 |  |  | 87.2 | 2022 | 87.1 | 2022 | 87.7 | 2021 | 88 | 2021 | 88.2 | 2021 | 87.5 | 2021 | 87.5 | 2021 | 86.7 | 2022 | 87 | 2022 | 87.7 | 2021 | 304544 HOLLY RG 115 304545 CASTLE H 115 1
LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304544 HOLLY RG 115 304545 CASTLE H 115 1 | LN | 179 | 90.1 | 2016 | 94.6 | 2019 | 94.1 | 2019 |  |  | 95.5 | 2018 | 96.5 | 2018 | 96.3 | 2018 | 96.4 | 2018 | 92.5 | 2019 | 93.2 | 2019 | 97.6 | 2017 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
LOCAL- PROJECT NEEDED | CASTLE HAYNE 230KV - JCKSNVLLE CITY 115KV | 304544 HOLLY RG 115 304546 E9-TOPSL 115 1 | LN | 179 |  |  | 88.4 | 2021 | 87.8 | 2021 | 90.3 | 2020 | 89.4 | 2021 | 90.3 | 2020 | 90.1 | 2020 | 90.2 | 2020 | 86.3 | 2022 | 87 | 2022 | 91.4 | 2020 | 304550 CSTL HYN 230 304564 SCOTT T 230 1
WSPN GEN ONLY | CASTLE HAYNE-JACSONVILLE 230KV | 304556 TOPSL T 230 304564 SCOTT T 230 1 | LN | 478 | [20 empty] | 85.2 | 2022 | 304022 BRUN 1 N 230 304354 I-ROCKY 230 1
LOCAL | CHESTNUT HILLS - FALLS 115KV | 304145 NEUSE 115 304185 FALLS 115 1 | LN | 201 |  |  | 85.3 | 2022 | 85.4 | 2022 | 85.6 | 2022 | 86.1 | 2022 | 86 | 2022 | 85.2 | 2022 | 85.4 | 2022 | 85.2 | 2022 | 85.2 | 2022 | 85.5 | 2022 | 304155 CHSTNT H 115 304163 MILBURNE 115 1
LOCAL- PROJECT NEEDED | CHESTNUT HILLS - MILBURNIE 115KV | 304155 CHSTNT H 115 304163 MILBURNE 115 1 | LN | 158 | 101.9 | 2011 | 112.4 | 2011 | 112.5 | 2011 | 112.9 | 2010 | 113.6 | 2010 | 113.5 | 2010 | 112.4 | 2011 | 112.6 | 2010 | 112.1 | 2011 | 111.7 | 2011 | 112.7 | 2010 | 304145 NEUSE 115 304185 FALLS 115 1
? OP. PROC. ? | CLINTON - VANDER 115KV | 304265 E15-STED 115 304401 VANDER 115 1 | LN | 163 | 85 | 2018 | [8 empty] | 90.6 | 2020 | 86.2 | 2022 | 87.5 | 2021 |  |  |  |  | 86.7 | 2022 | 304020 BRUN 2 N 230 304863 BRUN #2 24.0 1
OUTSIDE HORIZON | CUMBERLAND 500/230kV BANK | 304391 CUMBERLD 500 B$0303 CUMBERLD 1.00 1 | TR | 1000 | [8 empty] | 86.4 | 2026 | 85.1 | 2026 | [10 empty] | 304183 WAKE 500 304391 CUMBERLD 500 1
????? | FALLS - HENDERSON 115KV | 304111 E18-WK F 115 304185 FALLS 115 1 | LN | 170 | 95.7 | 2014 | 96 | 2018 | 96 | 2018 | 96.7 | 2018 | 97 | 2018 | 96.9 | 2018 | 96.9 | 2018 | 96.7 | 2018 | 92.4 | 2020 | 96.1 | 2018 | 96.7 | 2018 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
PROJECT IN 2013 | FALLS 230/115kV Bank #1 | 304182 FALLS 230 304185 FALLS 115 1 | TR | 300 | 103.1 | 2015 | [20 empty] | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115
PROJECT IN 2014- FULL RATING | FAYETTEVILLE - FAYETTEVILLE EAST 230KV | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1 | LN | 709 | 92.5 | 2015 | 85.5 | 2022 |  |  | 89.1 | 2021 | 88.4 | 2021 | 89.6 | 2021 | 93.8 | 2019 | 97.7 | 2017 | 87.6 | 2021 | 85.4 | 2022 | 96 | 2018 | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1
CUMB/WSPN GEN ONLY | FAYETTEVILLE - FT. BRG WODRUFF ST. 230KV | 304387 P1-FAY 0 230 304388 P3-FAYRR 230 1 | LN | 793 | [14 empty] | 87.9 | 2021 |  |  |  |  | 86.6 | 2022 | 304387 P1-FAY 0 230 304389 P2-FAY E 230 1
CUMB/WSPN GEN ONLY | FAYETTEVILLE - VANDER 115KV SOUTH | 304392 FAY 115 304401 VANDER 115 1 | LN | 163 | [14 empty] | 85.7 | 2022 |  |  |  |  | 85 | 2022 | 304392 FAY 115 304402 E15-VAND 115 1
SC ONLY | FLORENCE - KINGSTREE 230KV | 304671 SARDIS 230 304674 OLANTA 230 1 | LN | 478 | [6 empty] | 88.5 | 2021 | [14 empty] | MARION-MARION(SCPSA)230_1&2
SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304674 OLANTA 230 304675 LAKE CTY 230 1 | LN | 478 | [6 empty] | 91.5 | 2020 |  |  | 86.5 | 2022 | [10 empty] | MARION-MARION(SCPSA)230_1&2
SC&SCEG ONLY | FLORENCE - KINGSTREE 230KV | 304676 KINGST N 230 304677 KINGSTRE 230 1 | LN | 557 | [6 empty] | 86.6 | 2022 | [14 empty] | MARION-MARION(SCPSA)230_1&2
PROJECT IN 2014 | FRANKLINTON - HENDERSON 115KV | 304089 HENDERSN 115 304105 FRANKLIN 115 1 | LN | 201 | 86.4 | 2018 | [20 empty] | 304111 E18-WK F 115 304185 FALLS 115 1
PROJECT NEEDED | HAVELOCK - JACKSONVILLE 230KV | 304519 M-TARAWA 230 304524 JACKSONV 230 1 | LN | 478 | 86.2 | 2018 | 90.3 | 2020 | 90.1 | 2020 | 91.2 | 2020 | 91.3 | 2020 | 91.7 | 2020 | 91.2 | 2020 | 91.2 | 2020 | 89.2 | 2021 | 89.9 | 2021 | 91.6 | 2020 | 304465 NEW BERN 230 304484 HAVELOCK 230 1
LOCAL- PROJECT NEEDED | JACKSONVILLE - JACKSONVILLE CITY 115KV EAST | 304530 JACKSNVL 115 304535 NORTHWDS 115 1 | LN | 221 | 95.5 | 2014 | 107.5 | 2013 | 107.5 | 2013 | 106.9 | 2013 | 107.1 | 2013 | 106.8 | 2013 | 106.5 | 2013 | 106.4 | 2013 | 103.1 | 2014 | 107.5 | 2013 | 106 | 2013 | 304504 E9-N JAX 115 304530 JACKSNVL 115 1
LOCAL- PROJECT NEEDED | JCKSNVLLE - JCKSONVLL CITY 115KV WEST | 304504 E9-N JAX 115 304530 JACKSNVL 115 1 | LN | 220 | 96.2 | 2014 | 108.9 | 2012 | 108.9 | 2012 | 108.3 | 2012 | 108.5 | 2012 | 108.5 | 2012 | 108.1 | 2012 | 107.9 | 2012 | 108.9 | 2012 | 108.9 | 2012 | 107.6 | 2012 | JAX-TARAWA230_&_JAX-NORTHWDS115
LOCAL- PROJECT NEEDED | JCKSNVLLE - JCKSONVLL CITY 115KV WEST | 304504 E9-N JAX 115 304536 JAX CITY 115 1 | LN | 221 | 88.9 | 2017 | 100.7 | 2015 | 100.7 | 2015 | 100.1 | 2015 | 100.3 | 2015 | 100.2 | 2015 | 99.9 | 2017 | 99.7 | 2017 | 100.7 | 2015 | 100.7 | 2015 | 99.4 | 2017 | JAX-TARAWA230_&_JAX-NORTHWDS115
SCEG ONLY | KINGSTREE - SUMTER 115KV | 304685 ALCOLU 115 304686 SUMTER 115 1 | LN | 119 | [10 empty] | 86.6 | 2022 | [10 empty] | 43008 6KNGSTRE 230 304677 KINGSTRE 230 1
LAURNBRG GEN ONLY | LAURINBURG - WAGRAM 115KV | 304419 WAGRAMSW 115 304421 LAURINBG 115 1 | LN | 201 | [12 empty] | 95.8 | 2018 | [8 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
PROJECT IN 2013 | LAURINBURG 230/115kV BANK #1 & 2 (same) | 304421 LAURINBG 115 304424 LAURINBG 230 1 | TR | 200 | 93.7 | 2019 | [20 empty] | 304421 LAURINBG 115 304424 LAURINBG 230 2
SC-ONLY | MARION - WHITEVILLE 115KV | 304629 NICHOLS 115 304630 MULLINS 115 1 | LN | 179 | [6 empty] | 88.1 | 2021 | [14 empty] | 304587 E1-CHADP 230 304631 MARION 230 1
SCPSA JOINT STUDY | MARION - WHITEVILLE 115KV | 304630 MULLINS 115 304632 MARION 115 1 | LN | 179 | 87.5 | 2017 | 97.6 | 2017 | 96.1 | 2018 | 104.6 | 2014 | 97.5 |  | 103.6 | 2014 | 100.9 | 2015 | 94.2 | 2019 | 95.7 | 2018 | 95.4 | 2018 | 99.1 | 2017 | 304587 E1-CHADP 230 304631 MARION 230 1
OUTSIDE HORIZON | MARION 230/115 BANK #1 & 2 (same) | 304631 MARION 230 304632 MARION 115 1 | TR | 200 |  |  | 88 | 2025 | 87.8 | 2025 | 91 | 2024 | 88.5 | 2025 | 90.3 | 2024 | 90.4 | 2024 | 87.3 | 2025 | 87.7 | 2025 | 87.6 | 2025 | 87.6 | 2025 | 304631 MARION 230 304632 MARION 115 2
LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304137 METHOD 115 304153 TRYON HL 115 1 | LN | 108 |  |  | 91.1 | 2020 | 91.2 | 2020 | 91.4 | 2020 | 92 | 2020 | 91.9 | 2020 | 91 | 2020 | 91.2 | 2020 | 90.9 | 2020 | 90.9 | 2020 | 91.3 | 2020 | 304174 I-PERSTP 115 304181 GARNER E 115 1
LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304163 MILBURNE 115 304181 GARNER E 115 1 | LN | 118 |  |  | 93.3 | 2019 | 93.9 | 2019 | 94.9 | 2019 | 95.3 | 2018 | 95.6 | 2018 | 96.2 | 2018 | 96.8 | 2018 | 97 | 2018 | 95.6 | 2018 | 96 | 2018 | 304156 ROL/SQ T 230 304190 WAKE 230 1
LOCAL- PROJECT NEEDED | METHOD - MILBURNIE 115KV SOUTH | 304174 I-PERSTP 115 304181 GARNER E 115 1 | LN | 118 |  |  | 85.6 | 2022 | 85.7 | 2022 | 85.2 | 2022 | 85.2 | 2022 | 85.4 | 2022 |  |  | 85.3 | 2022 | 86.8 | 2022 | 86.7 | 2022 | 85.2 | 2022 | METHOD-PRISONF230_&_METHOD-BLUERDG230
LOCAL | METHOD - RALEIGH 115KV | 304137 METHOD 115 304150 I-NCSU S 115 1 | LN | 190 |  |  | 91.9 | 2020 | 92 | 2020 | 92.2 | 2020 | 92.6 | 2019 | 92.7 | 2019 | 91.8 | 2020 | 92 | 2020 | 91.7 | 2020 | 91.7 | 2020 | 92.1 | 2020 | 304163 MILBURNE 115 304168 YONKERS 115 1
LOCAL | METHOD - RALEIGH 115KV | 304148 RALEIGH 115 304150 I-NCSU S 115 1 | LN | 159 |  |  | 86.7 | 2022 | 86.8 | 2022 | 87 | 2022 | 87.4 | 2022 | 87.5 | 2021 | 86.6 | 2022 | 86.8 | 2022 | 86.6 | 2022 | 86.5 | 2022 | 86.9 | 2022 | 304163 MILBURNE 115 304168 YONKERS 115 1
LOCAL- PROJECT NEEDED | MILBURNIE - MORDECAI 115KV | 304163 MILBURNE 115 304168 YONKERS 115 1 | LN | 190 | 85.8 | 2018 | 94.1 | 2019 | 94.2 | 2019 | 94.5 | 2019 | 95 | 2018 | 94.9 | 2019 | 94.1 | 2019 | 94.2 | 2019 | 93.8 | 2019 | 93.8 | 2019 | 94.3 | 2019 | 304137 METHOD 115 304150 I-NCSU S 115 1
LAURNBRG GEN ONLY | RAEFORD 230KV SUB - WAGRAM 115KV | 304411 RAEFORD 115 304416 MAXAPT T 115 1 | LN | 190 | [12 empty] | 87.2 | 2022 | [8 empty] | 304378 RICHMOND 230 304415 RAEFORD 230 1
PROJECT NEEDED | RAEFORD 230KV SUB - WAGRAM 115KV | 304416 MAXAPT T 115 304419 WAGRAMSW 115 1 | LN | 190 | [6 empty] | 86.9 | 2022 | 85.4 | 2022 | 87.3 | 2022 | 100.3 | 2015 | [6 empty] | 85.3 | 2022 | 304378 RICHMOND 230 304415 RAEFORD 230 1
LAURNBRG GEN ONLY | RICHMOND - ROCKINGHAM 230KV | 304348 RKH 230 304378 RICHMOND 230 1 | LN | 1014 | [12 empty] | 86.5 | 2022 | [8 empty] | 304348 RKH 230 304378 RICHMOND 230 2
? OP. PROC. ? | ROCKINGHAM - WEST END 230KV WEST | 304348 RKH 230 304638 WDSB T 230 1 | LN | 539 | 96.6 | 2014 | 104.3 | 2014 | 102.7 | 2014 | 105.8 | 2013 | 105.6 | 2013 | 106.3 | 2013 | 106.8 | 2013 | 104.3 | 2014 | 101.9 | 2015 | 101.5 | 2015 | 105.4 | 2013 | 304348 RKH 230 304361 WEST END 230 1
? OP. PROC. ? | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304361 WEST END 230 1 | LN | 507 | 85.1 | 2018 | 91.7 | 2020 | 90.1 | 2020 | 93.2 | 2019 | 93.1 | 2019 | 93.8 | 2019 | 94.4 | 2019 | 91.8 | 2020 | 89.3 | 2021 | 88.8 | 2021 | 92.9 | 2019 | 304348 RKH 230 304361 WEST END 230 1
? OP. PROC. ? | ROCKINGHAM - WEST END 230KV WEST | 304360 ELLERBE 230 304638 WDSB T 230 1 | LN | 507 | 89.5 | 2017 | 96.5 | 2018 | 94.9 | 2019 | 98.1 | 2017 | 97.9 | 2017 | 98.6 | 2017 | 99.2 | 2017 | 96.6 | 2018 | 94.1 | 2019 | 93.6 | 2019 | 97.7 | 2017 | 304348 RKH 230 304361 WEST END 230 1
SELMA GEN ONLY | SELMA 230/115kV Bank #1 & 2 (exact same) | 304177 SELMA 115 304192 SELMA 230 1 | TR | 200 | [18 empty] | 91.1 | 2024 |  |  | 304177 SELMA 115 304192 SELMA 230 2
SCEG ONLY | SUMTER - SCE&G CANADYS 230KV | 42001 6SANTEE 230 304699 SUMMER T 230 1 | LN | 273 | [8 empty] | 85.9 | 2022 | 90.6 | 2020 | [10 empty] | 42002 6WATEREE 230 304700 SUMTER 230 1
SCEG ONLY | SUMTER - SCE&G EASTOVER 115KV | 42003 3EASTOVE 115 304696 SHAW TAP 115 1 | LN | 118 | [10 empty] | 91.5 | 2020 | [10 empty] | SUMT-SUMMRTN230_&_SUMT-WATEREE230
SCEG ONLY | SUMTER - SCE&G WATEREE PLANT 230KV | 42002 6WATEREE 230 304700 SUMTER 230 1 | LN | 500 | [10 empty] | 89.7 | 2021 | [10 empty] | 304018 ROB 2 N 230 304864 ROB #2 22.0 1
OP. PROC. | SUTTON PLANT - CASTLE HAYNE 230KV | 304039 SUT 3 F 230 304554 9THORG T 230 1 | LN | 590 | 107.3 | 2009 | 117.7 | 2008 | 117.3 | 2009 | 120.8 | 2007 | 117.4 | 2009 | 118.1 | 2008 | 118 | 2008 | 119.6 | 2008 | 116.3 | 2009 | 116.6 | 2009 | 119.5 | 2008 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
OP. PROC ? PROJECT NEEDED? | SUTTON PLANT - CASTLE HAYNE 230KV | 304550 CSTL HYN 230 304577 MURRAYVL 230 1 | LN | 590 | 86.9 | 2018 | 95.4 | 2018 | 95 | 2018 | 98.5 | 2017 | 95.3 | 2018 | 96 | 2018 | 96.6 | 2018 | 97.1 | 2018 | 94.1 | 2019 | 94.4 | 2019 | 97.2 | 2018 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
OP. PROC ? PROJECT NEEDED? | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304554 9THORG T 230 1 | LN | 590 | 99.2 | 2013 | 109.1 | 2012 | 108.7 | 2012 | 112.1 | 2011 | 108.9 | 2012 | 109.6 | 2012 | 109.7 | 2012 | 110.9 | 2011 | 107.7 | 2012 | 108.1 | 2012 | 110.9 | 2011 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
OP. PROC ? PROJECT NEEDED? | SUTTON PLANT - CASTLE HAYNE 230KV | 304552 WILMEAST 230 304577 MURRAYVL 230 1 | LN | 590 | 91.6 | 2016 | 100.7 | 2015 | 100.3 | 2015 | 103.8 | 2014 | 100.6 | 2015 | 101.3 | 2015 | 101.7 | 2015 | 102.4 | 2015 | 99.4 | 2017 | 99.7 | 2017 | 102.5 | 2015 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
OP. PROC. | SUTTON PLANT - DELCO 230KV | 304039 SUT 3 F 230 304582 DELCO 230 1 | LN | 478 | 90.8 | 2016 | 108 | 2012 | 107.3 | 2013 | 113.3 | 2010 | 111.1 | 2011 | 112.7 | 2010 | 111.9 | 2011 | 112.4 | 2011 | 106 | 2013 | 105.7 | 2013 | 114.1 | 2010 | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
LOCAL | SUTTON-CASTLE HAYNE 115KV LINE #2 | 304035 SUT 1-2F 115 304545 CASTLE H 115 2 | LN | 131 | 85.4 | 2018 | [20 empty] | BR1-BARCK230_&_BR2-BARCRK230(bus#chng)
PROJECT | WAKE 500/230 KV BANKS | 304183 WAKE 500 B$0831 WAKE#1 1.00 1 | TR | 1000 | 94.7 | 2018 | 100 | 2020 | 101.5 | 2019 | 103.4 | 2019 | 105.4 | 2018 | 105.3 | 2018 | 103.5 | 2019 | 104.4 | 2018 | 96.6 | 2021 | 94.9 | 2022 | 103 | 2019 | 3Wnd: OPEN B$0832 WAKE#2 2
WSPN GEN ONLY | WEATHERSPOON 230/115kV | 304046 WSPN BUS 230 304047 WSP BUS 115 1 | TR | 200 | [20 empty] | 91.5 | 2023 | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1
OP. PROC. | WEATHERSPOON PLANT - MARION 115KV | 304448 FAIRMONT 115 304654 DILLON T 115 1 | LN | 97 | [6 empty] | 87.6 | 2021 |  |  | 85.4 | 2022 | [10 empty] | 304663 LATTA 230 304682 DILLMP T 230 1
LOCAL- ?PROJECT NEEDED | WSPN PL. - FAYETTEVILLE DUP. SW. ST. 115KV | 304047 WSP BUS 115 304406 ST PAULS 115 1 | LN | 119 | [6 empty] | 88.5 | 2021 | 85.2 | 2022 | 88.3 | 2021 | 91.5 | 2020 | [6 empty] | 100.9 | 2020 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
WSPN GEN ONLY | WSPN PL. - FAY'VILLE DUP. SW. ST. 115KV | 304406 ST PAULS 115 304412 F DUP SW 115 1 | LN | 119 | [20 empty] | 87 | 2022
WSPN GEN ONLY | WSPN PLANT - FAYETTEVILLE 230KV | 304046 WSPN BUS 230 304387 P1-FAY 0 230 1 | LN | 478 | [20 empty] | 85.9 | 2022 | FAY-HAMLET230_&_RAEFORD-ROCKFISH230
SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304046 WSPN BUS 230 304682 DILLMP T 230 1 | LN | 478 | [6 empty] | 89.2 | 2021 |  |  | 87.6 | 2021 | [10 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
SC&SCEG ONLY | WSPN PLANT - LATTA 230KV | 304663 LATTA 230 304682 DILLMP T 230 1 | LN | 507 | [6 empty] | 93.4 | 2019 |  |  | 91.9 | 2020 | [10 empty] | WHITEVL-E1_CHADP230_&_WHTVL12T-WH_IND_T115
OP. PROC. | WSPN PLANT - MARION 115KV | 304632 MARION 115 304654 DILLON T 115 1 | LN | 97 | 102.6 | 2010 | 115.5 | 2009 | 113 | 2010 | 126.4 | 2005 | 113.1 | 2010 | 124.3 | 2006 | 113.4 | 2010 | 110.6 | 2011 | 112.7 | 2010 | 112 | 2011 | 102.3 | 2015 | 304663 LATTA 230 304682 DILLMP T 230 1
WSPN GEN ONLY | WSPN PLANT - RAEFORD 230KV SUB 115KV | 304047 WSP BUS 115 304432 PA-LMB#2 115 1 | LN | 133 | [20 empty] | 89.2 | 2021 | 304378 RICHMOND 230 304415 RAEFORD 230 1
Note on A25: RUN WAYNE CO.
Note on A62: Back down Gen
Note on A66: Back down Gen
Note on A70: OPEN 115kV LINE
Note on A76: OPEN LINE
Note on C3: PTI: ** From bus ** ** To bus ** Circuit Type
Note on E3: PTI: Branch Rating
Note on AB3: PTI: Contingency Description