NC Transmission Planning Collaborative

Planning Work Group (PWG)

Meeting Minutes

June 17, 2008

Duke Energy, Fairfax Operations Center

Greensboro, NC

10:00 AM – 3:00 PM Eastern

Attendees:

Denise Roeder						ElectriCities

Laura Lee 							Duke Energy

Bob Pierce							Duke Energy

Bob Beadle							NCEMC

James Manning						NCEMC

Mark Byrd							Progress Energy

Joey West							Progress Energy

Rick Anderson						Fayetteville PWC

Rich Wodyka							Accenture

Pam Kozlowski						Accenture

Frank Gaffney						R.W. Beck

- ADMINISTRATIVE

- Bob Beadle called the meeting to order at 10:01 AM.

- The group reviewed and approved the May PWG meeting minutes.

ACTION ITEM: Pam will post the meeting minutes to the PWG site.

- OSC UPDATE

- Rich Wodyka gave an update of the items discussed on the OSC and TAG meetings on May 9th:

  - The TAG did not submit any other questions or comments on the 2007 Supplemental Study other than the clarification already requested by Kim Jones of the NCUC (a footnote was included in the study report to address her question regarding costs). The final study report has been published.

  - PJM’s legal department is reviewing a proposed agreement to coordinate transmission planning studies with the transmission providers in the NCTPC. The studies and results would be discussed and reviewed by the PWG.

  - Ed Ernst has been in touch with Yadkin on a planning agreement similar to the one currently being discussed with PJM. Yadkin staff members are interested in the offer and are reviewing the proposed agreement.

  - Duke Energy and Progress Energy legal counsels have concluded that NCUC public staff and commissioners should go through the same confidentiality agreement process as other TAG stakeholders interested in seeing data, assumptions etc. for PWG studies. Jeff Trepel (Duke) is checking with FERC staff on whether commission staff can be granted a “hall pass” to review study data without signing a confidentiality agreement.

  - Mark Byrd reported that he has been in contact with Kim Jones to set up a meeting date/time to explain interchange tables.

- PWG ACTION ITEMS

- Mark Byrd completed the “Transmission Project Cost Estimates in the NCTPC” document including a discussion of escalation assumptions. The document was sent to the PWG shortly after the meeting and posted as a reference document on the PWG site.

- Mark Byrd agreed to check on the progress of the transformer ratings study. Mark clarified that the study scope has been refined to look at two specific projects: the Fayetteville 230/115kV banks and the West End 230/115kV banks—both projects include a capacity increase from 200 to 300 MVA and are tentatively scheduled for 2011, pending study results. Mark also agreed to check with Phil Creech on an update to the TRM presentation.

ACTION ITEM: Mark to follow up with internal asset management on transformer ratings study and give a status report at the July PWG meeting. Mark also agreed to follow up with Phil Creech on a TRM implementation update, with a tentative presentation scheduled for the August PWG meeting.

- Mark Byrd reported that the Durham 500kV “loop-in” project has been completed and is in service.

- Rich mentioned that the OSC has asked for an update on the in-service status of collaborative plan projects. The PWG agreed to complete an update at the July PWG meeting to be given to the OSC at their July meeting.

ACTION ITEM: Mark Byrd and Bob Pierce to provide updates to the PWG on projects currently listed in the collaborative plan, including any projects now in service or with modified in-service dates.

- Bob Pierce mentioned that Duke is looking at changing their line rating assumptions for transmission lines as a result of their recent merger.

- Pam Kozlowski reported that work is still underway on the TAG confidentiality agreement.

ACTION ITEM: Pam and Rich to complete changes to the agreement.

- South Carolina Regional Transmission Planning (SCRTP) Meeting and Southeast Inter-Regional Participation Process (SIRPP) Meeting Study Requests

- Bob Beadle gave an update on the June 16th SCRTP meeting, and asked if PWG members were interested in a request for an economic planning study on behalf of the NCTPC. Bob Pierce pointed out that given the relatively small scope of the SCRTP area, it did not look like they would receive very many requests—most would wind up being kicked up to the SIRPP. Further discussion resulted in consensus on two separate requests to study 600 MW from Santee Cooper to the CPLE control area and 600 MW from SCE&G to the Duke control area. The intent of the requests is to line up with existing NCTPC PWG studies.

ACTION ITEM: Bob Beadle will draft the SCRTP study request listed above, circulate it for PWG and OSC approval, and submit the request prior to the 6/30/08 deadline.

- Bob Beadle also mentioned the upcoming SIRPP meeting on 7/10/08, and stated that he was planning to attend the meeting. Bob indicated that study requests were being accepted for this process as well and asked PWG members if they were interested in submitting a request on behalf of the NCTPC. Bob Pierce suggested a study request for a 3000 MW transfer from MISO to VACAR for 2013, pointing out that this would be a sufficiently high level to test system adequacy for bulk power transfers. A study request for a 3000 MW transfer from SOCO to PJM (classic) was also suggested, including an analysis for both directions.

ACTION ITEM: Bob Beadle will draft the SIRPP study request and circulate it for PWG and OSC approval and submit the request prior to the 7/10/08 meeting.

- 2008 STUDY

- Joey West and Bob Pierce agreed to work on a paired file for 500kV elements in the 2018 case for the TPL standards sensitivity. The scope of the TPL standard analysis was also clarified to include all 230kV elements for the P4 & P5 runs. Common elements between Duke and CPLE would still be analyzed at the 500kV level. Frank Gaffney asked if the results could also include a summary of bus voltages below 0.91 per unit for N-2 events.

ACTION ITEM: Duke and PEC to start work on the TPL standard sensitivity and shoot for preliminary results to the PWG by the August PWG meeting (8/19).

- Bob Pierce advised the PWG that he had modeled (4) 50 MW point injections in the Duke 2018 wind case. Joey West reported that the Progress Energy 2018 wind case included 250 MW in 100/100/50 MW point injections near the Morehead City and Bayboro Substations. In the CPLW area, (6) 50 MW point injections were modeled at the Cane River 230kV, Black Mountain 115kV, Oteen 115kV, Cradle of Forestry 115kV, Maggie Valley 115kV, and Marshall 115kV Subs.

ACTION ITEM: Duke and PEC to complete preliminary results for the wind cases by the next PWG meeting on July 9th.

- Joey West reviewed the results from the reliability screenings for the CPLE area for the 2013S case. Joey reported that the Chestnut Hills-Milburnie 115kV line is a local loading issue. Joey added that the 115kV lines in the Wake Forest area were also showing up as a local loading issue. An existing internal project scheduled for 2014 will help with the problems but will only alleviate the problem longer term. Mark Byrd mentioned that Progress Energy currently has an operating procedure to move the load around in case of a contingency but the area is being studied in greater detail with an additional project likely to be announced later this year. Frank Gaffney asked whether a new local project in the Falls-Franklinton should be included in the collaborative plan since it is a local loading issue, but the cost may be over $10 Million. Mark responded that it would be appropriate to include it in the collaborative plan if the cost is above $10 Million and agreed to give an update on this item at the next meeting.

ACTION ITEM: Mark Byrd will update the PWG on the Falls-Henderson (Wake Forest) area loading study at the July PWG meeting.

- Mark Byrd gave an overview of the Sutton 115kV contingency, adding that it was a low probability but high consequence contingency since the Brunswick units would need to back down in order to avoid a line overload for the loss of a common tower on the river. One solution would be to separate the lines into two separate river crossings, as the loss of only one line does not present any issues.

- Bob Pierce discussed the results in the Duke screening, adding that the load growth used in the case was 1.6% (vs. 2% last year). The lower amount takes into account the effect of CFL regulations, energy efficiency efforts related to RPS implementation and slower economic conditions. Bob further clarified that the proposed Lee Nuclear Plant was not included in either case as it would be in service in 2018 at the very earliest. All cases had the new generation at Cliffside, Buck, and Dan River included. Bob Pierce also discussed analysis on the Antioch 500/230kV banks, adding that they have a flat rating at 840 MVA due to stray flux issues. If loading on the banks can stay within this level until 2011-2013, additional generation will be in service and should help with loading issues. Bob added that the NCTPC planning studies look fine but PJM transactions could account for additional loading on the banks not showing up in the study results.

- Frank Gaffney asked whether the base case should show the Yadkin High Rock-Tuckertown 100kV line open, as the pre-contingency loading on this line is in the range of 70-80% and it has picked up almost 20% in 5 years. Study screenings show a loading level of 130% by 2018. Rich pointed out that Order 890 imposes an obligation to report problems perceived on neighboring systems, even if an operating procedure addresses the problem. PWG members concluded that it might be appropriate to bring this to the OSC and ask if further action is needed. Bob Pierce performed a quick screening analysis of the base case with the Yadkin High Rock-Tuckertown 100kV line open and reported to the group that the OPG currently being used was still effective.

ACTION ITEM: Bob Beadle will advise the OSC of the screening results for the Yadkin facilities and ask whether the OSC perceives the need for any additional discussion with Yadkin in light of Order 890 requirements.

- LARGE GENERATOR INTERCONNECTION

- Mark Byrd gave an update of activity in Progress Energy’s generation queue, adding that Progress Energy has plans to move forward with another Wayne County unit in 2009 and the Richmond CC project in 2011. Other projects may also be forthcoming, including more CT’s at Wayne County. Bob Pierce asked about affiliate designations on generation queue requests, as they are no longer included in the Duke queue. Mark responded that the Progress Energy queue does not list affiliate designations. Mark added that he would not expect the need for any additional 230kv transmission to support a second unit at the Harris Plant as (8) 230kV lines extend from the plant switchyard and the original planning and construction took into account facilities to accommodate (4) units.

- 2008 WORK PLAN AND SCHEDULE

- PWG members reviewed the work plan and schedule, and concluded that the 2008 study process is on schedule.

- The next PWG meeting will be a conference call at 10am on July 9th (Bob Beadle will make arrangements for a call-in number and notify the PWG).

- Rich reported that he expects the next TAG meeting to be held in late August or early September.

- OTHER ITEMS

Bob Beadle adjourned the meeting at approximately 2:45 PM.