## Duke Summary
Transmission Facility | Worst-Case Information | 2012 Summer Base (2007 Study) | 2013 Summer Base | 2013 Summer Base with Fayetteville | 2018 Summer Base | 2018 Summer with Wind Generation | 2013 Summer Base PEC TRM Brunswick 1 Down | 2013 Summer Base PEC TRM Harris Down | 2013 Summer Base with Fayetteville PEC TRM Brunswick 1 Down | 2013 Summer Base with Fayetteville PEC TRM Harris Down | 2018 Summer Base PEC TRM Brunswick 1 Down | 2018 Summer Base PEC TRM Harris Down | COMMENTS | Transmission Facility
| Post-Contingency Loading (MVA) | 87.8 | 77.7 | 77.9 | 76.8 | 76.8 | - | - | - | - | 74.8 | 74.8 | Cont / 12 Hour / LTE Ratings 58.5 / 71.2 / 58.5 MVA
Wateree 100 kV Line | % Facility Rating | 114.9% | 101% | 101% | 100.8% | 100.8% | < 70% | < 70% | < 70% | < 70% | 97.9% | 98% | 2/0 Cu Conductor Limited (75°, 90° limits for Cu lines) | Wateree 100 kV Line
(Wateree-Great Falls) | Year Upgrade Required | 2012 | 2013 | 2013 | 2018 | 2018 | - | - | - | - | 2020 | 2020 | 2/0 Cu Conductor 58.5 / 71.2 / 58.5 MVA | (Wateree-Great Falls)
| Contingency | All5Gm w/ Wateree 100 kV Line | All5Gm w/ Wateree 100 kV Line | Oco3Gm w/Wateree 100 kV Line | Mcg1Gm w/Wateree 100 kV Line | Mcg1Gm w/Wateree 100 kV Line | - | - | - | - | Wateree 100 kV Line | Wateree 100 kV Line | Operating Guide in effect (Wateree 115/100 kV transformer open) - will need to reduce generation
| Post-Contingency Loading (MVA) | 118.3 | - | [9 empty] | 12 Hour / LTE Ratings 150 / 150 MVA
Wateree 115/100 kV | % Facility Rating | 78.8% | < 70% | [9 empty] | Transformer Limited | Wateree 115/100 kV
Transformer | Year Upgrade Required | 2025 | - | [9 empty] | Transformer 150 MVA | Transformer
| Contingency | Cli3Gm w/ Cat1Gc | - | [9 empty] | Operating Guide in effect (Wateree 115/100 kV transformer open)
| Post-Contingency Loading (MVA) | 117.4 | 114.9 | 112.9 | 113.3 | 92.1 | 112.1 | 111.9 | 110.9 | 110.8 | 109.9 | 109.8 | LTE Rating 108.3 MVA
Horseshoe 115/100 kV | % Facility Rating | 108.4% | 106.1% | 104.3% | 104.6% | 85% | 103.5% | 103.4% | 102.4% | 102.3% | 101.4% | 101.4% | 300 Cu Limited | Horseshoe 115/100 kV
Transformer | Year Upgrade Required | 2012 | 2013 | 2013 | 2018 | 2029 | 2013 | 2013 | 2013 | 2013 | 2018 | 2018 | Transformer 127 MVA | Transformer
| Contingency | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Cli5Gm w/ Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | Horseshoe 115/100 kV Transformer | 300 Cu, 1/2" Cu Pipe, 600 Cu Switch Upgrades (134.5 MVA) pushes to 2023
| Post-Contingency Loading (MVA) | 406 | 383.8 | 388.6 | 419 | 417.5 | 400.6 | 400.5 | 410.1 | 410 | 413.1 | 412.8 | Cont Rating 436.9 MVA - Should use 12 Hour Rating 478 MVA
Sandy Ridge 230 kV Line | % Facility Rating | 96.8% | 89.8% | 90.9% | 100.8% | 100.5% | 93.9% | 93.9% | 96.3% | 96.3% | 98.7% | 98.8% | CT/5 Ratio, CT/5-M Ratio, and 51XYZ Relay Limited | Sandy Ridge 230 kV Line
(Newport-Morning Star) | Year Upgrade Required | 2014 | 2020 | 2020 | 2018 | 2018 | 2017 | 2017 | 2016 | 2016 | 2019 | 2019 | 954 ACSR Conductor 506.7 MVA | (Newport-Morning Star)
| Contingency | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/ Richmond-Newport 500 kV Line | Mcg1Gm w/Anson-Oakboro 230 kV Line | Mcg1Gm w/Anson-Oakboro 230 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Reconductor Required by 2024 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 451.6 | 440 | 470.3 | 488.2 | 488.1 | 450.2 | 456.2 | 458.5 | 464.2 | 497.2 | 503.1 | 12 Hour Rating 478 MVA
Pleasant Garden 230 kV Line | % Facility Rating | 92.9% | 89.7% | 96% | 99.8% | 99.8% | 92.4% | 93.9% | 94.4% | 95.8% | 103.8% | 105.3% | CT/5 Ratio Limited | Pleasant Garden 230 kV Line
(Belews Creek-Bob White Tap) | Year Upgrade Required | 2016 | 2020 | 2016 | 2019 | 2019 | 2018 | 2017 | 2017 | 2016 | 2018 | 2018 | 2156 ACSR Conductor 851.7 MVA | (Belews Creek-Bob White Tap)
| Contingency | Oco3Gm w/ Godbey 500 kV Line | RwgsGm w/ Belews Creek 230 kV Line | Mcg2Gm w/Belews Creek 230 kV Line | RwgsGm w/ Belews Creek 230 kV Line | RwgsGm w/ Belews Creek 230 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | CT Upgrade (764.9 MVA) pushes out to 2048 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 433 | 428.7 | 428.1 | 468.8 | 483.9 | 402.7 | 404.1 | 411.3 | 412.5 | 452.3 | 453.7 | 12 Hour Rating 478 MVA
Fisher 230 kV Line | % Facility Rating | 91.7% | 90.8% | 90.6% | 100.5% | 103.9% | 85% | 85.3% | 86.9% | 87.2% | 96.8% | 97.1% | CT/5 Ratio and 51XYZ Relay Limited | Fisher 230 kV Line
(Central-Shady Grove Tap) | Year Upgrade Required | 2017 | 2020 | 2020 | 2018 | 2018 | 2024 | 2024 | 2022 | 2022 | 2021 | 2020 | (17.8 miles) 954 ACSR Conductor 506.7 MVA | (Central-Shady Grove Tap)
| Contingency | Cli5Gm w/ Fisher 230 kV Line | Cli5Gm w/ Fisher 230 kV Line | Cli5Gm w/ Fisher 230 kV Line | Cli5Gm w/ Fisher 230 kV Line | Cat1Gm w/Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Reconductor Required by 2020 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | - | - | - | 317.4 | 319.3 | - | - | - | - | - | - | LTE Rating 458.1 MVA
Fisher 230 kV Line | % Facility Rating | < 70% | < 70% | < 70% | 70.5% | 70.9% | < 70% | < 70% | < 70% | < 70% | < 70% | < 70% | 954 ACSR Conductor Limited | Fisher 230 kV Line
(North Greenville-Shady Grove Tap) | Year Upgrade Required | - | - | - | 2041 | 2040 | - | - | - | - | - | - | 954 ACSR Conductor 458.1 MVA | (North Greenville-Shady Grove Tap)
| Contingency | - | - | - | Cat1Gm w/Fisher 230 kV Line and Shady Grove 230/100 kV Transformer | Cat1Gm w/Fisher 230 kV Line and Shady Grove 230/100 kV Transformer | - | - | - | - | - | - | Reconductor Required by 2040 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) |  | 130.6 | 141.7 | 145.1 | 144.8 | 130.5 | 131.8 | 136.9 | 138 | 150.1 | 151.4 | 12 Hour Rating 113.1 MVA
Elon White 100 kV Line | % Facility Rating |  | 112.2% | 121.8% | 125.1% | 124.8% | 112.3% | 113.5% | 117.9% | 119.1% | 130.4% | 131.7% | 336 ACSR Conductor Limited | Elon White 100 kV Line
(Glen Raven-Reidsville Tap) | Year Upgrade Required |  | 2013 | 2013 | 2018 | 2018 | 2013 | 2013 | 2013 | 2013 | 2018 | 2018 |  | (Glen Raven-Reidsville Tap)
| Contingency |  | Oco3Gm w/Haw River W 100 kV Line | Mcg2Gm w/Haw River W 100 kV Line | ThrpGm w/Haw River 100 kV Line | RwgsGm w/Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | (Related to Dan River Generation)
| Post-Contingency Loading (MVA) | 84.9 | 125.2 | 136.1 | 139.1 | 138.7 | 125 | 126.3 | 131.3 | 132.5 | 143.9 | 145.2 | 12 Hour Rating 113.1 MVA
Elon Black 100 kV Line | % Facility Rating | 99.2% | 107.9% | 117.5% | 120.5% | 120.1% | 108% | 109.2% | 113.6% | 114.8% | 125.6% | 127% | 336 ACSR Conductor Limited | Elon Black 100 kV Line
(Glen Raven-Reidsville Tap) | Year Upgrade Required | 2020 | 2013 | 2013 | 2018 | 2018 | 2013 | 2013 | 2013 | 2013 | 2018 | 2018 | (18.68 miles) 336 ACSR Conductor 113.1 MVA | (Glen Raven-Reidsville Tap)
| Contingency | Joc1Gm w/ Haw River 100 kV Line | Oco3Gm w/Haw River W 100 kV Line | Mcg2Gm w/Haw River W 100 kV Line | ThrpGm w/Haw River 100 kV Line | RwgsGm w/Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | Haw River 100 kV Line | (Related to Dan River Generation)
| Post-Contingency Loading (MVA) | 688.5 | 767.4 | 739.2 | 828.6 | 829.4 | 762.9 | 763.7 | 736.5 | 737.3 | 850.6 | 851.4 | 12 Hour Rating 796.7 MVA
Pinoca 230 kV Line | % Facility Rating | 86.2% | 93.5% | 90% | 103.6% | 103.7% | 93.7% | 93.8% | 90.3% | 90.5% | 106.4% | 106.6% | CT/5 Ratio Limited | Pinoca 230 kV Line
(Lakewood-Riverbend) | Year Upgrade Required | 2020 | 2018 | 2020 | 2018 | 2018 | 2018 | 2018 | 2020 | 2020 | 2018 | 2018 | 2-954 ACSR Conductor 1176.4 MVA | (Lakewood-Riverbend)
| Contingency | Riv7Gm w/ Pinoca 230 kV Line | Riv7Gm w/ Pinoca 230 kV Line | Riv7Gm w/ Pinoca 230 kV Line | All5Gm w/Pinoca 230 kV Line | All5Gm w/Pinoca 230 kV Line | Pinoca 230 kV Line | Pinoca 230 kV Line | Pinoca 230 kV Line | Pinoca 230 kV Line | Pinoca 230 kV Line | Pinoca 230 kV Line | CT Upgrade (876.4 MVA) pushes out to 2022 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) |  | - | 610.7 | 787 | 791.6 | - | - | - | - | 692.9 | 689.8
Jacobs 230 kV Lines | % Facility Rating |  | < 70% | 93.8% | 121.6% | 122% | < 70% | < 70% | < 70% | < 70% | 107.6% | 107.2% |  | Jacobs 230 kV Lines
(Belews Creek-Ernest) | Year Upgrade Required |  | - | 2018 | 2018 | 2018 | - | - | - | - | 2018 | 2018 |  | (Belews Creek-Ernest)
| Contingency |  | - | Bel1Gm w/Jacobs 230 kV Line | Bel1Gm w/Jacobs 230 kV Line | Bel1Gm w/Jacobs 230 kV Line | - | - | - | - | Jacobs 230 kV Line | Jacobs 230 kV Line | (Related to Rockingham CT Generation)
| Post-Contingency Loading (MVA) |  | 488.2 | 492.4 | 648.2 | 645 | 428.3 | 431.3 | 406 | 409.1 | 561.2 | 564
Sadler 230/100 kV | % Facility Rating |  | 88.2% | 88.9% | 117.1% | 116.5% | 77.4% | 77.9% | 73.3% | 73.9% | 101.4% | 101.9% |  | Sadler 230/100 kV
Transformer Bank 3 | Year Upgrade Required |  | 2021 | 2021 | 2018 | 2018 | 2030 | 2029 | 2033 | 2033 | 2018 | 2018 |  | Transformer Bank 3
| Contingency |  | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | (Related to Dan River Generation)
| Post-Contingency Loading (MVA) |  | 475.2 | 479.5 | 634.6 | 631.5 | 414.9 | 417.8 | 392.4 | 395.1 | 546.9 | 549.7
Sadler 230/100 kV | % Facility Rating |  | 85.8% | 86.6% | 114.6% | 114% | 74.9% | 75.5% | 70.9% | 71.4% | 98.8% | 99.3% |  | Sadler 230/100 kV
Transformer Bank 4 | Year Upgrade Required |  | 2023 | 2023 | 2018 | 2018 | 2032 | 2031 | 2035 | 2035 | 2019 | 2019 |  | Transformer Bank 4
| Contingency |  | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | DrgsGm w/Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | Sadler 230/100 kV Transformer | (Related to Dan River Generation)
| Post-Contingency Loading (MVA) | - | 203.1 | 220.2 | 218 | 217 | 210.6 | 213.9 | 221.7 | 224.7 | 232 | 235.2
Alamance 100 kV Black Line | % Facility Rating | - | 100.9% | 109.7% | 110.2% | 108.9% | 105% | 107% | 110.9% | 112.7% | 118.1% | 120.2% |  | Alamance 100 kV Black Line
(Burlington Tap-Mebane) | Year Upgrade Required | - | 2013 | 2013 | 2018 | 2018 | 2013 | 2013 | 2013 | 2013 | 2018 | 2018 |  | (Burlington Tap-Mebane)
| Contingency | - | Oco3Gm w/ Alamance 100 kV Line | Mcg2Gm w/Alamance W 100 kV Line | ThrpGm w/Alamance 100 kV Line | NantGm w/Alamance 100 kV Line | Alamance 100 kV Line | Alamance 100 kV Line | Alamance 100 kV Line | Alamance 100 kV Line | Alamance 100 kV Line | Alamance 100 kV Line | (Related to Dan River Generation)
| Post-Contingency Loading (MVA) | Yadkin Not Monitored | 120.4 | 113.4 | 130.8 | 126.1 | 95 | 97.1 | 93.7 | 95.7 | 103.1 | 105.5 | Rating 102 MVA
High Rock-Tuckertown 100 kV Line | % Facility Rating |  | 118.4% | 111.5% | 129.5% | 124.6% | 93.2% | 95.4% | 92% | 94% | 104.6% | 107.3% | ???? Limited | High Rock-Tuckertown 100 kV Line
(Yadkin) | Year Upgrade Required |  | 2013 | 2013 | 2018 | 2018 | 2018 | 2016 | 2019 | 2017 | 2018 | 2018 | Line ???? MVA | (Yadkin)
| Contingency |  | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Yadkin: (Op Guide)
| Post-Contingency Loading (MVA) | Yadkin Not Monitored | 123 | 115.8 | 134.5 | 129.4 | 96.8 | 99 | 95.5 | 97.6 | 105.8 | 108.4 | Rating 116 MVA
Badin-Tuckertown 100 kV Line | % Facility Rating |  | 104.2% | 98.1% | 113.9% | 109.6% | 82% | 83.9% | 80.9% | 82.7% | 91.9% | 94.3% | ???? Limited | Badin-Tuckertown 100 kV Line
(Yadkin) | Year Upgrade Required |  | 2013 | 2015 | 2018 | 2018 | 2026 | 2025 | 2027 | 2025 | 2024 | 2022 | Line ???? MVA | (Yadkin)
| Contingency |  | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Bel1Gm w/ Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Godbey 500 kV Line | Yadkin: (Op Guide)
| Post-Contingency Loading (MVA) | 695.1 | 696.9 | 692.5 | 835.7 | 824.8 | - | 575.5 | - | 574.8 | 656.8 | 666.7 | 12 Hour Rating 796.7 MVA
Moser 230 kV Line | % Facility Rating | 87.1% | 86.5% | 85.4% | 106.1% | 104% | < 70% | 71% | < 70% | 71% | 82.4% | 83.7% | CT Limited | Moser 230 kV Line
(Catawba-Allen) | Year Upgrade Required | 2019 | 2023 | 2023 | 2018 | 2018 | - | 2035 | - | 2035 | 2031 | 2030 | 2-1272 ACSR Conductor 1436.5 MVA | (Catawba-Allen)
| Contingency | All4Gm w/ Moser 230 kV Line | All4Gm w/ Moser 230 kV Line | All4Gm w/ Moser 230 kV Line | Mcg1Gm w/Moser 230 kV Line | Mcg1Gm w/Moser 230 kV Line | - | Moser 230 kV Line | - | Moser 230 kV Line | Moser 230 kV Line | Moser 230 kV Line | CT Upgrade (940.1 MVA) pushes out to 2026 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | - | 497.8 | 506.3 | 646.5 | 655.5 | - | - | - | - | - | - | 12 Hour Rating 617.5 MVA
Norman 230 kV Line | % Facility Rating | < 70% | 78.3% | 79.7 | 103.4% | 104.8% | < 70% | < 70% | < 70% | < 70% | < 70% | < 70% | 1272 ACSR Conductor Limited (Summer) | Norman 230 kV Line
(McGuire-Riverbend) | Year Upgrade Required | - | 2029 | 2028 | 2018 | 2018 | - | - | - | - | - | - | (5.61 miles) 1272 ACSR Conductor 617.5 MVA (Summer) | (McGuire-Riverbend)
| Contingency | - | Cat1Gm w/Norman 230 kV Line | Cat1Gm w/Norman 230 kV Line | Cat1Gm w/Norman 230 kV Line | Cat1Gm w/Norman 230 kV Line | - | - | - | - | - | - | Install reactors or high temperature wire by 2018 (can't reconductor due to fault duty @ McGuire)
| Post-Contingency Loading (MVA) | 1434.8 | 1386.1 | 1403.2 | 1719 | 1724.4 | - | - | - | - | 1190.7 | 1198.5 | 12 Hour Rating 1680 MVA
McGuire 500/230 kV | % Facility Rating | 85.4% | 82.5% | 83.5% | 102.3% | 102.6% | < 70% | < 70% | < 70% | < 70% | 70.9% | 71.3% | Transformer Limited | McGuire 500/230 kV
Transformer Bank A1 | Year Upgrade Required | 2020 | 2026 | 2025 | 2018 | 2018 | - | - | - | - | 2040 | 2040 | Transformer 1680 MVA | Transformer Bank A1
| Contingency | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | Mcg1Gm w/ Godbey 500 kV Line | - | - | - | - | Godbey 500 kV Line | Godbey 500 kV Line | Installation of reactors for Noman 230 kV Lines will reduce loading on this transformer and push replacement beyond 2008-2018 Planning Window
| Post-Contingency Loading (MVA) | 702.3 | 628.8 | 613.8 | 663.4 | 663.9 | 617.2 | 617.5 | 616.2 | 616.4 | 654.2 | 654.5 | 12 Hour rating 717 MVA (should use LTE rating 595.5 MVA)
Steelberry 230 kV Line | % Facility Rating | 101.1% | 88.8% | 86.4% | 94.9% | 94.9% | 86.9% | 86.9% | 86.7% | 86.8% | 93.5% | 93.6% | CT/5-M Ratio Limited | Steelberry 230 kV Line
(Allen-Woodlawn) | Year Upgrade Required | 2012 | 2021 | 2023 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022 | 2023 | 2023 | 2156 ACSR Conductor 792.7 MVA | (Allen-Woodlawn)
| Contingency | All5Gm w/ Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | All5Gm w/ Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | All5Gm w/ Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | All5Gm w/ Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | All5Gm w/ Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | Steelberry 230 kV Line and Woodlawn 230/100/44 kV Transformer | CT upgrade (792.7 MVA) pushes out to 2028 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 1973.2 | 1768.1 | 1811.6 | 1879.6 | 1862.9 | 1689.4 | 1721.1 | 1737.5 | 1765.5 | 1782.9 | 1811.4 | 12 Hour Rating 1904.3 MVA
Godbey 500 kV Line | % Facility Rating | 100.3% | 88.5% | 90.8% | 95% | 94% | 85.3% | 87.2% | 88.1% | 89.9% | 91.2% | 93.2% | CT/5 Ratio Limited | Godbey 500 kV Line
(Woodleaf-Pleasant Garden) | Year Upgrade Required | 2012 | 2021 | 2020 | 2022 | 2022 | 2024 | 2022 | 2021 | 2020 | 2024 | 2023 | 2-2515 ACSR Conductor 4718 MVA | (Woodleaf-Pleasant Garden)
| Contingency | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/ Richmond-Newport 500 kV Line | Bel1Gm w/Rock Springs 500 kV Line | Bel1Gm w/Rock Springs 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | Richmond-Newport 500 kV Line | CT and MVA RDG Limit Upgrades (2669.4 MVA) push out to 2041
| Post-Contingency Loading (MVA) | 726.4 | 704.7 | 752 | 747.5 | 736.1 | 770 | 789.3 | 802.2 | 819.8 | 817.7 | 836 | 12 Hour Rating 796.7 MVA
Parkwoood 500/230 kV | % Facility Rating | 91.2% | 88.5% | 94.4% | 93.8% | 92.4% | 96.7% | 99.1% | 100.7% | 102.9% | 102.6% | 104.9% | CT/5 Ratio Limited | Parkwoood 500/230 kV
Transformer Bank 6 | Year Upgrade Required | 2017 | 2021 | 2017 | 2023 | 2023 | 2016 | 2014 | 2013 | 2013 | 2018 | 2018 | Transformer 1152.7 MVA | Transformer Bank 6
| Contingency | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/Parkwood 500/230 kV Transformer | ThrpGm w/Parkwood 500/230 kV Transformer | NantGm w/Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | CT Upgrade (1028.6 MVA) pushes out to 2033
| Post-Contingency Loading (MVA) | 785.3 | 677.3 | 639 | 720.9 | 725.7 | - | - | - | - | - | - | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 93.5% | 80.6% | 76.1% | 85.8% | 86.4% | < 70% | < 70% | < 70% | < 70% | < 70% | < 70% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 1 | Year Upgrade Required | 2016 | 2027 | 2031 | 2028 | 2028 | - | - | - | - | - | - | Transformer 840 MVA | Transformer Bank 1
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | - | - | - | - | - | - | Increased Transformer Capacity Required by 2028 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 829.6 | 715.1 | 674.8 | 761.3 | 766.3 | 602.4 | 610.8 | 594.7 | 602.8 | 607.7 | 615.8 | 12 Hour Rating 840 MVA
Antioch 500/230 kV | % Facility Rating | 98.8% | 85.1% | 80.3% | 90.6% | 91.2% | 71.7% | 72.7% | 70.8% | 71.8% | 72.3% | 73.3% | Transformer Limited | Antioch 500/230 kV
Transformer Bank 2 | Year Upgrade Required | 2013 | 2024 | 2027 | 2025 | 2024 | 2034 | 2034 | 2035 | 2034 | 2039 | 2038 | Transformer 840 MVA | Transformer Bank 2
| Contingency | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Bel1Gm w/ Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Antioch 500/230 kV Transformer | Increased Transformer Capacity Required by 2024 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 769.6 | - | - | 1107.2 | 1120.2 | - | - | - | - | - | - | 12 Hour Rating 1120 MVA
Newport 500/230 kV | % Facility Rating | 68.7% | < 70% | < 70% | 98.9% | 100% | < 70% | < 70% | < 70% | < 70% | < 70% | < 70% | Transformer Limited | Newport 500/230 kV
Transformer Bank A5 | Year Upgrade Required | 2031 | - | - | 2019 | 2018 | - | - | - | - | - | - | Transformer 1120 MVA | Transformer Bank A5
| Contingency | Cat1Gm w/ Cat2Gc | - | - | Cat1Gm w/Cat2Gc | Cat1Gm w/Cat2Gc | - | - | - | - | - | - | Increased Transformer Capacity Required by 2018
| Post-Contingency Loading (MVA) | 719.7 | 698.1 | 744.9 | 740.6 | 729.2 | 762.5 | 781.5 | 794.3 | 811.4 | 809.6 | 827.6 | 12 Hour Rating 840 MVA
Parkwoood 500/230 kV | % Facility Rating | 85.7% | 83.1% | 88.7% | 88.2% | 86.8% | 90.8% | 93% | 94.6% | 96.6% | 96.4% | 98.5% | Transformer Limited | Parkwoood 500/230 kV
Transformer Bank 5 | Year Upgrade Required | 2020 | 2025 | 2021 | 2026 | 2027 | 2020 | 2018 | 2017 | 2016 | 2021 | 2019 | Transformer 840 MVA - Stray Flux Issues??? | Transformer Bank 5
| Contingency | Cat1Gm w/ Parkwood 500/230 kV Transformer | Cat1Gm w/ Parkwood 500/230 kV Transformer | Oco1Gm w/Parkwood 500/230 kV Transformer | ThrpGm w/Parkwood 500/230 kV Transformer | NantGm w/Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Parkwood 500/230 kV Transformer | Increased Transformer Capacity Required by 2021 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) |  | - | - | 666.2 | 664.2 | - | - | - | - | 581.3 | 584.5 | 12 Hour Rating 717 MVA
Sadler 230 kV Line | % Facility Rating |  | < 70% | < 70% | 90.6% | 90.3% | < 70% | < 70% | < 70% | < 70% | 79.4% | 80% | 1272 ACSR Conductor Limited | Sadler 230 kV Line
(Sadler-Ernest) | Year Upgrade Required |  | - | - | 2025 | 2025 | - | - | - | - | 2033 | 2033 | 1272 ACSR Conductor 718.2 MVA | (Sadler-Ernest)
| Contingency |  | - | - | DrgsGm w/Sadler 230 kV Line | DrgsGm w/Sadler 230 kV Line | - | - | - | - | Sadler 230 kV Line | Sadler 230 kV Line | Reconductor Required by 2025 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 388.4 | 405.8 | 418.8 | 349.8 | 354.7 | 367.2 | 363.8 | 355 | 351.9 | 343.1 | 340.2 | 12 Hour Rating 452.5 MVA
London Creek 230 kV Lines | % Facility Rating | 86.5% | 88.8% | 91.6% | 78.5% | 79.7% | 80.4% | 79.7% | 77.7% | 77% | 77.2% | 76.6% | 795 ACSR Conductor Limited | London Creek 230 kV Lines
(Peach Valley-Riverview) | Year Upgrade Required | 2020 | 2021 | 2019 | 2034 | 2033 | 2027 | 2028 | 2029 | 2030 | 2035 | 2035 | (19.33 miles) 795 ACSR Conductor 452.5 MVA | (Peach Valley-Riverview)
| Contingency | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | Oco1Gm w/ London Creek 230 kV Line | ThrpGm w/ London Creek 230 kV Line | Joc1Gm w/London Creek 230 kV Line | London Creek 230 kV Line | London Creek 230 kV Line | London Creek 230 kV Line | London Creek 230 kV Line | London Creek 230 kV Line | London Creek 230 kV Line | Reconductor Required by 2019 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 369.1 | 393.5 | 388.5 | 392.2 | 421.4 | 366.6 | 365.4 | 365.8 | 364.7 | 370.7 | 369.7 | 12 Hour Rating 478 MVA
Shady Grove 230 kV Line | % Facility Rating | 78.8% | 84.2% | 83.2% | 84.7% | 91.5% | 78.2% | 77.9% | 78.1% | 77.9% | 80.3% | 80.1% | CT/5 Ratio Limited | Shady Grove 230 kV Line
(Shady Grove-Shady Grove Tap) | Year Upgrade Required | 2025 | 2024 | 2025 | 2029 | 2024 | 2029 | 2029 | 2029 | 2029 | 2032 | 2032 | 2515 ACSR Conductor 1085 MVA | (Shady Grove-Shady Grove Tap)
| Contingency | Lee3Gm w/ Fisher 230 kV Line | Lee3Gm w/Fisher 230 kV Line | Lee3Gm w/Fisher 230 kV Line | ThrpGm w/Fisher 230 kV Line | Lee3Gm w/Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | Fisher 230 kV Line | CT Upgrade (669 MVA) pushes out to 2045 (Outside 2008-2018 Planning Window)
| Post-Contingency Loading (MVA) | 374.6 | 368.7 | 368.8 | 411.4 | 420.2 | 343.2 | 344.3 | 351.9 | 352.9 | 374.5 | 387.9 | 12 Hour Rating 573.6 MVA
Dacus 230 kV Line | % Facility Rating | 79.2% | 77.9% | 77.9% | 88.2% | 90% | 72.3% | 72.5% | 74.2% | 74.4% | 79.9% | 82.8% | 51XYZ Relay Limited | Dacus 230 kV Line
(Oconee-North Greenville) | Year Upgrade Required | 2024 | 2029 | 2029 | 2026 | 2025 | 2034 | 2034 | 2032 | 2032 | 2033 | 2030 | (29.25 miles) 1272 ACSR Conductor 617.5 (12 Hour) MVA | (Oconee-North Greenville)
| Contingency | Cli5Gm w/ Dacus 230 kV Line | Cli5Gm w/ Dacus 230 kV Line | Cli5Gm w/ Dacus 230 kV Line | Cat1Gm w/Dacus 230 kV Line | Cat1Gm w/Dacus 230 kV Line | Dacus 230 kV Line | Dacus 230 kV Line | Dacus 230 kV Line | Dacus 230 kV Line | Shiloh 230 kV Line | Dacus 230 kV Line | CT and relay upgrade (617.5) pushes out to 2041 (Outside 2008-2018 Planning Window)
|  | Cliffside 6 800 MW | Cliffside 6 800 MW | Cliffside 6 800 MW | Cliffside 6 800 MW | 50 MW Highland
|  | Buck CC 620 MW | Buck CC 620 MW | Buck CC 620 MW | Buck CC 620 MW | 50 MW Sylva
|  |  | Dan River CC 620 MW | Dan River CC 620 MW | Dan River CC 620 MW | 50 MW Bryson
|  |  | added Rowan CC gm | added Rowan CC gm | added Rowan CC gm | 50 MW Whitier
|  |  | Wateree transformer open | Wateree transformer open | Wateree transformer open
Rockingham CT 628 MW
Note on D6: lxl8987: wateree xfmr open
Note on D90: lxl8987: increase in NR gen
Note on D94: lxl8987: increase in NR gen
Note on D102: lxl8987: increase in NR gen
Note on N101: lxl8987: is this rating right?

## 2012 Base
2 | % Yearly Load Growth |  | 2012 Summer Screening (2007 NCPWG Study Base Case) | [6 empty] | Directory: | P:\Bdm\NC PWG\2007 Study\Thermal Screening\Base12s\
2012 | Study Year |  | Thermal Screening
2012 | Implementation Year
2012 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 88 | > 5% worse | [10 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 53 | Not in original screening | [10 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 141 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings |  |  | GenMaint+LineCont (Base)
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | 2011 Summer Screening (2006 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2012 Summer Screening (2007 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Base | XXs | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | GmLc | Gm | GmGc | GmWh
BEL1GM | SINGLE 38 | 304020 | BRUN 2 N | 304863 | BRUN #2 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 655.6 | 1641.5 | 199.7 | 11861 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 199.7 | 77.3 | 80.1 | 79.3
WATRGM | SINGLE 872 | 304716 | CAM TAP | 304725 | CAMDEN | 1 | 304725 | CAMDEN 115.00 | 304731 | I-DUP CA 115.00 | 1 | 304725-304731-1 | 108 | 108 | 95.3 | 144.2 | 134.4 | 497 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 134.4 | 88.9 | - | 90.3
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEY JOHN 115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 45.8 | 158.3 | 132.2 | 45 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 132.2 | - | - | -
WATRGM | SINGLE 881 | 304725 | CAMDEN | 304731 | I-DUP CA | 1 | 304716 | CAM TAP 115.00 | 304725 | CAMDEN 115.00 | 1 | 304716-304725-1 | 108 | 108 | 71.8 | 132.3 | 124 | 242 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 124 | - | - | 67.8
WATRGM | SINGLE 872 | 304716 | CAM TAP | 304725 | CAMDEN | 1 | 304731 | I-DUP CA 115.00 | 304732 | ELGIN T 115.00 | 1 | 304731-304732-1 | 95 | 95 | 63.3 | 111.2 | 117.8 | 202 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 117.8 | - | - | 70.7
ALL5GM | WATEREE | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 60.3 | 87.8 | 114.9 | 680 | 58.5 | 46.6 | 70.9 | 113.3 | 666 | -1.6 | 2012 | 2015 | 3 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 114.9 | - | - | -
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115.00 | 304284 | WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 118.4 | 233.2 | 114.8 | 135 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 114.8 | - | - | 57.3
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARCRK W |  | 304039 | SUT 3 F 230.00 | 304554 | 9THORG T 230.00 | 1 | 304039-304554-1 | 590 | 590 | 239.3 | 638.9 | 109.2 | 45 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 109.2 | - | - | -
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 65 | 117.4 | 108.4 | 45 | 108.3 | 56.8 | 101.5 | 93.8 | 578 | -14.6 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.4 | - | 65.1 | 58
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 65 | 117.4 | 108.4 | 45 | 108.3 | 56.8 | 101.5 | 93.8 | 578 | -14.6 | 2012 | 2015 | 3 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.4 | - | - | -
ALL5GM | ROB-NUCOR230 | 304018 | ROB 2 N | 304666 | NUCOR T |  | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 1 | 375-416-1 | 58.5 | 58.5 | 60.3 | 67.2 | 107.9 | 635 | 58.5 | 46.6 | 70.9 | 113.3 | 623 | 5.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 107.9 | 96.9 | 129 | 95.2
WATRGM | SINGLE 872 | 304716 | CAM TAP | 304725 | CAMDEN | 1 | 304732 | ELGIN T 115.00 | 304734 | WATRE 115.00 | 1 | 304732-304734-1 | 95 | 95 | 53.7 | 100.9 | 107.4 | 102 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 107.4 | - | - | 61.1
BEL1GM | PARKWOOD2 | 847 | 6PARKWOD | 948 | PARKWOOD | 2 | 847 | 6PARKWOD 230.00 | 948 | PARKWOOD 100.00 | 1 | 847-948-1 | 458 | 458 | 304.2 | 484.4 | 105.8 | 239 | 415.7 | 291.3 | 464.9 | 111.8 | 1996 | 6 | 2012 | 2011 | -1 |  | 415.7 | 415.7 | 415.7 | PARKWOOD TIE 01 | 230/100 kV Transformer | 426.4 | 488.6 | 458.5 | 105.8 | 70.1 | 65.6 | 60.2
BEL1GM | PARKWOOD1 | 847 | 6PARKWOD | 948 | PARKWOOD | 1 | 847 | 6PARKWOD 230.00 | 948 | PARKWOOD 100.00 | 2 | 847-948-2 | 458 | 458 | 304.2 | 484.4 | 105.8 | 239 | 415.7 | 291.3 | 464.9 | 111.8 | 1996 | 6 | 2012 | 2011 | -1 |  | 415.7 | 415.7 | 415.7 | PARKWOOD TIE 02 | 230/100 kV Transformer | 426 | 487.9 | 458 | 105.8 | - | - | -
WATRGM | SINGLE 88 | 304044 | ROB 1 F | 304721 | BETHNE T | 1 | 304725 | CAMDEN 115.00 | 304730 | CAMDEN 230.00 | 1 | 304725-304730-1 | 200 | 200 | 168.3 | 210.9 | 105.5 | 649 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 105.5 | 84.1 | - | 85.3
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD C T 115.00 | 304284 | WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 94.1 | 209.3 | 103.1 | 45 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 103.1 | - | - | -
OCO3GM | HNDRSN-FRNKL | 304089 | HENDERSN | 304105 | FRANKLIN |  | 304182 | FALLS 230.00 | 304185 | FALLS 115.00 | 1 | 304182-304185-1 | 300 | 300 | 215 | 305.1 | 101.7 | 2392 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 101.7 | 71.7 | - | 71.3
WATRGM | SINGLE 881 | 304725 | CAMDEN | 304731 | I-DUP CA | 1 | 304716 | CAM TAP 115.00 | 304724 | CAMCTY01 115.00 | 1 | 304716-304724-1 | 108 | 108 | 47.8 | 108.2 | 101.4 | 74 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 101.4 | - | - | -
ALL5GM | WOODLAWN5 | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 473.4 | 702.3 | 101.1 | 254 | 717 | 413.6 | 625.2 | 88.9 | 2264 | -12.2 | 2012 | 2017 | 5 |  | 717 | 717 | 717 | STEELBERRY | 230 kV Line | 792.617 | 996.5466 | 792.617 | 101.1 | - | - | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARCRK W |  | 304552 | WILMEAST 230.00 | 304554 | 9THORG T 230.00 | 1 | 304552-304554-1 | 590 | 590 | 191.6 | 588.6 | 101.1 | 45 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 101.1 | - | - | -
WYLIGM | SINGLE 236 | 304145 | NEUSE | 304185 | FALLS | 1 | 304155 | CHSTNT H 115.00 | 304163 | MILBURNE 115.00 | 1 | 304155-304163-1 | 158 | 158 | 31.7 | 150.6 | 101 | 45 | - | - | - | - | - | - | 2012 | - | - |  | - | - | - | - | - | - | - | - | 101 | - | - | -
BEL1GM | SINGLE 931 | 304377 | RICHMOND | 337 | 8NEWPORT | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1785 | 1973.2 | 100.3 | 8995 | 1904.3 | 1689.7 | 1862.7 | 95.1 | 7910 | -5.2 | 2012 | 2014 | 2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 100.3 | 89.7 | 97.8 | 84.7
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 519.3 | 829.6 | 98.8 | 48 | 840 | 501.2 | 801.2 | 95.4 | 1888 | -3.4 | 2013 | 2014 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 98.8 | - | - | -
MCG1GM | SINGLE 931 | 304377 | RICHMOND | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 367.5 | 406 | 96.8 | 2174 | 436.9 | 338.7 | 380.8 | 90.4 | 2371 | -6.4 | 2014 | 2017 | 3 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE | 230 kV Line | 458.045 | 506.6376 | 458.045 | 96.8 | 87.3 | 85.8 | 77.7
OCO3GM | SINGLE 171 | 304089 | HENDERSN | 304105 | FRANKLIN | 1 | 304111 | E18-WK F 115.00 | 304185 | FALLS 115.00 | 1 | 304111-304185-1 | 170 | 170 | 79.1 | 160.3 | 96.4 | 270 | - | - | - | - | - | - | 2014 | - | - |  | - | - | - | - | - | - | - | - | 96.4 | - | - | -
WYLIGM | SINGLE 65 | 304030 | LEE 1-3F | 304877 | LEE #3 | 1 | 304030 | LEE 1-3F 115.00 | 304875 | LEE #1 13.800 | 1 | 304030-304875-1 | 111 | 111 | 81.5 | 105.5 | 95.1 | 180 | - | - | - | - | - | - | 2015 | - | - |  | - | - | - | - | - | - | - | - | 95.1 | 72.9 | 74.2 | 74.3
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARCRK W |  | 304552 | WILMEAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 146.5 | 543.8 | 93.5 | 45 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 93.5 | - | - | -
BEL1GM | ANTIOCH_XFM2 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 2 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 1 | 712-719-1 | 840 | 840 | 433.1 | 785.3 | 93.5 | 45 | 840 | 418 | 758.7 | 90.3 | 214 | -3.2 | 2016 | 2017 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 01 | 500/230 kV Transformer | 840 | 840 | 840 | 93.5 | - | 62.5 | 51.1
WYLIGM | SINGLE 510 | 304369 | FAY E | 304389 | P2-FAY E | 2 | 304369 | FAY E 69.000 | 304389 | P2-FAY E 230.00 | 1 | 304369-304389-1 | 150 | 150 | 70.1 | 139.9 | 93.3 | 45 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 93.3 | - | - | -
WYLIGM | SINGLE 509 | 304369 | FAY E | 304389 | P2-FAY E | 1 | 304369 | FAY E 69.000 | 304389 | P2-FAY E 230.00 | 2 | 304369-304389-2 | 150 | 150 | 69.7 | 139.9 | 93.3 | 45 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 93.3 | - | - | -
OCO3GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 373.3 | 451.6 | 92.9 | 1494 | 478 | 328.3 | 416.2 | 85.7 | 1478 | -7.2 | 2016 | 2019 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 92.9 | 76.6 | 76.6 | 75.6
OCO3GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 373.3 | 451.6 | 92.9 | 1538 | 478 | 328.3 | 416.2 | 85.7 | 1522 | -7.2 | 2016 | 2019 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 92.9 | 76.6 | 76.6 | 75.6
BEL1GM | SINGLE 721 | 304550 | CSTL HYN | 304564 | SCOTT T | 1 | 304544 | HOLLY RG 115.00 | 304545 | CASTLE H 115.00 | 1 | 304544-304545-1 | 179 | 179 | 123 | 158.8 | 92.9 | 1076 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 92.9 | 71.2 | - | 71.9
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 304047 | WSP BUS 115.00 | 304885 | WSP #3 13.800 | 1 | 304047-304885-1 | 95 | 95 | 88.1 | 88.1 | 92.8 | 179 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 92.8 | 90.9 | 92.3 | 92.4
RIV6GM | SINGLE 326 | 304221 | PA-RMT | 304222 | ROCKY MT | 2 | 304221 | PA-RMT 69.000 | 304222 | ROCKY MT 230.00 | 1 | 304221-304222-1 | 168 | 168 | 77.1 | 155.3 | 92.5 | 45 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 92.5 | - | - | -
BEL1GM | SINGLE 624 | 304465 | NEW BERN | 304471 | CCWDCG T | 1 | 304519 | M-TARAWA 230.00 | 304524 | JACKSONV 230.00 | 1 | 304519-304524-1 | 478 | 478 | 324 | 423.7 | 92.4 | 1715 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 92.4 | 70.2 | - | 71
WYLIGM | SINGLE 325 | 304221 | PA-RMT | 304222 | ROCKY MT | 1 | 304221 | PA-RMT 69.000 | 304222 | ROCKY MT 230.00 | 2 | 304221-304222-2 | 168 | 168 | 77.1 | 154.8 | 92.2 | 45 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 92.2 | - | - | -
CLI5GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 340.4 | 433 | 91.7 | 788 | 478 | 315.5 | 404.7 | 85.3 | 1797 | -6.4 | 2017 | 2020 | 3 |  | 458.045 | 478 | 458.045 | FISHER | 230 kV Line | 458.114 | 506.7139 | 458.114 | 91.7 | 74.7 | 79.7 | 67.8
CAT1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 426 | 726.4 | 91.2 | 54 | 796.7 | 435 | 745 | 93.5 | 3049 | 2.3 | 2017 | 2015 | -2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 91.2 | - | 52.8 | -
BEL1GM | ASHE ST B | 876 | E DURHAM | 852 | ASHE ST | &1 | 947 | OXFRD RD 100.00 | 876 | E DURHAM 100.00 | 1 | 876-947-1 | 129.9 | 129.9 | 85.4 | 119 | 91.1 | 48 | 129.9 | 77.5 | 111.7 | 86.3 | 649 | -4.8 | 2017 | 2019 | 2 |  | 118.8152 | 129.9 | 118.8152 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 91.1 | 71.4 | 82.7 | 68.1
BEL1GM | JAX-TARAWA23 | 304530 | JACKSNVL | 304535 | NORTHWDS |  | 304465 | NEW BERN 230.00 | 304471 | CCWDCG T 230.00 | 1 | 304465-304471-1 | 478 | 478 | 235.4 | 423.5 | 90.8 | 225 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 90.8 | - | - | 51.5
WYLIGM | JAX-TARAWA23 | 304530 | JACKSNVL | 304535 | NORTHWDS |  | 304504 | E9-N JAX 115.00 | 304530 | JACKSNVL 115.00 | 1 | 304504-304530-1 | 220 | 220 | 90.5 | 196.2 | 90.8 | 90 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 90.8 | - | - | -
BUC5GM | SINGLE 21 | 304009 | HARRIS1N | 304865 | HARRIS#1 | 1 | 304041 | CF 5-6 F 230.00 | 304053 | CAPE 5&6 115.00 | 1 | 304041-304053-1 | 350 | 350 | 310.2 | 317.3 | 90.7 | 135 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 90.7 | 87.2 | - | 88.9
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD C T 115.00 | 304285 | SEY JOHN 115.00 | 1 | 304239-304285-1 | 201 | 201 | 69.2 | 183.4 | 90.6 | 45 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 90.6 | - | - | -
WATRGM | SINGLE 881 | 304725 | CAMDEN | 304731 | I-DUP CA | 1 | 304723 | CAMD JCT 115.00 | 304734 | WATRE 115.00 | 1 | 304723-304734-1 | 131 | 131 | 47 | 115.4 | 90.6 | 31 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 90.6 | - | - | -
BEL1GM | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 848 | 6PL GRDN 230.00 | 850 | 8PL GRDN 500.00 | 5 | 848-850-5 | 1680 | 1680 | 978.8 | 1518.4 | 90.4 | 45 | 1680 | 885.4 | 1398.3 | 83.2 | 355 | -7.2 | 2018 | 2021 | 3 |  | 1680 | 1680 | 1680 | PLEASANT GARDEN TIE 05 | 500/230 kV Transformer | 1680 | 1680 | 1680 | 90.4 | - | 70.8 | 54.7
BEL1GM | SINGLE 582 | 304421 | LAURINBG | 304424 | LAURINBG | 2 | 304421 | LAURINBG 115.00 | 304424 | LAURINBG 230.00 | 1 | 304421-304424-1 | 200 | 200 | 99.6 | 180.4 | 90.2 | 45 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | 90.2 | - | - | -
BEL1GM | SINGLE 40 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304550 | CSTL HYN 230.00 | 304564 | SCOTT T 230.00 | 1 | 304550-304564-1 | 478 | 478 | 325.5 | 426.4 | 90.2 | 969 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | 90.2 | - | - | 69.2
BEL1GM | SINGLE 581 | 304421 | LAURINBG | 304424 | LAURINBG | 1 | 304421 | LAURINBG 115.00 | 304424 | LAURINBG 230.00 | 2 | 304421-304424-2 | 200 | 200 | 99 | 180.2 | 90.1 | 45 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | 90.1 | - | - | -
BEL1GM | ENO2 | 844 | 6ENO | 2620 | ENO 2 | 2 | 876 | E DURHAM 100.00 | 947 | OXFRD RD 100.00 | 1 | 876-947-1 | 118.8 | 118.8 | 85.4 | 101.6 | 85.2 | 370 | 129.9 | 77.5 | 111.7 | 86.3 | 649 | 1.1 | 2021 | 2014 | -7 |  | 118.8152 | 129.9 | 118.8152 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 91.1 | 71.4 | 82.7 | 68.1
BEL1GM | PARKWOOD2 | 847 | 6PARKWOD | 948 | PARKWOOD | 2 | 876 | E DURHAM 100.00 | 975 | WEAVERT 100.00 | 1 | 876-975-1 | 132.1 | 132.1 | 88.5 | 113.8 | 85.8 | 222 | 132.1 | 85 | 110.3 | 84 | 907 | -1.8 | 2020 | 2020 | 0 |  | 132.1516 | 163.5008 | 132.1516 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5 | 132.1516 | 85.8 | - | 74.7 | 55.8
BEL1GM | GEER WHITE | 876 | E DURHAM | 875 | DURHAM | &1 | 975 | WEAVERT 100.00 | 876 | E DURHAM 100.00 | 1 | 876-975-1 | 163.5 | 163.5 | 88.1 | 129.4 | 79 | 45 | 132.1 | 85 | 110.3 | 84 | 907 | 5 | 2024 | 2031 | 7 |  | 132.1516 | 163.5008 | 132.1516 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5 | 132.1516 | 85.8 | - | 74.7 | 55.8
BEL1GM | PARKWOOD2 | 847 | 6PARKWOD | 948 | PARKWOOD | 2 | 852 | ASHE ST 100.00 | 975 | WEAVERT 100.00 | 1 | 852-975-1 | 132 | 132 | 73.3 | 98.6 | 74.6 | 90 | 108.2 | 67.8 | 93 | 86.8 | 1320 | 12.2 | 2027 | 2029 | 2 |  | 108.25 | 118.642 | 108.25 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 74.6 | - | 63.2 | -
2 | % Yearly Load Growth |  | 2012 Summer Screening (2007 NCPWG Study Base Case) | [6 empty] | Directory: | P:\Bdm\NC PWG\2007 Study\Thermal Screening\Base12s\
2012 | Study Year |  | Thermal Screening
2012 | Implementation Year
2012 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 28 | > 5% worse | [10 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 9 | Not in original screening | [10 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 37 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings |  |  | GenMaint (Base)
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | 2011 Summer Screening (2006 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2012 Summer Screening (2007 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Base | XXs | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | GmLc | Gm | GmGc | GmWh
ALL5GM | - | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 56.7 | 96.9 | 180 | 58.5 | - | 45.9 | 78.5 | 172 | -18.4 | 2014 | 2024 | 10 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 107.9 | 96.9 | 129 | 95.2
BEL1GM | - | - | - | - | - | - | 304047 | WSP BUS | 304885 | WSP #3 | 1 | 304047-304885-1 | 95 | 95 | - | 86.3 | 90.9 | 180 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 92.8 | 90.9 | 92.3 | 92.4
BEL1GM | - | - | - | - | - | - | 876 | E DURHAM | 947 | OXFRD RD | 1 | 876-947-1 | 118.8 | 118.8 | - | 84.9 | 71.4 | 2 | 118.8 | - | 78 | 65.7 | 88 | -5.7 | 2030 | 2033 | 3 |  | 118.8152 | 129.9 | 118.8152 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 91.1 | 71.4 | 82.7 | 68.1
2 | % Yearly Load Growth |  | 2012 Summer Screening (2007 NCPWG Study Base Case) | [6 empty] | Directory: | P:\Bdm\NC PWG\2007 Study\Thermal Screening\Base12s\
2012 | Study Year |  | Thermal Screening
2012 | Implementation Year
2012 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 25 | > 5% worse | [10 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 9 | Not in original screening | [10 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 34 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings |  |  | GenMaint+GenCont (Base)
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | 2011 Summer Screening (2006 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2012 Summer Screening (2007 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Base | XXs | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | GmLc | Gm | GmGc | GmWh
ALL5GM | CAT1 | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 58.5 | 58.5 | - | 75.4 | 129 | 952 | 58.5 | - | 65.9 | 112.6 | 910 | -16.4 | 2012 | 2011 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 107.9 | 96.9 | 129 | 95.2
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1862.5 | 97.8 | 952 | 1904.3 | - | 1804.3 | 94.8 | 910 | -3 | 2014 | 2014 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 100.3 | 89.7 | 97.8 | 84.7
BEL1GM | BEL2 | - | - | - | - | - | 304047 | WSP BUS | 304885 | WSP #3 | 1 | 304047-304885-1 | 95 | 95 | - | 87.6 | 92.3 | 952 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | 92.8 | 90.9 | 92.3 | 92.4
BEL1GM | BEL2 | - | - | - | - | - | 876 | E DURHAM | 947 | OXFRD RD | 1 | 876-947-1 | 118.8 | 118.8 | - | 98.2 | 82.7 | 476 | 118.8 | - | 94.3 | 79.4 | 455 | -3.3 | 2022 | 2023 | 1 |  | 118.8152 | 129.9 | 118.8152 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 91.1 | 71.4 | 82.7 | 68.1
BEL1GM | BEL2 | - | - | - | - | - | 875 | DURHAM | 947 | OXFRD RD | 1 | 875-947-1 | 108.2 | 108.2 | - | 71.9 | 66.5 | 311 | 108.2 | - | 68 | 62.8 | 151 | -3.7 | 2033 | 2035 | 2 |  | 108.25 | 118.642 | 108.25 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | - | - | 66.5 | 53.9
BEL1GM | BEL2 | - | - | - | - | - | 876 | E DURHAM | 975 | WEAVERT | 1 | 876-975-1 | 132.1 | 132.1 | - | 98.7 | 74.7 | 476 | 132.1 | - | 98.5 | 74.5 | 455 | -0.2 | 2027 | 2026 | -1 |  | 132.1516 | 163.5008 | 132.1516 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5 | 132.1516 | 85.8 | - | 74.7 | 55.8
BEL1GM | BEL2 | - | - | - | - | - | 852 | ASHE ST | 975 | WEAVERT | 1 | 852-975-1 | 132 | 132 | - | 83.4 | 63.2 | 476 | 108.2 | - | 81.4 | 75.2 | 455 | 12 | 2036 | 2036 | 0 |  | 108.25 | 118.642 | 108.25 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 74.6 | - | 63.2 | -
2 | % Yearly Load Growth |  | 2012 Summer Screening (2007 NCPWG Study Base Case) | [6 empty] | Directory: | P:\Bdm\NC PWG\2007 Study\Thermal Screening\Base12s\
2012 | Study Year |  | Thermal Screening
2012 | Implementation Year
2012 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 15 | > 5% worse | [10 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 4 | Not in original screening | [10 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 19 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings |  |  | GenMaint+Whitewater (Base)
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | 2011 Summer Screening (2006 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2012 Summer Screening (2007 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Base | XXs | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | GmLc | Gm | GmGc | GmWh
ALL5GM | BADX | - | - | - | - | - | 375 | GT FALL1 | 416 | WATEREE | 1 | 375-416-1 | 71.2 | 71.2 | - | 67.8 | 95.2 | 44 | 71.2 | - | 57.3 | 80.4 | 42 | -14.8 | 2015 | 2023 | 8 |  | 58.5 | 71.2 | 58.5 | WATEREE | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 107.9 | 96.9 | 129 | 95.2
BEL1GM | BADX | - | - | - | - | - | 304047 | WSP BUS | 304885 | WSP #3 | 1 | 304047-304885-1 | 95 | 95 | - | 87.8 | 92.4 | 44 | - | - | - | - | - | - | 2016 | - | - |  | - | - | - | - | - | - | - | - | 92.8 | 90.9 | 92.3 | 92.4
CLI3GM | BADX | - | - | - | - | - | 304725 | CAMDEN | 304731 | I-DUP CA | 1 | 304725-304731-1 | 108 | 108 | - | 97.5 | 90.3 | 44 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | 134.4 | 88.9 | - | 90.3
BEL1GM | BADX | - | - | - | - | - | 876 | E DURHAM | 975 | WEAVERT | 1 | 876-975-1 | 163.5 | 163.5 | - | 91.2 | 55.8 | 22 | 163.5 | - | 89 | 54.4 | 21 | -1.4 | 2042 | 2042 | 0 |  | 132.1516 | 163.5008 | 132.1516 | ASHE ST. B | 100 kV Line | 132.1516 | 163.5 | 132.1516 | 85.8 | - | 74.7 | 55.8
BEL1GM | BADX | - | - | - | - | - | 876 | E DURHAM | 947 | OXFRD RD | 1 | 876-947-1 | 129.9 | 129.9 | - | 88.4 | 68.1 | 22 | 129.9 | - | 82 | 63.1 | 21 | -5 | 2032 | 2035 | 3 |  | 118.8152 | 129.9 | 118.8152 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 91.1 | 71.4 | 82.7 | 68.1
BEL1GM | BADX | - | - | - | - | - | 875 | DURHAM | 947 | OXFRD RD | 1 | 875-947-1 | 118.6 | 118.6 | - | 64 | 53.9 | 1 | - | - | - | - | - | - | 2044 | - | - |  | 108.25 | 118.642 | 108.25 | GEER W | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | - | - | 66.5 | 53.9

## 2013 Base
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 32 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 23 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 55 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 45.5 | 155 | 128.7 | 48 | 119 | 45.8 | 158.3 | 132.2 | 45 | 3.5 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 128.7 | - | - | - | 139.8 | - | - | -
BEL1GM | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 671 | 986 | 120 | 10818 | 822 | 655.6 | 1641.5 | 199.7 | 11861 | 79.7 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120 | 79.7 | 82.5 | 81.8 | 134.1 | 94 | 95.9 | 95.6
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 90.2 | 120.4 | 118.4 | 910 | - | - | - | - | - | - | 2013 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118.4 | - | - | - | 102.8 | - | - | -
OCO3GM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | 113.1 | 90.4 | 111.3 | 95.6 | 431 | -16.6 | 2013 | 2015 | 2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 19 | 16.5 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 116.5 | 231.1 | 112.2 | 144 | 201 | 118.4 | 233.2 | 114.8 | 135 | 2.6 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.2 | - | - | 56.4 | 118.9 | - | - | 59.7
OCO3GM | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 109.6 | 187.4 | 112.1 | 1070 | 170 | 79.1 | 160.3 | 96.4 | 270 | -15.7 | 2013 | 2015 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.1 | - | - | 64.8 | 114.1 | - | - | 67.3
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 243 | 644.5 | 108.7 | 48 | 590 | 239.3 | 638.9 | 109.2 | 45 | 0.5 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 108.7 | - | - | - | 109.8 | - | - | 52.6
OCO3GM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | 113.1 | 84.9 | 99.2 | 86.1 | 340 | -21.8 | 2013 | 2022 | 9 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 24.9 | 21.1 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 108.3 | 65 | 117.4 | 108.4 | 45 | 2.3 | 2013 | 2012 | -1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 18.9 | 17.5 | 106.1 | - | 63.5 | 56.7 | 102.2 | - | 61.1 | 54.7
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 108.3 | 65 | 117.4 | 108.4 | 45 | 2.3 | 2013 | 2012 | -1 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 18.9 | 17.5 | 106.1 | - | - | - | 102.2 | - | - | -
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 91.6 | 123 | 104.2 | 320 | - | - | - | - | - | - | 2013 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.2 | - | - | - | 90.4 | - | - | -
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 96 | 50 | 38.8 | 38.8 | 77.6 | 90 | -25.5 | 2013 | 2028 | 15 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
BEL1GM | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 135 | DANIEL 100.00 | 220 | 1BLREC25 100.00 | 1 | 135-220-1 | 86.6 | 86.6 | 51.8 | 88.9 | 101.8 | 48 | - | - | - | - | - | - | 2013 | - | - |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER BL | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | 101.8 | - | 59.1 | - | 128.4 | - | 66.5 | 50.9
OCO3GM | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 38.6 | 77.7 | 101 | 7 | 71.2 | 60.3 | 87.8 | 114.9 | 680 | 13.9 | 2013 | 2012 | -1 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 3.3 | 2 | 101 | - | - | - | - | - | - | -
OCO3GM | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | - | - | - | - | - | - | 2013 | - | - |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 100.9 | - | 67.6 | 58.8 | 105.7 | 73.5 | 70.9 | 61.7
WATRGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 92.4 | 204.8 | 100.5 | 48 | 201 | 94.1 | 209.3 | 103.1 | 45 | 2.6 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.5 | - | - | - | 107.2 | - | - | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 191.8 | 591.2 | 100.1 | 48 | 590 | 191.6 | 588.6 | 101.1 | 45 | 1 | 2013 | 2012 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.1 | - | - | - | 101.3 | - | - | -
WYLIGM | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 23.1 | 149.1 | 99.3 | 48 | 158 | 31.7 | 150.6 | 101 | 45 | 1.7 | 2014 | 2012 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.3 | - | - | - | 99.8 | - | - | -
RIV7GM | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | 796.7 | 394.6 | 688.5 | 86.2 | 77 | -7.3 | 2018 | 2022 | 4 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 147.7 | 16.7 | 93.5 | - | - | - | 92.9 | - | - | -
OCO3GM | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 110 | 174.9 | 93.4 | 96 | 201 | 114.5 | 161.4 | 84.4 | 90 | -9 | 2018 | 2023 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.4 | - | - | 55.2 | 96 | - | - | 58.5
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 146.7 | 546.3 | 92.6 | 48 | 590 | 146.5 | 543.8 | 93.5 | 45 | 0.9 | 2018 | 2017 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.6 | - | - | - | 93.8 | - | - | -
WYLIGM | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 92.6 | 201.2 | 91.3 | 96 | - | - | - | - | - | - | 2019 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | - | - | - | 94.9 | - | - | -
CLI5GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 335.9 | 428.7 | 90.8 | 665 | 478 | 340.4 | 433 | 91.7 | 788 | 0.9 | 2020 | 2018 | -2 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 33.4 | 7.9 | 90.8 | 73.6 | 78.6 | 66.9 | 87.5 | 75 | 75.6 | 64.1
CLI5GM | SINGLE 939 | 304800 | ASHEVILL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100.00 | 190 | PISGAH 100.00 | 1 | 164-190-1 | 108.2 | 108.2 | 43.3 | 94.2 | 90.2 | 96 | - | - | - | - | - | - | 2020 | - | - |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 46.9 | 91.4 | 79.5 | 2.8 | 10.7 | 90.2 | - | - | - | 85.8 | - | - | -
CLI5GM | SINGLE 939 | 304800 | ASHEVILL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100.00 | 190 | PISGAH 100.00 | 2 | 164-190-2 | 108.2 | 108.2 | 43.3 | 94.2 | 90.2 | 96 | - | - | - | - | - | - | 2020 | - | - |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 46.9 | 91.4 | 79.5 | 2.8 | 10.7 | 90.2 | - | - | - | 85.8 | - | - | -
WYLIGM | SINGLE 627 | 304530 | JACKSV11 | 305068 | E9-JAX N | 1 | 304530 | JACKSV115 TT115.00 | 304535 | NORTHWOODS 115.00 | 1 | 304530-304535-1 | 221 | 221 | 109 | 196.6 | 90 | 240 | 221 | 106.7 | 191 | 89.4 | 180 | -0.6 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | - | - | - | 94 | - | - | 51.7
MCG1GM | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | 436.9 | 367.5 | 406 | 96.8 | 2174 | 7 | 2020 | 2015 | -5 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | -10.7 | 5.1 | 89.8 | 82 | 80.8 | 72.8 | 90.9 | 83.1 | 80.6 | 72.1
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 365.4 | 440 | 89.7 | 1473 | 478 | 373.3 | 451.6 | 92.9 | 1494 | 3.2 | 2020 | 2017 | -3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 10 | 2.1 | 89.7 | 74.3 | 74.7 | 73.4 | 91.5 | 76.7 | 76.3 | 74.8
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 365.4 | 440 | 89.7 | 1520 | 478 | 373.3 | 451.6 | 92.9 | 1538 | 3.2 | 2020 | 2017 | -3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 10 | 2.1 | 89.7 | 74.3 | 74.7 | 73.4 | 91.5 | 76.7 | 76.3 | 74.8
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
99ISGM | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.4 | 104.9 | 96 | 50 | - | 39.6 | 79.2 | 180 | -25.7 | 2013 | 2027 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
OCO3GM | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.8 | 96.2 | 96 | 102.7 | - | 83.4 | 81.2 | 176 | -15 | 2016 | 2026 | 10 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 14.6 | 14.2 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
OCO3GM | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.5 | 100.8 | 48 | 102.7 | - | 88.5 | 86.2 | 90 | -14.6 | 2013 | 2022 | 9 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 14.6 | 14.2 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
TURNGM | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.1 | 90.3 | 48 | 22.2 | - | 18.5 | 83.2 | 90 | -7.1 | 2020 | 2024 | 4 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 16 | 71.8 | 4.1 | 18.5 | - | 90.3 | 89.7 | 74.2 | 90.7 | 90.8 | 90.7 | 74.9
BEL1GM | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.5 | 48 | 120 | - | 107.8 | 89.8 | 90 | -6.7 | 2016 | 2019 | 3 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 5 | - | 96.5 | 96.3 | 89.3 | 96.3 | 96.4 | 96.3 | 89.1
BUG1GM | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.5 | 97.6 | 46 | - | - | - | - | - | - | 2015 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 97.6 | 98.9 | 90 | 97.7 | 97.5 | 89.3 | 81.2
RIV7GM | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 97.8 | 95.2 | 47 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | 100.3 | 87.3 | 94.4 | 98.3 | 98.7 | 78.7
99ISGM | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.3 | 93.6 | 48 | - | - | - | - | - | - | 2018 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | 93.6 | 93.8 | 84.4 | 93.6 | 93.6 | 93.6 | 84.4
RIV7GM | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 95.5 | 93 | 43 | - | - | - | - | - | - | 2018 | - | - |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 93 | 97.8 | 85.3 | 92.3 | 96.1 | 96.4 | 76.6
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 7 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 13 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
OCO3GM | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.8 | 96.2 | 1384 | 102.7 | - | 83.4 | 81.2 | 952 | -15 | 2016 | 2026 | 10 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 14.6 | 14.2 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
OCO1GM | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.4 | 100.7 | 692 | 102.7 | - | 88.5 | 86.1 | 476 | -14.6 | 2013 | 2022 | 9 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.5 | 14.5 | 14.2 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
ALL5GM | CAT1 | - | - | - | - | - | 437 | UNEMC 12 | 635 | OAKBORO | 1 | 437-635-1 | 174.2 | 174.2 | - | 157.3 | 90.3 | 692 | 173.3 | - | 133.4 | 77 | 476 | -13.3 | 2020 | 2029 | 9 |  | 174.2 | 204.7 | 174.2 | ROCKY RIVER WH | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 173.3 | - | 122.2 | 70.5 | 35.1 | 19.8 | - | 84.6 | 90.3 | 73.5 | 88.8 | 84.3 | 87.4 | 71.4
OCO1GM | OCO2 | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 116.7 | 92.3 | 692 | 126.4 | - | 104.1 | 82.4 | 476 | -9.9 | 2019 | 2025 | 6 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 101.1 | 80 | 15.6 | 12.3 | - | 88.4 | 92.3 | 82.8 | 97.6 | 90.3 | 89.4 | 80.6
BAD1GM | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 692 | 120.4 | - | 107.9 | 89.7 | 476 | -6.6 | 2016 | 2019 | 3 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.1 | 91.5 | 5.8 | 4.8 | - | 96.5 | 96.3 | 89.3 | 96.3 | 96.4 | 96.3 | 89.1
CAT1GM | CAT2 | - | - | - | - | - | 600 | HARRISBG | 601 | HCKRY GR | 1 | 600-601-1 | 125.6 | 125.6 | - | 114.9 | 91.5 | 692 | 125.6 | - | 108.1 | 86.1 | 476 | -5.4 | 2019 | 2022 | 3 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 125.6 | - | 97.5 | 77.7 | 17.4 | 13.8 | - | 88.1 | 91.5 | 81.7 | 90.1 | 89.8 | 87.5 | 78.9
RIV7GM | RIV4 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 103 | 100.3 | 692 | - | - | - | - | - | - | 2013 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | 100.3 | 87.3 | 94.4 | 98.3 | 98.7 | 78.7
BUG1GM | MCG1 | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 85.7 | 98.9 | 689 | - | - | - | - | - | - | 2014 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | 86.6 | - | 48.3 | 55.7 | 37.4 | 43.2 | - | 97.6 | 98.9 | 90 | 97.7 | 97.5 | 89.3 | 81.2
RIV7GM | RIV4 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 100.4 | 97.8 | 692 | - | - | - | - | - | - | 2015 | - | - |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 93 | 97.8 | 85.3 | 92.3 | 96.1 | 96.4 | 76.6
CAT1GM | CAT2 | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 522.4 | 93.8 | 692 | - | - | - | - | - | - | 2018 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | 93.6 | 93.8 | 84.4 | 93.6 | 93.6 | 93.6 | 84.4
RIV7GM | RIV4 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95.9 | 93.4 | 692 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.2 | 93.4 | 81.8 | 88.7 | 92.2 | 92.5 | 73.1
BUG1GM | MCG1 | - | - | - | - | - | 737 | DAN RIV | 10810 | WENTW WH | 1 | 737-10810-1 | 86.6 | 86.6 | - | 78.5 | 90.6 | 686 | - | - | - | - | - | - | 2020 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 89.3 | 90.6 | 82.4 | 89.4 | 89.1 | 80.9 | 73.5
BUG1GM | MCG1 | - | - | - | - | - | 2089 | WAYNICKR | 10810 | WENTW WH | 1 | 2089-10810-1 | 86.6 | 86.6 | - | 78.4 | 90.6 | 1372 | - | - | - | - | - | - | 2020 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 89.2 | 90.6 | 82.3 | 89.3 | 89.1 | 80.8 | 73.4
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 3 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GM | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.4 | 104.8 | 52 | 50 | - | 39.6 | 79.1 | 44 | -25.7 | 2013 | 2027 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
OCO1GM | BADX | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 113.1 | 113.1 | - | 101.8 | 90 | 26 | 113.1 | - | 86.7 | 76.6 | 22 | -13.4 | 2020 | 2029 | 9 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 87.1 | 77 | 14.7 | 13 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
BUG1GM | BADX | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 94.7 | 94.7 | - | 85.2 | 90 | 26 | - | - | - | - | - | - | 2020 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | 94.7 | - | 47.9 | 50.5 | 37.3 | 39.5 | - | 97.6 | 98.9 | 90 | 97.7 | 97.5 | 89.3 | 81.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 135 | DANIEL 100.00 | 220 | 1BLREC25 100.00 | 1 | 135-220-1 | 86.6 | 86.6 | 58.2 | 113.5 | 128.4 | 16 | 86.6 | 57.4 | 65.1 | 74.9 | 2 | -53.5 | 2013 | 2031 | 18 |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER BL | 100 kV Line | 86.6 | 106 | 86.6 | 86.6 | 59.6 | 67.5 | 77.1 | 46 | 51.3 | 101.8 | - | 59.1 | - | 128.4 | - | 66.5 | 50.9
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 897 | GLEN RVN 100.00 | 1 | 857-897-1 | 207.8 | 207.8 | 149.2 | 233.3 | 109.9 | 104 | 207.8 | 130.9 | 159.6 | 77.6 | 12 | -32.3 | 2013 | 2028 | 15 |  | 207.8 | 207.8 | 207.8 | ALAMANCE BL | 100 kV Line | 282.4892 | 327.0016 | 282.4892 | 207.8 | 122.6 | 153 | 73.4 | 80.3 | 36.5 | - | - | 67.7 | 65.4 | 109.9 | 72.8 | 70.5 | 68.2
STUDYRCH1VRS | OAKLAWNW | 631 | N CHARLT | 552 | BANCROFT | 1 | 611 | LAKEWOOD 100.00 | 10143 | BANCRO B 100.00 | 1 | 611-10143-1 | 207.8 | 207.8 | 149.9 | 219.1 | 102.8 | 335 | 199.2 | 122.9 | 148.2 | 75.4 | 46 | -27.4 | 2013 | 2033 | 20 |  | 199.2 | 207.8 | 199.2 | OAKLAWN BL | 100 kV Line | 199.18 | 220.3104 | 199.18 | - | - | - | - | - | - | - | 73.9 | 76.7 | 69.7 | 102.8 | 79.2 | 76.2 | 69.4
STUDYVCS1VRS | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 26 | 50 | 38.8 | 38.8 | 77.6 | 36 | -25.5 | 2013 | 2028 | 15 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
STUDYASH1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737 | DAN RIV 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 737-10779-1 | 139.4 | 139.4 | 92 | 134 | 92.5 | 30 | 139.4 | 55.3 | 99.9 | 70.3 | 2 | -22.2 | 2018 | 2035 | 17 |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | 139.4 | 57.1 | 101.2 | 71 | 32.8 | 21.5 | - | 76.2 | 78.1 | 70 | 92.5 | 76 | 71.9 | 64.5
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 182 | N GRNVLE 100.00 | 10135 | DANIELWH 100.00 | 1 | 182-10135-1 | 118.8 | 118.8 | 58 | 110.8 | 91.5 | 10 | 129.9 | 19 | 95.5 | 72.4 | 1 | -19.1 | 2019 | 2027 | 8 |  | 118.8 | 129.9 | 118.8 | DAVIDSON RIVER WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 129.9 | 23.1 | 95.1 | 71.6 | 15.7 | 19.9 | 72.3 | - | - | - | 91.5 | - | - | -
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 100.8 | 124.6 | 107.6 | 117 | 113.1 | 87.9 | 102.7 | 89.3 | 98 | -18.3 | 2013 | 2020 | 7 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 83.3 | 97.3 | 84.3 | 27.3 | 23.3 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
STUDYVCS1VRS | MULLW | 465 | HICKORY | 483 | NEWTON T | 1 | 465 | HICKORY 100.00 | 10423 | ZIONCTAP 100.00 | 1 | 465-10423-1 | 141.2 | 141.2 | 71.7 | 147.6 | 103.1 | 13 | 104 | 79.2 | 91.1 | 87.1 | 130 | -16 | 2013 | 2040 | 27 |  | 103.9 | 141.2 | 128 | MULL BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 104 | 68.1 | 81 | 76.9 | 66.6 | 26.2 | - | - | 58.8 | 50.3 | 103.1 | 72.3 | 58.7 | -
STUDYBRN1VRS | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 108.3 | 190.1 | 114.1 | 296 | 170 | 77.4 | 162.6 | 98.1 | 75 | -16 | 2013 | 2014 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.1 | - | - | 64.8 | 114.1 | - | - | 67.3
STUDYASH1VRS | NEWTON1 | 3482 | NEWTON2 | 2013 | 1NEWTON | 1 | 2013 | 1NEWTON 44.000 | 3482 | NEWTON2 100.00 | 2 | 2013-3482-2 | 44.9 | 44.9 | 24.1 | 51 | 113.5 | 1 | 44.9 | 21.9 | 44.2 | 98.5 | 12 | -15 | 2013 | 2013 | 0 |  | 42.3 | 44.9 | 44.9 | NEWTON TIE 02 | 100/44 kV Transformer | 42.3 | 44.9 | 44.9 | 44.9 | 21.2 | 43.3 | 96.5 | 7.7 | 17 | - | - | - | - | 113.5 | - | - | -
STUDYBTH1VRS | NEWTON2 | 3482 | NEWTON2 | 2013 | 1NEWTON | 2 | 2013 | 1NEWTON 44.000 | 3482 | NEWTON2 100.00 | 1 | 2013-3482-1 | 45.7 | 45.7 | 26 | 50.9 | 111.3 | 13 | 45.7 | 23.6 | 44.3 | 97 | 12 | -14.3 | 2013 | 2014 | 1 |  | 41.2 | 45.7 | 44.5 | NEWTON TIE 01 | 100/44 kV Transformer | 41.2 | 45.7 | 44.5 | 45.7 | 22.8 | 43.4 | 94.9 | 7.5 | 16.4 | - | - | 56.3 | 54.6 | 111.3 | - | 56.2 | 54.5
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 106.1 | 130.1 | 111.8 | 117 | 113.1 | 93.4 | 114.8 | 98.9 | 120 | -12.9 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 88.5 | 108.6 | 93.4 | 21.5 | 18.4 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
STUDYROX4VRS | NGBORO2 | 846 | 6N GRNSB | 2643 | N GRNB 2 | 2 | 846 | 6N GRNSB 230.00 | 2644 | N GRNB 3 1.0000 | 3 | 846-2644-3 | 500 | 500 | 367 | 490.1 | 98 | 390 | 550.5 | 358.3 | 486.2 | 88.3 | 24 | -9.7 | 2015 | 2014 | -1 |  | 500 | 500 | 500 | N GREENSBORO TIE 03 | 230/100/44 kV Transformer | 522.7 | 546.4 | 546.4 | 597.3 | 347.3 | 472.4 | 79.1 | 17.7 | 18.9 | - | 72.8 | 75.8 | 72.5 | 98 | 73 | 75.2 | 70.7
STUDYROX4VRS | NGBORO2 | 846 | 6N GRNSB | 2643 | N GRNB 2 | 2 | 943 | N GREENS 100.00 | 2644 | N GRNB 3 1.0000 | 3 | 943-2644-3 | 500 | 500 | 367 | 490.1 | 98 | 390 | 550.5 | 358.3 | 486.2 | 88.3 | 24 | -9.7 | 2015 | 2014 | -1 |  | 500 | 500 | 500 | N GREENSBORO TIE 03 | 230/100/44 kV Transformer | 522.7 | 546.4 | 546.4 | 597.3 | 347.3 | 472.5 | 79.1 | 17.6 | 18.9 | - | 73.2 | 76.3 | 73 | 98 | 73.4 | 75.6 | 71.2
STUDYROX4VRS | TABLEROCK3 | 3497 | TABL RO2 | 2055 | 1TABL RK | 3 | 2055 | 1TABL RK 44.000 | 3497 | TABL RO2 100.00 | 1 | 2055-3497-1 | 25.9 | 25.9 | 14.7 | 23.3 | 90 | 26 | 25.4 | 13.1 | 20.5 | 80.8 | 24 | -9.2 | 2020 | 2027 | 7 |  | 25.4 | 25.9 | 25.9 | TABLE ROCK TIE 01 | 100/44 kV Transformer | 25.4 | 25.9 | 25.9 | 25.9 | 12.4 | 19.3 | 74.7 | 4 | 15.3 | - | - | 56.9 | 56.3 | 90 | - | 56.4 | 56
STUDYBRN1VRS | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 115.8 | 179.2 | 96 | 28 | 201 | 120.5 | 165.7 | 87 | 41 | -9 | 2016 | 2021 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.4 | - | - | 55.2 | 96 | - | - | 58.5
STUDYRCH1VRS | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 439.2 | 757.3 | 92.9 | 39 | 796.7 | 393.4 | 686.8 | 85.6 | 24 | -7.3 | 2018 | 2022 | 4 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 351.1 | 614.5 | 75.7 | 142.8 | 17.2 | 93.5 | - | - | - | 92.9 | - | - | -
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1411 | 1BRDRV 4 44.000 | 1479 | 1INMAN 44.000 | 1 | 1411-1479-1 | 22.2 | 22.2 | 20.7 | 20.7 | 90.7 | 39 | 22.2 | 19.1 | 19.1 | 83.6 | 36 | -7.1 | 2020 | 2024 | 4 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | 16.5 | 16.5 | 72.9 | 4.2 | 17.8 | - | 90.3 | 89.7 | 74.2 | 90.7 | 90.8 | 90.7 | 74.9
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 875 | DURHAM 100.00 | 941 | DACIANTB 100.00 | 1 | 875-941-1 | 120 | 120 | 119.2 | 119.2 | 96.3 | 39 | 120 | 109.3 | 109.3 | 89.7 | 49 | -6.6 | 2016 | 2019 | 3 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | 112.4 | 112.4 | 90.8 | 6.8 | 5.5 | - | 96.5 | 96.3 | 89.3 | 96.3 | 96.4 | 96.3 | 89.1
STUDYHAR1VRS | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 735 | 735 | 439.2 | 685.1 | 91.2 | 26 | 796.7 | 393.4 | 686.8 | 85.6 | 24 | -5.6 | 2019 | 2017 | -2 |  | 735 | 796.7 | 735 | PINOCA BL | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 351.1 | 614.5 | 75.7 | 70.6 | 15.5 | - | - | 60.1 | 53.4 | 91.2 | - | 60.9 | 53.1
STUDYVCS1VRS | TABLEROCK1 | 3497 | TABL RO2 | 2055 | 1TABL RK | 1 | 2055 | 1TABL RK 44.000 | 3497 | TABL RO2 100.00 | 3 | 2055-3497-3 | 25.2 | 25.2 | 16.1 | 24.3 | 96.5 | 26 | 23.6 | 14.4 | 21.5 | 91 | 24 | -5.5 | 2016 | 2023 | 7 |  | 23.6 | 25.9 | 25.2 | TABLE ROCK TIE 03 | 100/44 kV Transformer | 23.6 | 25.9 | 25.2 | 25.2 | 13.6 | 20.2 | 80.3 | 4.1 | 16.2 | - | - | - | - | 96.5 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 220 | 1BLREC25 100.00 | 10177 | MARIETBL 100.00 | 1 | 220-10177-1 | 86.6 | 86.6 | 37.3 | 92 | 105.8 | 13 | - | - | - | - | - | - | 2013 | - | - |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER BL | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | 78.9 | - | - | - | 105.8 | - | - | -
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 128.4 | 212.3 | 105.7 | 63 | - | - | - | - | - | - | 2013 | - | - |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 100.9 | - | 67.6 | 58.8 | 105.7 | 73.5 | 70.9 | 61.7
STUDYROX4VRS | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 76.5 | 104.6 | 102.8 | 232 | - | - | - | - | - | - | 2013 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118.4 | - | - | - | 102.8 | - | - | -
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 737 | DAN RIV 100.00 | 810 | WENTWRTH 100.00 | 1 | 737-810-1 | 86.6 | 86.6 | 79.1 | 87.8 | 97.7 | 183 | - | - | - | - | - | - | 2015 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 97.6 | 98.9 | 90 | 97.7 | 97.5 | 89.3 | 81.2
STUDYRCH1VRS | LAKEWOODBK2 | 539 | 6LAKEWOD | 2628 | LAKEW 2 | 2 | 539 | 6LAKEWOD 230.00 | 2695 | 1LAKEWOOD 1.0000 | 1 | 539-2695-1 | 415.7 | 415.7 | 302.3 | 404.5 | 97.3 | 571 | - | - | - | - | - | - | 2015 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71 | 72.9 | 70.2 | 97.3 | 73.7 | 73.8 | 69.7
STUDYRCH1VRS | LAKEWOODBK2 | 539 | 6LAKEWOD | 2628 | LAKEW 2 | 2 | 611 | LAKEWOOD 100.00 | 2695 | 1LAKEWOOD 1.0000 | 1 | 611-2695-1 | 415.7 | 415.7 | 302.3 | 404.5 | 97.3 | 571 | - | - | - | - | - | - | 2015 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4 | 73.3 | 70.7 | 97.3 | 74.2 | 74.2 | 70.1
STUDYBRN1VRS | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 96.7 | 209.2 | 94.9 | 30 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | - | - | - | 94.9 | - | - | -
STUDYROX4VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 611 | LAKEWOOD 100.00 | 10680 | BFORDRET 100.00 | 1 | 611-10680-1 | 110.8 | 110.8 | 90.3 | 107.2 | 94.4 | 193 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | 100.3 | 87.3 | 94.4 | 98.3 | 98.7 | 78.7
STUDYBRN1VRS | SINGLE 26 | 304020 | BRUN 2 N | 304615 | BARN CRK | 1 | 304020 | BRUN 2 N 230.00 | 305005 | E1-SOUTHPORT230.00 | 1 | 304020-305005-1 | 478 | 478 | 228.4 | 451.2 | 94.2 | 14 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 72.5 | - | - | - | 94.2 | - | - | -
STUDYRCH1VRS | CPL8 | 304391 | CUMB500 | 304377 | RICH500 | 1 | 304378 | RICH230 TT 230.00 | 304978 | RICH CC2 18.000 | 1 | 304378-304978-1 | 795 | 795 | 721.9 | 746.4 | 93.9 | 328 | - | - | - | - | - | - | 2017 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 88.4 | 82.8 | 84.5 | 84.1 | 93.9 | 87.9 | 89 | 88
STUDYVCS1VRS | BASE CASE | 0 |  | 0 |  |  | 265 | 6RIVERVW 230.00 | 10316 | 6BRECBL2 230.00 | 2 | 265-10316-2 | 556.9 | 556.9 | 526.5 | 526.5 | 93.6 | 39 | - | - | - | - | - | - | 2018 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | 93.6 | 93.8 | 84.4 | 93.6 | 93.6 | 93.6 | 84.4
STUDYASH1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 821 | DANVALYT 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 821-10779-1 | 139.4 | 139.4 | 91.2 | 132.3 | 92.5 | 30 | - | - | - | - | - | - | 2018 | - | - |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 76.2 | 78.1 | 70 | 92.5 | 76 | 71.9 | 64.5
STUDYROX4VRS | VANWYCK1 | 415 | VAN WYCK | 1829 | 1VANWYCK | 1 | 415 | VAN WYCK 100.00 | 1829 | 1VANWYCK 44.000 | 2 | 415-1829-2 | 27.8 | 27.8 | 8.9 | 25.6 | 92.2 | 13 | - | - | - | - | - | - | 2019 | - | - |  | 26.1 | 28.5 | 27.8 | VAN WYCK TIE 02 | 100/44 kV Transformer | 26.1 | 28.5 | 27.8 | - | - | - | - | - | - | - | - | - | - | 92.2 | - | - | -
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304354 | I-ROCKY PT 230.00 | 305069 | E9-MEADOW 230.00 | 1 | 304354-305069-1 | 478 | 478 | 308.1 | 420.2 | 90.5 | 193 | - | - | - | - | - | - | 2020 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 87.9 | - | - | 64.4 | 90.5 | - | - | 66.2
STUDYROX4VRS | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 77.7 | 106.7 | 90.4 | 100 | - | - | - | - | - | - | 2020 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.2 | - | - | - | 90.4 | - | - | -
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 39.8 | 79.7 | 600 | -25.7 | 2013 | 2027 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 87.7 | 85.4 | 592 | -14.5 | 2014 | 2022 | 8 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 92.8 | 90.4 | 300 | -14.1 | 2013 | 2019 | 6 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 101.7 | 80.4 | 300 | -9.9 | 2020 | 2026 | 6 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 88.4 | 92.3 | 82.8 | 97.6 | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 18.6 | 83.6 | 300 | -7.2 | 2020 | 2024 | 4 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | - | 90.3 | 89.7 | 74.2 | 90.7 | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 107.8 | 89.8 | 300 | -6.6 | 2016 | 2019 | 3 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 96.5 | 96.3 | 89.3 | 96.3 | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | - | - | - | - | - | - | 2015 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | 100.3 | 87.3 | 94.4 | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | - | - | - | - | - | - | 2015 | - | - |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 97.6 | 98.9 | 90 | 97.7 | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | - | - | - | - | - | - | 2016 | - | - |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 93 | 97.8 | 85.3 | 92.3 | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | - | - | - | - | - | - | 2018 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | 93.6 | 93.8 | 84.4 | 93.6 | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | - | - | - | - | - | - | 2019 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.2 | 93.4 | 81.8 | 88.7 | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 23.8 | 76.8 | 504 | -13.7 | 2020 | 2029 | 9 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.9 | 86.1 | 87.6 | 87.8 | 86.6 | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 86.4 | 84.1 | 504 | -11.7 | 2016 | 2023 | 7 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 107.9 | 96.2 | 96.2 | 85.9 | 107.6 | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 91.5 | 89.1 | 252 | -11.3 | 2013 | 2020 | 7 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 112.2 | 100.8 | 100.7 | 90 | 111.8 | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 18.6 | 83.6 | 252 | -7.1 | 2020 | 2024 | 4 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | - | 90.3 | 89.7 | 74.2 | 90.7 | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 107.8 | 89.6 | 252 | -6.7 | 2016 | 2019 | 3 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 96.5 | 96.3 | 89.3 | 96.3 | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | - | - | - | - | - | - | 2014 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | 100.3 | 87.3 | 94.4 | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | - | - | - | - | - | - | 2016 | - | - |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 93 | 97.8 | 85.3 | 92.3 | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | - | - | - | - | - | - | 2018 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | 93.6 | 93.8 | 84.4 | 93.6 | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.2 | 93.4 | 81.8 | 88.7 | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | 2013 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base13s\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2013.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2012 Summer Screening (2007 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2013 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 39.8 | 79.5 | 24 | -25.7 | 2013 | 2027 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 104.9 | - | 104.8 | 103.1 | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 23.9 | 77 | 24 | -13.8 | 2020 | 2029 | 9 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.9 | 86.1 | 87.6 | 87.8 | 86.6 | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2013 FPWC
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 6 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 12 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 44.3 | 153 | 127 | 48 | 119 | 45.5 | 155 | 128.7 | 48 | 1.7 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 127 | - | - | - | 138 | - | - | -
BEL1GM | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 687.9 | 1003.4 | 122.1 | 11301 | 822 | 671 | 986 | 120 | 10818 | -2.1 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 122.1 | 81.6 | 84.2 | 83.7 | 136.7 | 96 | 98.2 | 97.9
MCG2GM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 115.6 | 141.7 | 121.8 | 441 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -9.6 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 30.1 | 26.1 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
MCG2GM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 110.2 | 136.1 | 117.5 | 439 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -9.6 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 35.8 | 30.7 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
OCO3GM | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 108.8 | 188.6 | 113 | 916 | 170 | 109.6 | 187.4 | 112.1 | 1070 | -0.9 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 113 | - | - | 64.4 | 114.9 | - | - | 66.8
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 82.3 | 113.4 | 111.5 | 780 | 102 | 90.2 | 120.4 | 118.4 | 910 | 6.9 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 111.5 | - | - | - | 100.3 | - | - | -
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 115.3 | 229 | 111.2 | 144 | 201 | 116.5 | 231.1 | 112.2 | 144 | 1 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 111.2 | - | - | 55.8 | 117.8 | - | - | 59.1
MCG2GM | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 133.3 | 220.2 | 109.7 | 243 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -8.8 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 109.7 | 73.7 | 73.6 | 64.2 | 111.2 | 79.5 | 74.6 | 65.1
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 243.9 | 645.5 | 108.9 | 48 | 590 | 243 | 644.5 | 108.7 | 48 | -0.2 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 108.9 | - | - | - | 110.3 | - | - | 52.8
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 62.5 | 112.9 | 104.3 | 48 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 1.8 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 16.9 | 15.7 | 104.3 | - | 62.4 | 55.7 | 101.1 | - | 60.5 | 54.1
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 62.5 | 112.9 | 104.3 | 48 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 1.8 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 16.9 | 15.7 | 104.3 | - | - | - | 101.1 | - | - | -
WYLIGM | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 96 | 50 | 51.6 | 51.6 | 103.1 | 96 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105 | - | 104.9 | 103.1 | 105.6 | - | 105.4
OCO3GM | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 38.6 | 77.9 | 101 | 16 | 71.2 | 38.6 | 77.7 | 101 | 7 | 0 | 2013 | 2013 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 3.5 | 2 | 101 | - | - | - | - | - | - | -
DRGSGM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 192.8 | 591.9 | 100.3 | 48 | 590 | 191.8 | 591.2 | 100.1 | 48 | -0.2 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.3 | - | - | - | 101.8 | - | - | -
OCO3GM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 91.2 | 202.9 | 99.5 | 48 | 201 | 92.4 | 204.8 | 100.5 | 48 | 1 | 2014 | 2013 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.5 | - | - | - | 106.1 | - | - | -
WYLIGM | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 20.6 | 149.2 | 99.4 | 48 | 158 | 23.1 | 149.1 | 99.3 | 48 | -0.1 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.4 | - | - | - | 100 | - | - | -
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 83.5 | 115.8 | 98.1 | 201 | 116 | 91.6 | 123 | 104.2 | 320 | 6.1 | 2015 | 2013 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.1 | - | - | - | 88.2 | - | - | -
MCG2GM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 391.4 | 470.3 | 96 | 1461 | 478 | 365.4 | 440 | 89.7 | 1473 | -6.3 | 2016 | 2020 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 40.3 | 8.4 | 96 | 79.7 | 80 | 78.7 | 93.2 | 82.1 | 77.6 | 76.1
MCG2GM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 391.4 | 470.3 | 96 | 1508 | 478 | 365.4 | 440 | 89.7 | 1520 | -6.3 | 2016 | 2020 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 40.3 | 8.4 | 96 | 79.7 | 80 | 78.7 | 93.2 | 82.1 | 77.6 | 76.1
CAT1GM | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 113.5 | 177.2 | 94.7 | 96 | 201 | 110 | 174.9 | 93.4 | 96 | -1.3 | 2017 | 2018 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.7 | - | - | 56.8 | 97.3 | - | - | 60
OCO1GM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 442.1 | 752 | 94.4 | 60 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -5.9 | 2017 | 2021 | 4 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 51.1 | 6.4 | 94.4 | - | 54.2 | 50.5 | 101 | - | - | 54.5
BEL1GM | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 346.6 | 610.7 | 93.8 | 4 | - | - | - | - | - | - | 2018 | - | - |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 93.8 | - | 65.7 | 53.8 | - | - | - | -
DRGSGM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 147.7 | 547 | 92.8 | 48 | 590 | 146.7 | 546.3 | 92.6 | 48 | -0.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.8 | - | - | - | 94.3 | - | - | -
OCO1GM | LONDONCREEKB | 236 | 6PEACH V | 265 | 6RIVERVW | 1 | 236 | 6PEACH V 230.00 | 265 | 6RIVERVW 230.00 | 2 | 236-265-2 | 452.5 | 452.5 | 281.3 | 418.8 | 91.6 | 50 | 452.5 | 272.5 | 405.8 | 88.8 | 48 | -2.8 | 2019 | 2021 | 2 |  | 409.0541 | 452.5 | 409.0541 | LONDON CRK WH | 230 kV Line | 409.1157 | 452.537 | 409.1157 | 452.5 | 263.3 | 390.3 | 86.4 | 28.5 | 5.2 | 91.6 | - | - | - | 84.5 | - | - | -
CAT1GM | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 92.5 | 201.1 | 91.3 | 96 | 220 | 92.6 | 201.2 | 91.3 | 96 | 0 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | - | - | - | 94.8 | - | - | -
MCG1GM | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 352.5 | 388.6 | 90.9 | 2232 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -1.1 | 2020 | 2020 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | -5.9 | 6.2 | 90.9 | 82.2 | 80.9 | 73 | 92.8 | 83.3 | 81.5 | 73
BEL1GM | RICHMOND | 337 | 8NEWPORT | 304377 | RICH500 | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1642.3 | 1811.6 | 90.8 | 8385 | 1904.3 | 1614.7 | 1768.1 | 88.5 | 2731 | -2.3 | 2020 | 2021 | 1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1478.9 | 1641.2 | 81.8 | 170.4 | 9 | 90.8 | 81.7 | 89.2 | 76.7 | 84.9 | 86.5 | 82.5 | 70.4
CLI5GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 335 | 428.1 | 90.6 | 672 | 478 | 335.9 | 428.7 | 90.8 | 665 | 0.2 | 2020 | 2020 | 0 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 32.8 | 7.7 | 90.6 | 73.4 | 78.4 | 66.7 | 88 | 74.8 | 76.1 | 64.6
RIV7GM | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 427.2 | 739.2 | 90 | 144 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | 3.5 | 2020 | 2018 | -2 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 119.5 | 13.2 | 90 | - | - | - | 89.3 | - | - | -
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
MCG2GM | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 107.7 | 104.8 | 96 | 102.7 | - | 98.8 | 96.2 | 96 | -8.6 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 23.5 | 22.8 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
MCG1GM | - | - | - | - | - | - | 2089 | WAYNICKR | 10810 | WENTW WH | 1 | 2089-10810-1 | 86.6 | 86.6 | - | 81.6 | 94.2 | 92 | 86.6 | - | 77.2 | 89.2 | 92 | -5 | 2017 | 2021 | 4 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.2 | 95.5 | 86.9 | 98 | 94.1 | 89.6 | 81.5
MCG1GM | - | - | - | - | - | - | 737 | DAN RIV | 10810 | WENTW WH | 1 | 737-10810-1 | 86.6 | 86.6 | - | 81.7 | 94.3 | 46 | 86.6 | - | 77.3 | 89.3 | 46 | -5 | 2017 | 2021 | 4 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.3 | 95.6 | 87 | 98.1 | 94.2 | 89.7 | 81.6
MCG2GM | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 112.4 | 109.4 | 48 | 102.7 | - | 103.5 | 100.8 | 48 | -8.6 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 23.5 | 22.8 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 3 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
MCG2GM | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 107.6 | 104.8 | 1384 | 102.7 | - | 98.8 | 96.2 | 1384 | -8.6 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 23.4 | 22.8 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
CAT1GM | MCG1 | - | - | - | - | - | 737 | DAN RIV | 10810 | WENTW WH | 1 | 737-10810-1 | 86.6 | 86.6 | - | 82.7 | 95.6 | 689 | 86.6 | - | 78.5 | 90.6 | 686 | -5 | 2016 | 2020 | 4 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.3 | 95.6 | 87 | 98.1 | 94.2 | 89.7 | 81.6
MCG2GM | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 112.4 | 109.4 | 692 | 102.7 | - | 103.4 | 100.7 | 692 | -8.7 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.5 | 23.5 | 22.9 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
MCG2GM | BADX | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 113.1 | 113.1 | - | 110.7 | 97.9 | 26 | 113.1 | - | 101.8 | 90 | 26 | -7.9 | 2015 | 2020 | 5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 87.1 | 77 | 23.6 | 20.9 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
MCG2GM | BADX | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 113.1 | 113.1 | - | 106 | 93.7 | 52 | 113.1 | - | 97.1 | 85.9 | 52 | -7.8 | 2018 | 2023 | 5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 82.4 | 72.9 | 23.6 | 20.8 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 9 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 6 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 15 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDYASH1VRS | INMANBK2 | 3260 | INMAN 2 | 1479 | 1INMAN | 2 | 1479 | 1INMAN 44.000 | 3260 | INMAN 2 100.00 | 1 | 1479-3260-1 | 25.3 | 25.3 | 18.7 | 23.7 | 93.8 | 40 | 23.6 | 18.7 | 18.7 | 79.3 | 38 | -14.5 | 2018 | 2032 | 14 |  | 23.6 | 26.2 | 25.3 | INMAN TIE 01 | 100/44 kV Transformer | 23.6 | 26.2 | 25.3 | 25.3 | 18.4 | 18.4 | 72.7 | 5.3 | 21.1 | 78.5 | 77.6 | 71.9 | 68.9 | 93.8 | 78.6 | 73.2 | 70.2
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 2089 | WAYNICKR 100.00 | 10810 | WENTW WH 100.00 | 1 | 2089-10810-1 | 86.6 | 86.6 | 78.8 | 87.4 | 98 | 191 | 86.6 | 70.8 | 79.6 | 89.3 | 160 | -8.7 | 2015 | 2021 | 6 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.2 | 95.5 | 86.9 | 98 | 94.1 | 89.6 | 81.5
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 737 | DAN RIV 100.00 | 10810 | WENTW WH 100.00 | 1 | 737-10810-1 | 86.6 | 86.6 | 79.5 | 88.3 | 98.1 | 193 | 86.6 | 71.5 | 80.3 | 89.4 | 167 | -8.7 | 2015 | 2021 | 6 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.3 | 95.6 | 87 | 98.1 | 94.2 | 89.7 | 81.6
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 737 | DAN RIV 100.00 | 810 | WENTWRTH 100.00 | 1 | 737-810-1 | 86.6 | 86.6 | 87 | 95.6 | 106.3 | 185 | 86.6 | 79.1 | 87.8 | 97.7 | 183 | -8.6 | 2013 | 2015 | 2 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 102.5 | 103.7 | 94.5 | 106.3 | 102.4 | 97.9 | 89.1
STUDYASH1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 758 | MADISON 100.00 | 821 | DANVALYT 100.00 | 1 | 758-821-1 | 118.6 | 118.6 | 72.5 | 114.9 | 96.2 | 26 | 118.6 | 66.9 | 106.8 | 89.6 | 13 | -6.6 | 2016 | 2020 | 4 |  | 108.3 | 118.6 | 108.3 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 71.6 | 73.5 | 66.5 | 96.2 | 71.3 | 68 | 61.3
STUDYRCH1VRS | OAKLAWNB | 631 | N CHARLT | 10143 | BANCRO B | 1 | 552 | BANCROFT 100.00 | 631 | N CHARLT 100.00 | 1 | 552-631-1 | 207.8 | 207.8 | 134.6 | 200.4 | 94.8 | 133 | 207.8 | 125.8 | 187.2 | 88.6 | 39 | -6.2 | 2017 | 2021 | 4 |  | 199.2 | 207.8 | 199.2 | OAKLAWN WH | 100 kV Line | 199.18 | 220.3104 | 199.18 | - | - | - | - | - | - | - | - | 66.2 | 59.8 | 94.8 | - | 68.9 | 62.5
STUDYRCH1VRS | OAKLAWNB | 631 | N CHARLT | 10143 | BANCRO B | 1 | 552 | BANCROFT 100.00 | 695 | BUCKEYET 100.00 | 1 | 552-695-1 | 207.8 | 207.8 | 134.7 | 200.7 | 94.8 | 133 | 207.8 | 125.9 | 187.5 | 88.6 | 39 | -6.2 | 2017 | 2021 | 4 |  | 199.2 | 207.8 | 199.2 | OAKLAWN WH | 100 kV Line | 199.18 | 220.3104 | 199.18 | 207.8 | 106.3 | 162.9 | 77.6 | 37.8 | 17.2 | - | - | 66.2 | 59.8 | 94.8 | - | 68.9 | 62.5
STUDYASH1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737 | DAN RIV 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 737-10779-1 | 139.4 | 139.4 | 97.5 | 142 | 97.9 | 103 | 139.4 | 92 | 134 | 92.5 | 30 | -5.4 | 2015 | 2018 | 3 |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | 139.4 | 57.1 | 101.2 | 71 | 40.8 | 26.9 | - | 79.1 | 80.7 | 72.6 | 97.9 | 78.8 | 76 | 68.2
STUDYASH1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 821 | DANVALYT 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 821-10779-1 | 139.4 | 139.4 | 96.6 | 140.1 | 97.9 | 103 | 139.4 | 91.2 | 132.3 | 92.5 | 30 | -5.4 | 2015 | 2018 | 3 |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 79 | 80.7 | 72.6 | 97.9 | 78.8 | 76 | 68.2
STUDYRCH1VRS | OAKLAWNB | 631 | N CHARLT | 10143 | BANCRO B | 1 | 611 | LAKEWOOD 100.00 | 695 | BUCKEYET 100.00 | 1 | 611-695-1 | 207.8 | 207.8 | 161 | 227.1 | 107.2 | 457 | 207.8 | 152.2 | 213.9 | 101 | 349 | -6.2 | 2013 | 2013 | 0 |  | 199.2 | 207.8 | 199.2 | OAKLAWN WH | 100 kV Line | 199.18 | 220.3104 | 199.18 | 207.8 | 128.3 | 185.7 | 88.4 | 41.4 | 18.8 | - | 76.4 | 79.3 | 72.1 | 107.2 | 81.8 | 81.9 | 74.8
STUDYRCH1VRS | OAKLAWNW | 631 | N CHARLT | 552 | BANCROFT | 1 | 611 | LAKEWOOD 100.00 | 10143 | BANCRO B 100.00 | 1 | 611-10143-1 | 207.8 | 207.8 | 158.7 | 232.5 | 109 | 422 | 207.8 | 149.9 | 219.1 | 102.8 | 335 | -6.2 | 2013 | 2013 | 0 |  | 199.2 | 207.8 | 199.2 | OAKLAWN BL | 100 kV Line | 199.18 | 220.3104 | 199.18 | - | - | - | - | - | - | - | 74.9 | 77.8 | 70.7 | 109 | 80.3 | 80.4 | 73.4
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 134.9 | 222.9 | 111.2 | 104 | 196.8 | 128.4 | 212.3 | 105.7 | 63 | -5.5 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 109.7 | 73.7 | 73.6 | 64.2 | 111.2 | 79.5 | 74.6 | 65.1
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 105.8 | 130.8 | 113 | 117 | 113.1 | 100.8 | 124.6 | 107.6 | 117 | -5.4 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 83.3 | 97.3 | 84.3 | 33.5 | 28.7 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 897 | GLEN RVN 100.00 | 1 | 857-897-1 | 207.8 | 207.8 | 155.8 | 244 | 115.2 | 173 | 207.8 | 149.2 | 233.3 | 109.9 | 104 | -5.3 | 2013 | 2013 | 0 |  | 207.8 | 207.8 | 207.8 | ALAMANCE BL | 100 kV Line | 282.4892 | 327.0016 | 282.4892 | 207.8 | 122.6 | 153 | 73.4 | 91 | 41.8 | - | 72.9 | 72.9 | 70.6 | 115.2 | 78 | 73.7 | 71.4
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 111.1 | 136.3 | 117.3 | 117 | 113.1 | 106.1 | 130.1 | 111.8 | 117 | -5.5 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 88.5 | 108.6 | 93.4 | 27.7 | 23.9 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
MCG2GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 111.5 | 108.6 | 702 | 102.7 | - | 102.6 | 99.9 | 702 | -8.7 | 2013 | 2014 | 1 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 22.9 | 22.3 | 117.5 | 104.8 | 104.8 | 93.7 | 113 | 108.6 | 100.7 | 90
MCG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 10810 | WENTW WH | 1 | 737-10810-1 | 86.6 | 86.6 | - | 81.6 | 94.2 | 325 | 86.6 | - | 77.2 | 89.1 | 325 | -5.1 | 2017 | 2021 | 4 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.3 | 95.6 | 87 | 98.1 | 94.2 | 89.7 | 81.6
MCG1GMASH1VRS | - | - | - | - | - | - | 2089 | WAYNICKR | 10810 | WENTW WH | 1 | 2089-10810-1 | 86.6 | 86.6 | - | 81.5 | 94.1 | 650 | 86.6 | - | 77.1 | 89.1 | 650 | -5 | 2017 | 2021 | 4 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 94.2 | 95.5 | 86.9 | 98 | 94.1 | 89.6 | 81.5
MCG2GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 116.3 | 113.2 | 351 | 102.7 | - | 107.3 | 104.5 | 351 | -8.7 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 22.9 | 22.3 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG1 | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.8 | 97.9 | 329 | 86.6 | - | 77.3 | 89.3 | 324 | -8.6 | 2015 | 2021 | 6 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 102.5 | 103.7 | 94.5 | 106.3 | 102.4 | 97.9 | 89.1
STUDY | RWGS | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 108.2 | 105.4 | 337 | 102.7 | - | 103.1 | 100.4 | 337 | -5 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 21.7 | 21.1 | 121.8 | 109.4 | 109.4 | 97.9 | 117.3 | 113.2 | 105.4 | 94.2
1.6 | % Yearly Load Growth |  | 2013 Summer Screening with Fayetteville | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2013_FPWC\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013_FPWC.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2013 Summer Screening with Fayetteville | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2013 Summer Screening with Fayetteville |  |  |  | 2013 Summer Screening with Fayetteville
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
Populate Summary Worksheet

## 2018 Base
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2018 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 222 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 58 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 280 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
THRPGM | SINGLE 455 | 304369 | FAY EAST | 304389 | P2-FAY E | 2 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 1 | 304369-304389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 100 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | 76.7 | 77.9 | 77.9 | 155.5 | 79.6 | 80.7 | 80.8
THRPGM | SINGLE 454 | 304369 | FAY EAST | 304389 | P2-FAY E | 1 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 2 | 304369-304389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 100 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | - | - | - | 155.6 | - | - | -
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 50.9 | 171.1 | 142.4 | 75 | 119 | 45.5 | 155 | 128.7 | 48 | -13.7 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 142.4 | - | - | - | 153.7 | - | - | -
THRPGM | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 70.4 | 70.4 | 140.9 | 50 | 50 | 51.6 | 51.6 | 103.1 | 96 | -37.8 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 96.3 | 129.1 | 127.6 | 661 | 102 | 90.2 | 120.4 | 118.4 | 910 | -9.2 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 127.6 | - | - | - | 111.5 | - | - | -
THRPGM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 118.3 | 145.1 | 125.1 | 275 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -12.9 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 33.5 | 29.4 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 126.2 | 251.8 | 122.1 | 125 | 201 | 116.5 | 231.1 | 112.2 | 144 | -9.9 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 122.1 | - | - | 61.1 | 129 | - | - | 64.5
BEL1GM | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 448 | 789.8 | 121.7 | 85 | - | - | - | - | - | - | 2018 | - | - |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 121.7 | 74.3 | 82.8 | 69.5 | 109.2 | 74.2 | 74.7 | 62.5
BEL1GM | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 681.6 | 992.4 | 120.7 | 6129 | 822 | 671 | 986 | 120 | 10818 | -0.7 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 120.7 | 80.2 | 84.1 | 82.6 | 136.4 | 96.7 | 98.7 | 98
THRPGM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 112.5 | 139.1 | 120.5 | 275 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -12.6 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 38.8 | 33.7 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
THRPGM | HNDRSN-FRNKL | 304089 | HENDER11 | 304105 | FRANKLIN |  | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 119.6 | 193.3 | 118 | 845 | 170 | 109.6 | 187.4 | 112.1 | 1070 | -5.9 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | 72.3 | - | 72 | 119.3 | 75.2 | - | 74.9
DRGSGM | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 718 | 6SADLER 230.00 | 2679 | SADLE 3 1.0000 | 3 | 718-2679-3 | 553.7 | 553.7 | 376.3 | 646.8 | 116.8 | 41 | 553.7 | 283.2 | 488.2 | 88.2 | 43 | -28.6 | 2018 | 2021 | 3 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 261.1 | 460.7 | 83.2 | 186.1 | 33.6 | 116.8 | - | 75.1 | 64.3 | 101.5 | - | 70.9 | 56
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 259.4 | 678.5 | 115.6 | 100 | 590 | 243 | 644.5 | 108.7 | 48 | -6.9 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.6 | - | - | - | 116.6 | - | - | 55.5
OCO3GM | SINGLE 190 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 36.6 | 170.2 | 115.4 | 25 | 158 | 23.1 | 149.1 | 99.3 | 48 | -16.1 | 2018 | 2014 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.4 | - | - | - | 116.2 | - | - | -
DRGSGM | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 718 | 6SADLER 230.00 | 2673 | SADLE 4 1.0000 | 4 | 718-2673-4 | 553.7 | 553.7 | 385.9 | 633.3 | 114.4 | 41 | 553.7 | 292.3 | 475.2 | 85.8 | 26 | -28.6 | 2018 | 2023 | 5 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 184.4 | 33.3 | 114.4 | 70.7 | 76.9 | 61.5 | 99 | 72.3 | 72.7 | 53.8
DRGSGM | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 790 | SADLER 100.00 | 2673 | SADLE 4 1.0000 | 4 | 790-2673-4 | 553.7 | 553.7 | 385.9 | 633.3 | 114.4 | 41 | 553.7 | 292.3 | 475.2 | 85.8 | 26 | -28.6 | 2018 | 2023 | 5 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 184.4 | 33.3 | 114.4 | 71.1 | 77.3 | 61.8 | 99 | 72.7 | 73.1 | 54.1
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 98.1 | 132.5 | 112.3 | 429 | 116 | 91.6 | 123 | 104.2 | 320 | -8.1 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.3 | - | - | - | 98.1 | - | - | -
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 101.1 | 223.9 | 110 | 25 | 201 | 92.4 | 204.8 | 100.5 | 48 | -9.5 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | - | - | - | 116.8 | - | - | 52.5
THRPGM | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 132.4 | 219 | 110 | 199 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -9.1 | 2018 | 2013 | -5 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 110 | 73.8 | 73.7 | 64.3 | 118.3 | 79.7 | 79.4 | 69.4
DRGSGM | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 790 | SADLER 100.00 | 2679 | SADLE 3 1.0000 | 3 | 790-2679-3 | 553.7 | 553.7 | 329.4 | 600.1 | 108.4 | 25 | 553.7 | 239.8 | 444.3 | 80.2 | 2 | -28.2 | 2018 | 2027 | 9 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 217.1 | 415.9 | 75.1 | 184.2 | 33.3 | 108.4 | - | 67 | 56.6 | 92.8 | - | 63 | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 205.2 | 623.5 | 106.5 | 25 | 590 | 191.8 | 591.2 | 100.1 | 48 | -6.4 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 106.5 | - | - | - | 107.6 | - | - | -
MCG1GM | MOSERB | 332 | 6CATAWBA | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 332 | 6CATAWBA 230.00 | 2 | 331-332-2 | 796.6 | 796.6 | 558.2 | 836 | 105.5 | 192 | 796.6 | 464.4 | 696.9 | 86.5 | 47 | -19 | 2018 | 2023 | 5 |  | 766.3292 | 796.6 | 796.6 | MOSER BL | 230 kV Line | 1151.8836 | 1436.2698 | 1151.8836 | 796.6 | 464.9 | 705.9 | 87.9 | 130.1 | 17.6 | 105.5 | - | - | - | 85.2 | - | - | -
MCG1GM | SINGLE 146 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304099 | E18-POCO 115.00 | 304105 | FRANKLIN 115.00 | 1 | 304099-304105-1 | 170 | 170 | 43.5 | 166.5 | 104.9 | 25 | 170 | 13.9 | 122.1 | 77.9 | 48 | -27 | 2018 | 2029 | 11 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.9 | - | - | - | 105.4 | - | - | -
CLI5GM | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 62.7 | 113.3 | 104.6 | 25 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 1.5 | 2018 | 2013 | -5 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 17.3 | 16 | 104.6 | - | 62.7 | 55.7 | 101.2 | - | 60.3 | 53.9
CLI5GM | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 62.7 | 113.3 | 104.6 | 25 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 1.5 | 2018 | 2013 | -5 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 17.3 | 16 | 104.6 | - | - | - | 101.2 | - | - | -
BEL1GM | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304047 | WSPN115 TT 115.00 | 304406 | ST PAULS 115.00 | 1 | 304047-304406-1 | 119 | 119 | 100.4 | 125 | 104.3 | 895 | 119 | 70.3 | 89 | 74.5 | 191 | -29.8 | 2018 | 2032 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.3 | 84.3 | - | 88.1 | 109.3 | 91.1 | - | 92.2
ALL5GM | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 481.5 | 828.6 | 103.6 | 75 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | -10.1 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 208.9 | 26.8 | 103.6 | - | - | - | 104.9 | - | - | -
CAT1GM | NORMANB | 540 | 6MCGUIRE | 543 | 6RIVRBEN | 1 | 540 | 6MCGUIRE 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 540-543-2 | 617.5 | 617.5 | 407.2 | 646.5 | 103.4 | 57 | 617.5 | 313.4 | 497.8 | 78.3 | 1 | -25.1 | 2018 | 2029 | 11 |  | 529.8 | 617.5 | 553.7 | NORMAN BL | 230 kV Line | 556.9073 | 617.458 | 556.9073 | - | - | - | - | - | - | 103.4 | - | - | - | 75.1 | - | - | -
MCG1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 540 | 6MCGUIRE 230.00 | 546 | 8MCGUIRE 500.00 | A1 | 540-546-A1 | 1680 | 1680 | 1215.6 | 1719 | 102.3 | 333 | 1680 | 909.2 | 1386.1 | 82.5 | 2 | -19.8 | 2018 | 2026 | 8 |  | 1573.1 | 1680 | 1680 | MCGUIRE SWITCHING STA 01 | 500/230 kV Transformer | 1680 | 1680 | 1680 | - | - | - | - | - | - | 102.3 | 75.3 | 80.9 | 67.8 | 74.1 | 71.8 | 68.6 | -
MCG1GM | ANSON-OAKBOR | 542 | 6OAKBORO | 304985 | LILES SS |  | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 382.4 | 419 | 100.8 | 1415 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -11 | 2018 | 2020 | 2 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 24.5 | 16.1 | 100.8 | 90.8 | 88.7 | 80.8 | 95 | 91.7 | 85.5 | 76.6
MCG1GM | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 37.2 | 76.8 | 100.8 | 25 | 71.2 | 38.6 | 77.7 | 101 | 7 | 0.2 | 2018 | 2013 | -5 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 2.4 | 1.8 | 100.8 | - | - | - | 100.6 | - | - | -
BEL1GM | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304550 | CASTLE HAYNE230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304550-304564-1 | 478 | 478 | 369.2 | 477.3 | 100.5 | 2440 | 478 | 322.5 | 427.3 | 89.3 | 874 | -11.2 | 2018 | 2021 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.5 | 77 | - | 78.1 | 102.8 | 79.5 | - | 79.8
CLI5GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 372.7 | 468.8 | 100.5 | 1138 | 478 | 335.9 | 428.7 | 90.8 | 665 | -9.7 | 2018 | 2020 | 2 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 73.5 | 17.6 | 100.5 | 83.3 | 89.3 | 76.1 | 99 | 84.6 | 85.7 | 73.6
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 2 | 304035-304545-2 | 131 | 131 | 71.2 | 133.3 | 100.1 | 125 | 131 | 52.4 | 111 | 83.3 | 48 | -16.8 | 2018 | 2025 | 7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.1 | - | - | 54.2 | 103.9 | - | - | -
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 405.4 | 488.2 | 99.8 | 849 | 478 | 365.4 | 440 | 89.7 | 1473 | -10.1 | 2019 | 2020 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 58.2 | 12.2 | 99.8 | 82.6 | 83 | 81.7 | 102.1 | 85.1 | 85.2 | 83.7
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 405.4 | 488.2 | 99.8 | 874 | 478 | 365.4 | 440 | 89.7 | 1520 | -10.1 | 2019 | 2020 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 58.2 | 12.2 | 99.8 | 82.6 | 83 | 81.7 | 102.1 | 85.1 | 85.2 | 83.7
BEL1GM | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 353.5 | 543.2 | 99.6 | 53 | 539 | 318.7 | 488.1 | 89 | 48 | -10.6 | 2019 | 2021 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.6 | - | - | 64 | 110.8 | 72.3 | - | 70.5
BEL1GM | SINGLE 878 | 304761 | I-SOUTHE | 304762 | ENKA SW | 1 | 304790 | VANDERBILT 115.00 | 304791 | W ASHEVILE 115.00 | 1 | 304790-304791-1 | 123 | 123 | 80.8 | 121.8 | 99.3 | 295 | 123 | 65.4 | 99.5 | 80.6 | 194 | -18.7 | 2019 | 2027 | 8 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.3 | - | - | 57.5 | 97.6 | - | - | 56.4
BEL1GM | SINGLE 462 | 304378 | RICH230 | 304415 | RAEFORD | 1 | 304047 | WSPN115 TT 115.00 | 304432 | PA-LUMB#2 115.00 | 1 | 304047-304432-1 | 133 | 133 | 99.5 | 128.3 | 98.8 | 556 | 133 | 69.8 | 99.5 | 75.7 | 96 | -23.1 | 2019 | 2031 | 12 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.8 | 75.6 | - | 79.5 | 101.7 | 78.6 | - | 81.1
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 155.8 | 575.8 | 98.4 | 25 | 590 | 146.7 | 546.3 | 92.6 | 48 | -5.8 | 2020 | 2018 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.4 | - | - | - | 99.5 | - | - | -
THRPGM | SINGLE 179 | 304137 | METHOD | 304150 | I-NCSU S | 1 | 304163 | MILB115 TT 115.00 | 304168 | YONKERS 115.00 | 1 | 304163-304168-1 | 190 | 190 | 57 | 178.1 | 97.9 | 100 | 190 | 45.6 | 155.8 | 84.5 | 48 | -13.4 | 2020 | 2024 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.9 | - | - | - | 98.6 | - | - | -
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 76.2 | 198.1 | 97.6 | 25 | 201 | 68.4 | 180 | 88.5 | 48 | -9.1 | 2020 | 2021 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.6 | - | - | - | 104.4 | - | - | -
BEL1GM | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 67.5 | 94.1 | 96.8 | 423 | 97 | 55.6 | 76 | 77.2 | 87 | -19.6 | 2021 | 2030 | 9 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.8 | - | - | 74.4 | 106.1 | 79.8 | - | 80
BEL1GM | SINGLE 208 | 304162 | MILB230 | 304163 | MILB115 | 2 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 1 | 304162-304163-1 | 300 | 300 | 214.6 | 289.4 | 96.5 | 1150 | 300 | 192.5 | 252.8 | 84.3 | 482 | -12.2 | 2021 | 2024 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.5 | 71.6 | - | 71.7 | 97.7 | 73.2 | - | 72.9
BEL1GM | SINGLE 418 | 304347 | ABERDEEN | 304348 | ROCKHM23 | 1 | 304001 | BLEWETT 115.00 | 304004 | TIL 1-4H 115.00 | 1 | 304001-304004-1 | 119 | 119 | 90.2 | 119.2 | 96.3 | 444 | - | - | - | - | - | - | 2021 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.3 | 72.8 | - | 76.8 | 88.7 | 73.5 | - | 70.3
STUDY | SINGLE 855 | 304730 | CAMDEN | 312715 | 6LUGOFF | 1 | 304723 | CAMDEN JCT 115.00 | 304726 | CAMDEN DUSTY115.00 | 1 | 304723-304726-1 | 108 | 108 | 40.4 | 93 | 96.2 | 75 | 108 | 35.6 | 86.8 | 87.7 | 96 | -8.5 | 2021 | 2022 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.2 | - | - | - | 96.2 | - | - | -
MCG1GM | SINGLE 213 | 304163 | MILB115 | 304168 | YONKERS | 1 | 304137 | METHOD 115.00 | 304150 | I-NCSU S 115.00 | 1 | 304137-304150-1 | 190 | 190 | 121 | 177.4 | 95.2 | 272 | 190 | 111 | 155.4 | 82.4 | 48 | -12.8 | 2022 | 2026 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | - | - | 64.6 | 95.9 | - | - | 67
BEL1GM | ROCK_SPRINGS | 546 | 8MCGUIRE | 719 | 8ANTIOCH | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1704.8 | 1879.6 | 95 | 5974 | 1904.3 | 1614.7 | 1768.1 | 88.5 | 2731 | -6.5 | 2022 | 2021 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1478.9 | 1641.2 | 81.8 | 238.4 | 13.2 | 95 | 85.5 | 93.3 | 80.5 | 88.7 | 90.2 | 87.2 | 75.1
ALL5GM | AB_STEEL_W_S | 331 | 6ALLEN | 545 | 6WOODLWN | 2 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 1 | 331-545-1 | 717 | 717 | 453.5 | 663.4 | 94.9 | 26 | 717 | 429.9 | 628.8 | 88.8 | 48 | -6.1 | 2022 | 2021 | -1 |  | 717 | 717 | 717 | STEELBERRY WH | 230 kV Line | 792.617 | 996.5466 | 792.617 | - | - | - | - | - | - | 94.9 | - | 65.6 | 63.7 | 92.2 | - | 64.7 | 61.9
ALL5GM | AB_WOODBK4_L | 545 | 6WOODLWN | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 453.5 | 663.4 | 94.9 | 76 | 717 | 429.9 | 628.8 | 88.8 | 144 | -6.1 | 2022 | 2021 | -1 |  | 717 | 717 | 717 | STEELBERRY BL | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 444.2 | 658.7 | 93.6 | 4.7 | 1.3 | 94.9 | - | - | - | 92.2 | - | - | -
BEL1GM | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304556 | TOPSAIL TAP 230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304556-304564-1 | 478 | 478 | 340.1 | 447.7 | 94.7 | 1577 | 478 | 298 | 402.1 | 84.4 | 481 | -10.3 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.7 | 71.3 | - | 72.3 | 96.9 | 73.7 | - | 74
THRPGM | SINGLE 659 | 304563 | LELAND I | 304568 | DELCO | 1 | 304035 | SUT 1-2F 115.00 | 304560 | I-ASMPCS 115.00 | 1 | 304035-304560-1 | 159 | 159 | 77.3 | 151.2 | 94.1 | 50 | 159 | 63.3 | 133.5 | 83 | 48 | -11.1 | 2022 | 2025 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.1 | - | - | - | 94.1 | - | - | -
THRPGM | SINGLE 215 | 304163 | MILB115 | 304174 | I-PERSTO | 1 | 304137 | METHOD 115.00 | 304153 | TRYON HILLS 115.00 | 1 | 304137-304153-1 | 108 | 108 | 61.3 | 97.6 | 93.9 | 175 | 108 | 57.7 | 85.9 | 81.5 | 193 | -12.4 | 2022 | 2026 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.9 | - | - | 57.7 | 94.7 | - | - | 60.4
THRPGM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 439.2 | 747.5 | 93.8 | 49 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -5.3 | 2023 | 2021 | -2 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 46.6 | 5.8 | 93.8 | - | 54.3 | 50.7 | 103.2 | - | - | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304550 | CASTLE HAYNE230.00 | 304577 | MURRAYVL 230.00 | 1 | 304550-304577-1 | 590 | 590 | 122.9 | 544.8 | 93 | 25 | 590 | 118 | 518 | 87.8 | 48 | -5.2 | 2023 | 2022 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93 | - | - | - | 94.2 | - | - | -
THRPGM | BASE CASE | 0 |  | 0 |  |  | 304615 | BARN CRK E 230.00 | 304616 | BARNARD 115.00 | 1 | 304615-304616-1 | 150 | 150 | 139.4 | 139.4 | 92.9 | 50 | 150 | 122.6 | 122.6 | 81.7 | 96 | -11.2 | 2023 | 2026 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
BEL1GM | SINGLE 647 | 304550 | CASTLE H | 304564 | SCOTT T | 1 | 304545 | CASTLE HAYNE115.00 | 305063 | E9-ELECTRIC 115.00 | 1 | 304545-305063-1 | 179 | 179 | 90.8 | 161.6 | 92.5 | 75 | 179 | 109.1 | 137.3 | 78.2 | 389 | -14.3 | 2023 | 2029 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.5 | - | - | 51.9 | 94.1 | - | - | 52.7
BEL1GM | SINGLE 613 | 304519 | M-TARAWA | 304524 | JACKSV23 | 1 | 304251 | LEE230 SUB 230.00 | 304957 | WYNCO#2 18.000 | 1 | 304251-304957-1 | 220 | 220 | 195.5 | 203 | 92.3 | 200 | 220 | 187.7 | 187.7 | 85.3 | 144 | -7 | 2024 | 2024 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.3 | 86.1 | 87.4 | 87.2 | 96.3 | 89.9 | 90.8 | 90.9
BEL1GM | ROB-NUCOR230 | 304018 | ROB 2 N | 304666 | NUCOR TA |  | 304057 | DARLINGTON 230.00 | 304954 | DCP#12 13.800 | 1 | 304057-304954-1 | 150 | 150 | 128.9 | 138.3 | 92.2 | 186 | 150 | 111.9 | 116.9 | 78 | 145 | -14.2 | 2024 | 2029 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | 83.2 | 85.6 | 85.2 | 96.2 | 90.9 | 92 | 92.1
MCG1GM | SINGLE 424 | 304348 | ROCKHM23 | 304378 | RICH230 | 2 | 304348 | ROCKHM230 TT230.00 | 304378 | RICH230 TT 230.00 | 1 | 304348-304378-1 | 1014 | 1014 | 595.3 | 950.7 | 92.2 | 75 | 1014 | 543.8 | 870.9 | 84 | 48 | -8.2 | 2024 | 2024 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | - | - | 58.2 | 91.1 | - | - | 57.7
CAT1GM | MCGUIRE_XFMR | 546 | 8MCGUIRE | 540 | 6MCGUIRE | A1 | 333 | 6NEWPORT 230.00 | 337 | 8NEWPORT 500.00 | A5 | 333-337-A5 | 1120 | 1120 | 721.1 | 1032.9 | 92.2 | 11 | - | - | - | - | - | - | 2024 | - | - |  | 1120 | 1120 | 1120 | NEWPORT TIE AT5 | 500/230 kV Transformer | 1120 | 1120 | 1120 | - | - | - | - | - | - | 92.2 | - | 98.9 | 61.3 | - | - | 64.4 | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304354 | I-ROCKY PT 230.00 | 305069 | E9-MEADOW 230.00 | 1 | 304354-305069-1 | 478 | 478 | 310.9 | 425.8 | 92.1 | 498 | 478 | 300 | 410.4 | 87.9 | 768 | -4.2 | 2024 | 2022 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.1 | - | - | 66.8 | 94.5 | - | - | 68.4
THRPGM | SINGLE 232 | 304182 | FALLS230 | 304185 | FALLS115 | 2 | 304182 | FALLS230 TT 230.00 | 304185 | FALLS115 TT 115.00 | 1 | 304182-304185-1 | 300 | 300 | 197.7 | 276.1 | 92 | 481 | 300 | 167.5 | 233.9 | 78 | 192 | -14 | 2024 | 2029 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | 66 | 92.6 | - | - | 66.5
BEL1GM | SINGLE 635 | 304540 | GEIGER T | 304542 | FOLKSTN | 1 | 304543 | FOLKSTN 115 115.00 | 305061 | E9-DAWSON 115.00 | 1 | 304543-305061-1 | 158 | 158 | 79.1 | 145.3 | 92 | 50 | - | - | - | - | - | - | 2024 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | 51.4 | 94.3 | - | - | 52.5
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 304378 | RICH230 TT 230.00 | 304978 | RICH CC2 18.000 | 1 | 304378-304978-1 | 795 | 795 | 696.8 | 728.8 | 91.7 | 690 | 795 | 673.5 | 702.4 | 88.4 | 798 | -3.3 | 2024 | 2021 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.7 | 84.4 | 86.7 | 85.6 | 93.8 | 88.9 | 89.7 | 88.9
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 1 | 304035-304545-1 | 159 | 159 | 78.8 | 144.5 | 91.2 | 50 | 159 | 57.6 | 120.9 | 76 | 48 | -15.2 | 2024 | 2031 | 7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.2 | - | - | - | 93.2 | - | - | 55
BEL1GM | SINGLE 240 | 304190 | WAKE 230 | 304191 | WENDELL | 1 | 304156 | ROL/SQD TAP 230.00 | 304190 | WAKE 230 230.00 | 1 | 304156-304190-1 | 797 | 797 | 552.7 | 734.5 | 91.1 | 1084 | 797 | 448.6 | 625 | 76.9 | 147 | -14.2 | 2024 | 2030 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.1 | - | - | 69.2 | 92.4 | 72.4 | - | 70.2
BEL1GM | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304406 | ST PAULS 115.00 | 304412 | FLOR DUP SW 115.00 | 1 | 304406-304412-1 | 119 | 119 | 82.8 | 106.1 | 90.8 | 597 | - | - | - | - | - | - | 2025 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | 70.8 | - | 74.6 | 95.7 | 77.5 | - | 78.7
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 476.2 | 761.3 | 90.6 | 14 | 840 | 447.7 | 715.1 | 85.1 | 7 | -5.5 | 2025 | 2024 | -1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 460.2 | 736.3 | 87.7 | 25 | 2.9 | 90.6 | - | - | 56 | - | - | 55.7 | -
DRGSGM | SADLERB | 826 | 6ERNEST2 | 718 | 6SADLER | 1 | 718 | 6SADLER 230.00 | 826 | 6ERNEST2 230.00 | 2 | 718-826-2 | 717 | 717 | 379 | 666.2 | 90.6 | 24 | - | - | - | - | - | - | 2025 | - | - |  | 576 | 717 | 576 | SADLER WH | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 90.6 | - | - | - | 79.1 | - | - | -
BEL1GM | SINGLE 207 | 304162 | MILB230 | 304163 | MILB115 | 1 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 2 | 304162-304163-2 | 300 | 300 | 202.4 | 271.4 | 90.5 | 405 | 300 | 182.9 | 236.9 | 79 | 144 | -11.5 | 2025 | 2028 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.5 | - | - | - | 91.5 | - | - | -
MCG1GM | SINGLE 613 | 304519 | M-TARAWA | 304524 | JACKSV23 | 1 | 304251 | LEE230 SUB 230.00 | 304956 | WYNCO#1 18.000 | 1 | 304251-304956-1 | 220 | 220 | 191 | 198.6 | 90.3 | 200 | 220 | 183.1 | 183.1 | 83.2 | 144 | -7.1 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.3 | 84.1 | 85.4 | 85.1 | 94.3 | 88 | 88.8 | 88.9
BEL1GM | SINGLE 552 | 304465 | NWBERN23 | 304484 | HAVELOCK | 1 | 304519 | M-TARAWA 230.00 | 304524 | JACKSV230 TT230.00 | 1 | 304519-304524-1 | 478 | 478 | 325.7 | 419 | 90 | 1062 | 478 | 317.4 | 410.6 | 87.7 | 635 | -2.3 | 2025 | 2022 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | - | - | 70.2 | 91 | 71 | - | 71.1
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 48 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 53 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
CAT1GM | - | - | - | - | - | - | 183 | OAKVALE | 195 | SHADY GR | 1 | 183-195-1 | 207.8 | 207.8 | - | 206.2 | 99.2 | 50 | 207.8 | - | 161.3 | 77.6 | 96 | -21.6 | 2019 | 2029 | 10 |  | 207.8 | 284.9 | 240.7 | OAKVALE BL | 100 kV Line | 264.3032 | 327.0016 | 264.3032 | - | - | - | - | - | - | - | 99.2 | 83.4 | 65.6 | 84.6 | 99.3 | 70.5 | 56
BEL1GM | - | - | - | - | - | - | 382 | MCADENVL | 647 | RANKIN T | 1 | 382-647-1 | 170.1 | 170.1 | - | 162.4 | 95.5 | 50 | 170.1 | - | 131.3 | 77.2 | 6 | -18.3 | 2021 | 2030 | 9 |  | 170.1 | 196.8 | 177.9 | MOUNTAIN ISLAND | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 170.1 | - | 122.7 | 72.1 | 39.7 | 23.4 | - | 95.5 | 97.4 | 81.1 | 93.9 | 93.8 | 87.6 | 73
CAT1GM | - | - | - | - | - | - | 465 | HICKORY | 483 | NEWTON T | 1 | 465-483-1 | 103.9 | 103.9 | - | 122.4 | 117.8 | 25 | 103.9 | - | 103.6 | 99.7 | 48 | -18.1 | 2018 | 2014 | -4 |  | 103.9 | 141.2 | 128 | MULL WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 104 | - | 98.6 | 94.8 | 23.8 | 23 | - | 117.8 | 103.4 | 86.4 | 117.5 | 121.1 | 98.4 | 86.4
CAT1GM | - | - | - | - | - | - | 242 | BUSH RIV | 283 | NEWBERRY | 1 | 242-283-1 | 86.6 | 86.6 | - | 79.8 | 92.1 | 25 | 86.6 | - | 64.3 | 74.3 | 1 | -17.8 | 2024 | 2032 | 8 |  | 86.6 | 121.24 | 108.3 | MIDWAY WH | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | - | - | - | - | - | - | - | 92.1 | 87.5 | 72.9 | 76.7 | 91.6 | 73.6 | 61.7
CAT1GM | - | - | - | - | - | - | 687 | WINECOFF | 10642 | POPLRT B | 1 | 687-10642-1 | 120 | 120 | - | 118.4 | 98.7 | 25 | 120 | - | 100.1 | 83.4 | 44 | -15.3 | 2019 | 2025 | 6 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
CAT1GM | - | - | - | - | - | - | 642 | POPLR TN | 687 | WINECOFF | 1 | 642-687-1 | 120 | 120 | - | 109.7 | 91.4 | 25 | 120 | - | 91.7 | 76.4 | 13 | -15 | 2024 | 2030 | 6 |  | 120 | 129.9 | 125.6 | HOPEWHELL WH | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 91.4 | 97.1 | 85.2 | 94.9 | 90.5 | 87.3 | 81.6
BEL1GM | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 113 | 110 | 25 | 102.7 | - | 97.8 | 95.2 | 47 | -14.8 | 2018 | 2017 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
CAT1GM | - | - | - | - | - | - | 2259 | EASTFLDR | 10642 | POPLRT B | 1 | 2259-10642-1 | 126.4 | 126.4 | - | 118.5 | 93.7 | 25 | 126.4 | - | 100.2 | 79.2 | 39 | -14.5 | 2023 | 2028 | 5 |  | 126.4 | 139.4 | 126.7 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 93.7 | 103.4 | 85.7 | 100.3 | 92.9 | 93.5 | 82.3
BEL1GM | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 110 | 107.1 | 25 | 102.7 | - | 95.5 | 93 | 43 | -14.1 | 2018 | 2018 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
CAT1GM | - | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 108.3 | 108.3 | - | 120 | 110.8 | 25 | 108.3 | - | 105.2 | 97.2 | 48 | -13.6 | 2018 | 2015 | -3 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.6 | 80.9 | 32.4 | 29.9 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
BEL1GM | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 104.9 | 102.2 | 25 | 102.7 | - | 91.6 | 89.2 | 39 | -13 | 2018 | 2021 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
BUC5GM | - | - | - | - | - | - | 536 | 6BUCK | 561 | BUCK TIE | A4 | 536-561-A4 | 509 | 509 | - | 468 | 91.9 | 25 | 509 | - | 402 | 79 | 44 | -12.9 | 2024 | 2028 | 4 |  | 509 | 584.2 | 547.9 | BUCK TIE AT4 | 230/100 kV Transformer | 509 | 584.2 | 547.9 | - | - | - | - | - | - | - | 91.9 | 91.7 | 79.6 | 91.3 | 92.5 | 86.5 | 74.7
BEL1GM | - | - | - | - | - | - | 611 | LAKEWOOD | 10555 | BELHAV W | 1 | 611-10555-1 | 177.9 | 177.9 | - | 168.2 | 94.6 | 25 | 177.9 | - | 145.8 | 82 | 39 | -12.6 | 2022 | 2026 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
BEL1GM | - | - | - | - | - | - | 673 | THRIFT T | 10555 | BELHAV W | 1 | 673-10555-1 | 177.9 | 177.9 | - | 168.2 | 94.6 | 25 | 177.9 | - | 145.8 | 82 | 39 | -12.6 | 2022 | 2026 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
CAT1GM | - | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 120 | 120 | - | 123.2 | 102.6 | 25 | 120 | - | 108 | 90 | 48 | -12.6 | 2018 | 2020 | 2 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 120 | - | 87.7 | 73 | 35.5 | 29.6 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
CAT1GM | - | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 108.3 | 108.3 | - | 112.4 | 103.8 | 25 | 108.3 | - | 98.8 | 91.2 | 48 | -12.6 | 2018 | 2019 | 1 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.6 | 80.9 | 24.8 | 22.9 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
BEL1GM | - | - | - | - | - | - | 555 | BELHAVEN | 611 | LAKEWOOD | 1 | 555-611-1 | 177.9 | 177.9 | - | 163.4 | 91.9 | 25 | 177.9 | - | 142 | 79.8 | 39 | -12.1 | 2024 | 2028 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | - | - | - | - | - | - | - | 91.9 | 94.7 | 82.3 | 93.3 | 94 | 94.3 | 82.1
BEL1GM | - | - | - | - | - | - | 304615 | BARN CRK | 304616 | BARNARD | 1 | 304615-304616-1 | 150 | 150 | - | 137.5 | 91.7 | 25 | 150 | - | 120.4 | 80.2 | 48 | -11.5 | 2024 | 2027 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
BAD1GM | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 110.2 | 107.3 | 50 | 102.7 | - | 98.8 | 96.2 | 96 | -11.1 | 2018 | 2016 | -2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 26 | 25.3 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
MCG1GM | - | - | - | - | - | - | 648 | REAMES R | 10590 | GERDAU W | 1 | 648-10590-1 | 91.2 | 91.2 | - | 96.8 | 106.2 | 25 | 91.2 | - | 87.1 | 95.5 | 48 | -10.7 | 2018 | 2016 | -2 |  | 91.2 | 112.3 | 91.2 | REAMES RD. RET. TAP | 100 kV Line | 106 | 130.6 | 106 | 91.2 | - | 97.2 | 106.5 | -0.4 | -0.3 | - | 106.2 | 110.3 | 85.9 | 104.8 | 105.9 | 105.6 | 84.9
MCG1GM | - | - | - | - | - | - | 928 | JESUPTWN | 943 | N GREENS | 1 | 928-943-1 | 177.9 | 177.9 | - | 176.4 | 99.2 | 25 | 177.9 | - | 159 | 89.4 | 48 | -9.8 | 2019 | 2021 | 2 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 163.5 | - | 144.2 | 88.2 | 32.2 | 11 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
CAT1GM | - | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 28.9 | 28.9 | - | 29.1 | 100.8 | 50 | 28.9 | - | 26.3 | 91.1 | 96 | -9.7 | 2018 | 2019 | 1 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 28.9 | - | 25.6 | 88.6 | 3.5 | 12.2 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
ALL5GM | - | - | - | - | - | - | 385 | NEWPORT | 10119 | ROCK H7 | 2 | 385-10119-2 | 196.8 | 196.8 | - | 185.5 | 94.3 | 25 | 196.8 | - | 166.8 | 84.7 | 47 | -9.6 | 2022 | 2024 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 94.3 | 100 | 80.6 | 97.3 | 93.3 | 93.9 | 74.1
ALL5GM | - | - | - | - | - | - | 385 | NEWPORT | 417 | WYLIE HY | 1 | 385-417-1 | 196.8 | 196.8 | - | 179.3 | 91.1 | 25 | 196.8 | - | 161 | 81.8 | 47 | -9.3 | 2024 | 2026 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 91.1 | 96.7 | 77.8 | 94.1 | 90.1 | 90.7 | 71.4
MCG1GM | - | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37.2 | 93 | 25 | 40 | - | 33.6 | 84 | 48 | -9 | 2023 | 2024 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 30.6 | 76.6 | 6.6 | 16.4 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
CAT1GM | - | - | - | - | - | - | 1291 | 1JPS SLA | 1352 | 1TIGERVT | 1 | 1291-1352-1 | 25.8 | 25.8 | - | 24.1 | 93.4 | 25 | 25.8 | - | 21.8 | 84.6 | 48 | -8.8 | 2023 | 2024 | 1 |  | 25.8 | 31.3 | 25.8 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 20.4 | 78.9 | 3.7 | 14.5 | - | 93.4 | 94.8 | 76.6 | 92.5 | 93.5 | 93 | 76
MCG1GM | - | - | - | - | - | - | 2413 | 1AO SMIT | 2456 | 1WLTR KI | 1 | 2413-2456-1 | 40 | 40 | - | 36.1 | 90.2 | 25 | 40 | - | 32.5 | 81.4 | 48 | -8.8 | 2025 | 2026 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 29.5 | 73.8 | 6.6 | 16.4 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
MCG1GM | - | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 436.9 | 436.9 | - | 396.6 | 90.8 | 50 | 436.9 | - | 358.2 | 82 | 94 | -8.8 | 2025 | 2026 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 436.9 | - | 366.4 | 83.8 | 30.2 | 7 | 100.8 | 90.8 | 88.7 | 80.8 | 95 | 91.7 | 85.5 | 76.6
MCG1GM | - | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 128 | 128 | - | 122.7 | 95.9 | 25 | 128 | - | 111.6 | 87.2 | 48 | -8.7 | 2021 | 2022 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 100.5 | 78.5 | 22.2 | 17.4 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
ALL5GM | - | - | - | - | - | - | 894 | GILBRTHT | 10968 | TROLNGWB | 1 | 894-10968-1 | 118.8 | 118.8 | - | 111.4 | 93.8 | 25 | 118.8 | - | 101.3 | 85.3 | 48 | -8.5 | 2023 | 2024 | 1 |  | 118.8 | 130.8 | 118.8 | SWEPSONVILLE BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 118.8 | - | 91.4 | 76.9 | 20 | 16.9 | - | 93.8 | 93.9 | 84.9 | 94.5 | 94.6 | 94.5 | 85.4
CAT1GM | - | - | - | - | - | - | 1309 | 1MARIETA | 1322 | 1MRRTTA | 1 | 1309-1322-1 | 44.7 | 44.7 | - | 41.3 | 92.6 | 25 | 44.7 | - | 37.7 | 84.4 | 48 | -8.2 | 2023 | 2024 | 1 |  | 44.6532 | 49.149 | 44.6532 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 35.1 | 78.7 | 6.2 | 13.9 | - | 92.6 | 93.9 | 83.7 | 91.7 | 92.7 | 92.3 | 83.1
CAT1GM | - | - | - | - | - | - | 1331 | 1PENROS | 1335 | 1PISGAH | 1 | 1331-1335-1 | 25.8 | 25.8 | - | 23.7 | 91.7 | 25 | 25.8 | - | 21.6 | 83.6 | 48 | -8.1 | 2024 | 2025 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 19.7 | 76.5 | 4 | 15.2 | - | 91.7 | 92.1 | 75.4 | 91.5 | 92 | 91.7 | 75.2
CAT1GM | - | - | - | - | - | - | 195 | SHADY GR | 10181 | MOONVI W | 1 | 195-10181-1 | 126.4 | 126.4 | - | 118.3 | 93.6 | 25 | 126.4 | - | 108.1 | 85.5 | 48 | -8.1 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 94.3 | 74.6 | 24 | 19 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
THRPGM | - | - | - | - | - | - | 2422 | 1ENO | 2621 | ENO 3 | 3 | 2422-2621-3 | 40 | 40 | - | 38 | 95 | 50 | 40 | - | 34.7 | 86.9 | 96 | -8.1 | 2022 | 2022 | 0 |  | 40 | 50 | 50 | ENO TIE 03 TERT | 230/100/44 kV Transformer | 40 | 50 | 50 | 40 | - | 28 | 70.1 | 10 | 24.9 | - | 95 | 76 | 75.5 | 94 | 96 | 76.8 | 76.3
CAT1GM | - | - | - | - | - | - | 10180 | MICHMV W | 10181 | MOONVI W | 1 | 10180-10181-1 | 126.4 | 126.4 | - | 118.3 | 93.6 | 25 | 126.4 | - | 108.1 | 85.6 | 48 | -8 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 94.3 | 74.6 | 24 | 19 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
CAT1GM | - | - | - | - | - | - | 103 | 3M TAP | 10180 | MICHMV W | 1 | 103-10180-1 | 126.1 | 126.1 | - | 118.3 | 93.8 | 25 | 126.1 | - | 108.2 | 85.8 | 48 | -8 | 2023 | 2023 | 0 |  | 126.1 | 139.4 | 126.1 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.1 | - | 94.3 | 74.8 | 24 | 19 | - | 93.8 | 94.9 | 84.7 | 92.6 | 93.9 | 93.1 | 83.7
CAT1GM | - | - | - | - | - | - | 1271 | 1GEN ELE | 1280 | 1HEND MN | 1 | 1271-1280-1 | 25.8 | 25.8 | - | 24.4 | 94.5 | 25 | 25.8 | - | 22.3 | 86.5 | 48 | -8 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | HENDERSONVILLE #1 | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.4 | 83 | 3 | 11.5 | - | 94.5 | 95.6 | 77.6 | 94.4 | 94.9 | 94.7 | 77.7
CAT1GM | - | - | - | - | - | - | 1280 | 1HEND MN | 1295 | 1KANUGA | 1 | 1280-1295-1 | 25.8 | 25.8 | - | 24.4 | 94.5 | 25 | 25.8 | - | 22.3 | 86.5 | 48 | -8 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.4 | 83 | 3 | 11.5 | - | 94.5 | 95.7 | 77.6 | 94.5 | 94.9 | 94.7 | 77.7
CAT1GM | - | - | - | - | - | - | 600 | HARRISBG | 601 | HCKRY GR | 1 | 600-601-1 | 120 | 120 | - | 115.3 | 96.1 | 25 | 120 | - | 105.7 | 88.1 | 48 | -8 | 2021 | 2021 | 0 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 120 | - | 89.8 | 74.8 | 25.5 | 21.3 | - | 96.1 | 103.7 | 88.9 | 96.9 | 97.4 | 93.9 | 84.7
MCG1GM | - | - | - | - | - | - | 1989 | 1LONVIEW | 2022 | 1QUAKER | 1 | 1989-2022-1 | 38.1 | 38.1 | - | 34.3 | 90.1 | 25 | 38.1 | - | 31.3 | 82.2 | 48 | -7.9 | 2025 | 2026 | 1 |  | 38.1 | 41.7 | 38.1 | PONS | 44 kV Line | 0 | 0 | 0 | 38.1 | - | 27.8 | 73.1 | 6.5 | 17 | - | 90.1 | 92.6 | 82 | 89 | 89.6 | 89.6 | 81.2
CLI5GM | - | - | - | - | - | - | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 254-324-1 | 120 | 120 | - | 123 | 102.5 | 50 | 120 | - | 113.7 | 94.8 | 96 | -7.7 | 2018 | 2017 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 120 | - | 100.7 | 83.9 | 22.3 | 18.6 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
ALL5GM | - | - | - | - | - | - | 663 | STELCK R | 684 | WESTNHSW | 1 | 663-684-1 | 102.7 | 102.7 | - | 93 | 90.6 | 25 | 102.7 | - | 85.3 | 83.1 | 48 | -7.5 | 2025 | 2025 | 0 |  | 102.7 | 113.1 | 102.7 | WESTINGHOUSE TAP LINE WH | 100 kV Line | 102.7 | 113.1 | 102.7 | 102.7 | - | 76.1 | 74.1 | 16.9 | 16.5 | - | 90.6 | 94.6 | 82.1 | 89.7 | 90.5 | 90.5 | 81.3
CAT1GM | - | - | - | - | - | - | 1382 | 1NEWBERY | 1390 | 1NWBYC3 | 1 | 1382-1390-1 | 22 | 22 | - | 19.9 | 90.2 | 25 | 22 | - | 18.2 | 82.8 | 48 | -7.4 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | 22 | - | 17.8 | 80.8 | 2.1 | 9.4 | - | 90.2 | 90.7 | 90.2 | 89.5 | 90.2 | 89.9 | 89.6
CAT1GM | - | - | - | - | - | - | 925 | IMPERALW | 10944 | NORTEL W | 1 | 925-10944-1 | 130.6 | 130.6 | - | 119.6 | 91.6 | 25 | 130.6 | - | 109.9 | 84.2 | 48 | -7.4 | 2024 | 2024 | 0 |  | 130.6 | 161.4 | 130.6 | PANTHER WH | 100 kV Line | 130.5928 | 161.4224 | 130.5928 | 130.6 | - | 106.2 | 81.3 | 13.4 | 10.3 | - | 91.6 | 91.9 | 73.9 | 92.2 | 92.4 | 92.3 | 74.3
OCO1GM | - | - | - | - | - | - | 1030 | 1BLREC 7 | 1206 | 1BEACON | 1 | 1030-1206-1 | 31 | 31 | - | 28.2 | 91.1 | 25 | 31 | - | 26 | 83.8 | 48 | -7.3 | 2024 | 2025 | 1 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | - | 24.5 | 79 | 3.7 | 12.1 | - | 91.1 | 92.9 | 85.4 | 90.4 | 91.2 | 91 | 84.8
MAR3GM | - | - | - | - | - | - | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737-779-1 | 126.4 | 126.4 | - | 117.5 | 93 | 25 | 126.4 | - | 109.6 | 86.7 | 46 | -6.3 | 2023 | 2022 | -1 |  | 126.4 | 139.4 | 126.4 | MAYO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 93 | 95 | 85.1 | 95.6 | 92.7 | 93.5 | 84
CAT1GM | - | - | - | - | - | - | 437 | UNEMC 12 | 635 | OAKBORO | 1 | 437-635-1 | 183.9 | 183.9 | - | 165.5 | 90 | 25 | 174.2 | - | 147.3 | 84.6 | 48 | -5.4 | 2025 | 2027 | 2 |  | 174.2 | 204.7 | 174.2 | ROCKY RIVER WH | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | - | - | - | - | - | - | - | 90 | 101.3 | 80.9 | 92.3 | 89.6 | 91 | 77.1
BEL1GM | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 21.2 | 95.4 | 25 | 22.2 | - | 20.1 | 90.3 | 48 | -5.1 | 2021 | 2020 | -1 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 16 | 71.8 | 5.2 | 23.6 | - | 95.4 | 95.5 | 78.8 | 98 | 96.6 | 96 | 79.3
CAT1GM | - | - | - | - | - | - | 41 | LEE | 151 | ESTES TB | 1 | 41-151-1 | 103.4 | 103.4 | - | 142 | 137.3 | 46 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 137.3 | 145.8 | 143.1 | 93.2 | 138.5 | 84.8 | 83.5
CAT1GM | - | - | - | - | - | - | 41 | LEE | 195 | SHADY GR | 1 | 41-195-1 | 103.4 | 103.4 | - | 133.9 | 129.5 | 142 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 129.5 | 137.9 | 135.4 | 85 | 130.7 | 76.9 | 75.6
CAT1GM | - | - | - | - | - | - | 151 | ESTES TB | 195 | SHADY GR | 1 | 151-195-1 | 103.4 | 103.4 | - | 109.2 | 105.6 | 9 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 105.6 | 113.4 | 111.7 | - | 106.8 | 52.4 | 51.6
JOC1GM | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 115.4 | 112.4 | 25 | 102.7 | - | 103.5 | 100.8 | 48 | -11.6 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 26.5 | 25.8 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
ALL4GM | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 72.7 | 145.5 | 50 | 50 | - | 52.4 | 104.9 | 96 | -40.6 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 68 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 73 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
CAT1GM | CAT2 | - | - | - | - | - | 41 | LEE | 151 | ESTES TB | 1 | 41-151-1 | 103.4 | 103.4 | - | 150.8 | 145.8 | 1182 | 103.4 | - | 74.9 | 72.4 | 1282 | -73.4 | 2018 | 2034 | 16 |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | 103.4 | - | 77.8 | 75.3 | 73 | 70.5 | - | 137.3 | 145.8 | 143.1 | 93.2 | 138.5 | 84.8 | 83.5
CAT1GM | CAT2 | - | - | - | - | - | 41 | LEE | 195 | SHADY GR | 1 | 41-195-1 | 103.4 | 103.4 | - | 142.6 | 137.9 | 3544 | 103.4 | - | 67.3 | 65.1 | 3806 | -72.8 | 2018 | 2041 | 23 |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | 103.4 | - | 71.2 | 68.8 | 71.4 | 69.1 | - | 129.5 | 137.9 | 135.4 | 85 | 130.7 | 76.9 | 75.6
CAT1GM | CAT2 | - | - | - | - | - | 333 | 6NEWPORT | 337 | 8NEWPORT | A5 | 333-337-A5 | 1120 | 1120 | - | 1107.2 | 98.9 | 48 | 1120 | - | 826.6 | 73.8 | 14 | -25.1 | 2019 | 2033 | 14 |  | 1120 | 1120 | 1120 | NEWPORT TIE AT5 | 500/230 kV Transformer | 1120 | 1120 | 1120 | 1120 | - | 644.2 | 57.5 | 463 | 41.4 | 92.2 | - | 98.9 | 61.3 | - | - | 64.4 | -
CAT1GM | CAT2 | - | - | - | - | - | 170 | GREER D3 | 10184 | PEBBLE W | 1 | 170-10184-1 | 58.5 | 58.5 | - | 54 | 92.3 | 587 | 58.5 | - | 40.4 | 69 | 348 | -23.3 | 2024 | 2037 | 13 |  | 58.5 | 71.2 | 58.5 | UNION WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 35.6 | 60.9 | 18.4 | 31.4 | - | 79.8 | 92.3 | 60.5 | 79.8 | 77.5 | 67.3 | -
CAT1GM | CAT2 | - | - | - | - | - | 198 | TIGER | 10275 | SPRGLYMW | 1 | 198-10275-1 | 86.2 | 86.2 | - | 84.6 | 98.1 | 591 | 86.2 | - | 65.8 | 76.3 | 688 | -21.8 | 2020 | 2031 | 11 |  | 86.2 | 94.2 | 86.2 | TIGER WH | 100 kV Line | 88.6784 | 97.6848 | 88.6784 | 86.2 | - | 61.9 | 71.8 | 22.7 | 26.3 | - | 85.9 | 98.1 | 73.1 | 78.4 | 83.8 | 76.3 | 56.3
CAT1GM | CAT2 | - | - | - | - | - | 271 | LELIA TP | 10275 | SPRGLYMW | 1 | 271-10275-1 | 86.2 | 86.2 | - | 84.6 | 98.1 | 1182 | 86.2 | - | 65.8 | 76.4 | 1376 | -21.7 | 2020 | 2030 | 10 |  | 86.2 | 94.2 | 86.2 | TIGER WH | 100 kV Line | 88.6784 | 97.6848 | 88.6784 | 86.2 | - | 61.9 | 71.9 | 22.7 | 26.2 | - | 85.9 | 98.1 | 73.1 | 78.4 | 83.8 | 76.3 | 56.4
CAT1GM | CAT2 | - | - | - | - | - | 540 | 6MCGUIRE | 543 | 6RIVRBEN | 1 | 540-543-1 | 553.7 | 553.7 | - | 523.5 | 94.5 | 1002 | 553.7 | - | 404 | 73 | 106 | -21.5 | 2022 | 2033 | 11 |  | 529.8 | 617.5 | 553.7 | NORMAN WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 495.6 | - | 290.6 | 58.6 | 232.9 | 35.9 | 84.7 | 75.7 | 94.5 | 65.7 | - | - | 70.1 | -
CAT1GM | CAT2 | - | - | - | - | - | 275 | SPRGLYMB | 307 | WALDEN T | 1 | 275-307-1 | 86.2 | 86.2 | - | 78.3 | 90.9 | 591 | 86.2 | - | 60.2 | 69.9 | 636 | -21 | 2025 | 2036 | 11 |  | 86.2 | 94.2 | 86.2 | TIGER BL | 100 kV Line | 88.6784 | 97.6848 | 88.6784 | 86.2 | - | 52.9 | 61.3 | 25.4 | 29.6 | - | 78.7 | 90.9 | 66.7 | 71.4 | 76.7 | 69.4 | 50.3
CAT1GM | CAT2 | - | - | - | - | - | 198 | TIGER | 275 | SPRGLYMB | 1 | 198-275-1 | 86.2 | 86.2 | - | 78.4 | 91 | 1182 | 86.2 | - | 60.3 | 70 | 1272 | -21 | 2024 | 2036 | 12 |  | 86.2 | 94.2 | 86.2 | TIGER BL | 100 kV Line | 88.6784 | 97.6848 | 88.6784 | 86.2 | - | 53.1 | 61.7 | 25.3 | 29.3 | - | 78.8 | 91 | 66.7 | 71.5 | 76.8 | 69.4 | 50.3
CAT1GM | CAT2 | - | - | - | - | - | 687 | WINECOFF | 10642 | POPLRT B | 1 | 687-10642-1 | 125.6 | 125.6 | - | 130.9 | 104.3 | 591 | 125.6 | - | 106.9 | 85.1 | 692 | -19.2 | 2018 | 2024 | 6 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | 125.6 | - | 86.8 | 69.1 | 44.1 | 35.2 | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
CAT1GM | CAT2 | - | - | - | - | - | 465 | HICKORY | 483 | NEWTON T | 1 | 465-483-1 | 128 | 128 | - | 132.4 | 103.4 | 591 | 128 | - | 108 | 84.4 | 692 | -19 | 2018 | 2024 | 6 |  | 103.9 | 141.2 | 128 | MULL WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 104.3 | 81.5 | 28.1 | 21.9 | - | 117.8 | 103.4 | 86.4 | 117.5 | 121.1 | 98.4 | 86.4
CAT1GM | CAT2 | - | - | - | - | - | 2259 | EASTFLDR | 10642 | POPLRT B | 1 | 2259-10642-1 | 126.7 | 126.7 | - | 131 | 103.4 | 591 | 126.7 | - | 107 | 84.4 | 692 | -19 | 2018 | 2024 | 6 |  | 126.4 | 139.4 | 126.7 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.7 | - | 86.8 | 68.5 | 44.2 | 34.9 | - | 93.7 | 103.4 | 85.7 | 100.3 | 92.9 | 93.5 | 82.3
CAT1GM | CAT2 | - | - | - | - | - | 642 | POPLR TN | 687 | WINECOFF | 1 | 642-687-1 | 125.6 | 125.6 | - | 122 | 97.1 | 591 | 125.6 | - | 98.6 | 78.5 | 692 | -18.6 | 2020 | 2029 | 9 |  | 120 | 129.9 | 125.6 | HOPEWHELL WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 125.6 | - | 88.6 | 70.5 | 33.4 | 26.6 | - | 91.4 | 97.1 | 85.2 | 94.9 | 90.5 | 87.3 | 81.6
BEL1GM | BEL2 | - | - | - | - | - | 382 | MCADENVL | 647 | RANKIN T | 1 | 382-647-1 | 177.9 | 177.9 | - | 173.4 | 97.4 | 1180 | 177.9 | - | 141 | 79.3 | 1330 | -18.1 | 2020 | 2028 | 8 |  | 170.1 | 196.8 | 177.9 | MOUNTAIN ISLAND | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 177.9 | - | 134.3 | 75.5 | 39.1 | 21.9 | - | 95.5 | 97.4 | 81.1 | 93.9 | 93.8 | 87.6 | 73
CAT1GM | CAT2 | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 108.3 | 108.3 | - | 119.2 | 110.1 | 591 | 108.3 | - | 102.3 | 94.4 | 692 | -15.7 | 2018 | 2017 | -1 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 92.9 | 85.7 | 26.3 | 24.4 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
CAT1GM | CAT2 | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 125.6 | 125.6 | - | 130.8 | 104.1 | 591 | 125.6 | - | 111.8 | 89 | 692 | -15.1 | 2018 | 2021 | 3 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 125.6 | - | 92.9 | 74 | 37.9 | 30.1 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
CAT1GM | CAT2 | - | - | - | - | - | 648 | REAMES R | 10590 | GERDAU W | 1 | 648-10590-1 | 91.2 | 91.2 | - | 100.6 | 110.3 | 591 | 91.2 | - | 87.7 | 96.2 | 692 | -14.1 | 2018 | 2016 | -2 |  | 91.2 | 112.3 | 91.2 | REAMES RD. RET. TAP | 100 kV Line | 106 | 130.6 | 106 | 91.2 | - | 98.5 | 108 | 2.1 | 2.3 | - | 106.2 | 110.3 | 85.9 | 104.8 | 105.9 | 105.6 | 84.9
CAT1GM | CAT2 | - | - | - | - | - | 538 | 6HARRISB | 2625 | HARRI 4 | 4 | 538-2625-4 | 500 | 500 | - | 452.6 | 90.5 | 591 | 500 | - | 384.6 | 76.9 | 692 | -13.6 | 2025 | 2030 | 5 |  | 246.4 | 275.4 | 268.5 | HARRISBURG TIE 04 | 230/100/44 kV Transformer | 246.4 | 275.4 | 268.5 | 268.5 | - | 205.4 | 76.5 | 247.2 | 14 | - | 83.1 | 90.5 | 83.1 | 99.8 | 83 | 83.6 | 79.7
CAT1GM | CAT2 | - | - | - | - | - | 600 | HARRISBG | 2625 | HARRI 4 | 4 | 600-2625-4 | 500 | 500 | - | 452.6 | 90.5 | 591 | 500 | - | 384.5 | 76.9 | 692 | -13.6 | 2025 | 2030 | 5 |  | 246.4 | 275.4 | 268.5 | HARRISBURG TIE 04 | 230/100/44 kV Transformer | 246.4 | 275.4 | 268.5 | 268.5 | - | 205.4 | 76.5 | 247.2 | 14 | - | 83.1 | 90.5 | 83.1 | 97.4 | 83 | 83.6 | 79.7
CAT1GM | CAT2 | - | - | - | - | - | 1927 | 1CATAWBA | 1934 | 1COMM/SC | 1 | 1927-1934-1 | 44.7 | 44.7 | - | 40.5 | 90.8 | 591 | 44.7 | - | 34.5 | 77.3 | 692 | -13.5 | 2025 | 2030 | 5 |  | 44.6532 | 49.2 | 44.6532 | TERRELL | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 29.9 | 67 | 10.6 | 23.8 | 87.7 | 87.7 | 90.8 | 79.1 | 86.4 | 87.2 | 87.1 | 78
BEL1GM | BEL2 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 114 | 111 | 591 | 102.7 | - | 100.4 | 97.8 | 692 | -13.2 | 2018 | 2015 | -3 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
BEL1GM | BEL2 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 108.7 | 105.9 | 591 | 102.7 | - | 95.9 | 93.4 | 692 | -12.5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
CAT1GM | CAT2 | - | - | - | - | - | 1727 | 1LANDO T | 1733 | 1LANDORT | 1 | 1727-1733-1 | 40 | 40 | - | 36 | 90 | 591 | 40 | - | 31.1 | 77.7 | 692 | -12.3 | 2025 | 2029 | 4 |  | - | - | - | - | - | - | - | - | 40 | - | 23.5 | 58.7 | 12.5 | 31.3 | 84.3 | 84.3 | 90 | 84 | 83.5 | 84.2 | 84 | 83.3
CAT1GM | CAT2 | - | - | - | - | - | 600 | HARRISBG | 601 | HCKRY GR | 1 | 600-601-1 | 125.6 | 125.6 | - | 130.3 | 103.7 | 591 | 125.6 | - | 114.9 | 91.5 | 692 | -12.2 | 2018 | 2019 | 1 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 125.6 | - | 97.5 | 77.7 | 32.8 | 26 | - | 96.1 | 103.7 | 88.9 | 96.9 | 97.4 | 93.9 | 84.7
CAT1GM | CAT2 | - | - | - | - | - | 627 | MONROE | 3627 | MONROE2 | 1 | 627-3627-1 | 207.8 | 207.8 | - | 193 | 92.9 | 591 | 207.8 | - | 168 | 80.9 | 692 | -12 | 2023 | 2027 | 4 |  | 207.8 | 207.8 | 207.8 | MONROE MAIN | High Side 100\44 kV Xfmr Breaker | 0 | 0 | 0 | 207.8 | - | 181.9 | 87.6 | 11.1 | 5.3 | 89 | 89 | 92.9 | 88.7 | 87.9 | 88.9 | 88.7 | 87.7
BEL1GM | BEL2 | - | - | - | - | - | 611 | LAKEWOOD | 10555 | BELHAV W | 1 | 611-10555-1 | 177.9 | 177.9 | - | 173.4 | 97.5 | 591 | 177.9 | - | 153.1 | 86 | 692 | -11.5 | 2020 | 2023 | 3 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
BEL1GM | BEL2 | - | - | - | - | - | 673 | THRIFT T | 10555 | BELHAV W | 1 | 673-10555-1 | 177.9 | 177.9 | - | 173.4 | 97.5 | 591 | 177.9 | - | 153.1 | 86 | 692 | -11.5 | 2020 | 2023 | 3 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
CAT1GM | CAT2 | - | - | - | - | - | 635 | OAKBORO | 10554 | BEAVER B | 1 | 635-10554-1 | 183.9 | 183.9 | - | 182.8 | 99.4 | 591 | 174.2 | - | 153.6 | 88.2 | 692 | -11.2 | 2019 | 2025 | 6 |  | 174.2 | 204.7 | 174.2 | ROCKY RIVER BL | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 173.3 | - | 146.2 | 84.4 | 36.6 | 15 | - | 87.9 | 99.4 | 79.1 | 91.4 | 87.5 | 88.9 | 75.3
CAT1GM | CAT2 | - | - | - | - | - | 663 | STELCK R | 684 | WESTNHSW | 1 | 663-684-1 | 102.7 | 102.7 | - | 97.2 | 94.6 | 591 | 102.7 | - | 85.8 | 83.5 | 692 | -11.1 | 2022 | 2025 | 3 |  | 102.7 | 113.1 | 102.7 | WESTINGHOUSE TAP LINE WH | 100 kV Line | 102.7 | 113.1 | 102.7 | 102.7 | - | 76.7 | 74.7 | 20.5 | 19.9 | - | 90.6 | 94.6 | 82.1 | 89.7 | 90.5 | 90.5 | 81.3
BAD1GM | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 110.2 | 107.3 | 1182 | 102.7 | - | 98.8 | 96.2 | 1384 | -11.1 | 2018 | 2016 | -2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 26 | 25.3 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
BEL1GM | BEL2 | - | - | - | - | - | 555 | BELHAVEN | 611 | LAKEWOOD | 1 | 555-611-1 | 177.9 | 177.9 | - | 168.4 | 94.7 | 591 | 177.9 | - | 148.8 | 83.7 | 692 | -11 | 2022 | 2025 | 3 |  | 177.9 | 196.8 | 177.9 | RIVERBEND | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 177.9 | - | 122 | 68.6 | 46.4 | 26.1 | - | 91.9 | 94.7 | 82.3 | 93.3 | 94 | 94.3 | 82.1
MCG1GM | ALL5 | - | - | - | - | - | 385 | NEWPORT | 10119 | ROCK H7 | 2 | 385-10119-2 | 196.8 | 196.8 | - | 196.7 | 100 | 591 | 196.8 | - | 175.1 | 89 | 692 | -11 | 2018 | 2021 | 3 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | 196.8 | - | 129.8 | 65.9 | 66.9 | 34.1 | - | 94.3 | 100 | 80.6 | 97.3 | 93.3 | 93.9 | 74.1
CAT1GM | CAT2 | - | - | - | - | - | 437 | UNEMC 12 | 635 | OAKBORO | 1 | 437-635-1 | 183.9 | 183.9 | - | 186.3 | 101.3 | 591 | 174.2 | - | 157.3 | 90.3 | 692 | -11 | 2018 | 2023 | 5 |  | 174.2 | 204.7 | 174.2 | ROCKY RIVER WH | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 173.3 | - | 122.2 | 70.5 | 64.1 | 30.8 | - | 90 | 101.3 | 80.9 | 92.3 | 89.6 | 91 | 77.1
CAT1GM | CAT2 | - | - | - | - | - | 618 | MATTHEWS | 679 | STUMPT_T | 1 | 618-679-1 | 240.7 | 240.7 | - | 222.9 | 92.6 | 591 | 240.7 | - | 196.5 | 81.7 | 692 | -10.9 | 2023 | 2026 | 3 |  | 240.7 | 284.9 | 240.7 | STUMPTOWN TAP LINE | 100 kV Line | 250.4472 | 312.2796 | 250.4472 | 240.7 | - | 153.1 | 63.6 | 69.8 | 29 | 88.8 | 88.8 | 92.6 | 74.7 | 87.7 | 88.6 | 88.4 | 73.9
CAT1GM | CAT2 | - | - | - | - | - | 600 | HARRISBG | 10601 | HIC GRO | 1 | 600-10601-1 | 125.6 | 125.6 | - | 115.4 | 91.9 | 591 | 125.6 | - | 101.8 | 81.1 | 692 | -10.8 | 2024 | 2027 | 3 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | - | - | - | - | - | - | 89.7 | 84.2 | 91.9 | 77.9 | 85.5 | 85.6 | 82.6 | 73.8
BUC5GM | BUC6 | - | - | - | - | - | 536 | 6BUCK | 561 | BUCK TIE | A4 | 536-561-A4 | 547.9 | 547.9 | - | 502.3 | 91.7 | 591 | 547.9 | - | 443.1 | 80.9 | 690 | -10.8 | 2024 | 2027 | 3 |  | 509 | 584.2 | 547.9 | BUCK TIE AT4 | 230/100 kV Transformer | 509 | 584.2 | 547.9 | 547.9 | - | 336.1 | 61.3 | 166.2 | 30.4 | - | 91.9 | 91.7 | 79.6 | 91.3 | 92.5 | 86.5 | 74.7
MCG1GM | ALL5 | - | - | - | - | - | 385 | NEWPORT | 417 | WYLIE HY | 1 | 385-417-1 | 196.8 | 196.8 | - | 190.4 | 96.7 | 591 | 196.8 | - | 169.3 | 86 | 692 | -10.7 | 2021 | 2023 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | 196.8 | - | 126.1 | 64.1 | 64.3 | 32.6 | - | 91.1 | 96.7 | 77.8 | 94.1 | 90.1 | 90.7 | 71.4
CAT1GM | CAT2 | - | - | - | - | - | 381 | LNCST RT | 392 | RED ROSE | 1 | 381-392-1 | 58.5 | 58.5 | - | 54.3 | 92.9 | 591 | 58.5 | - | 48.2 | 82.4 | 692 | -10.5 | 2023 | 2026 | 3 |  | 58.5 | 71.2 | 58.5 | MONROE BL | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | - | 44.6 | 76.3 | 9.7 | 16.6 | 88.7 | 88.7 | 92.9 | 72.7 | 87.8 | 88.6 | 88.4 | 72
MCG1GM | ALL5 | - | - | - | - | - | 417 | WYLIE HY | 10119 | ROCK H7 | 2 | 417-10119-2 | 196.8 | 196.8 | - | 177.8 | 90.4 | 590 | 196.8 | - | 157.9 | 80.2 | 692 | -10.2 | 2025 | 2027 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | 196.8 | - | 119.3 | 60.6 | 58.5 | 29.8 | - | 84.8 | 90.4 | 72.4 | 88.7 | 83.8 | 84.4 | 66
CAT1GM | CAT2 | - | - | - | - | - | 600 | HARRISBG | 622 | MINE SFT | 1 | 600-622-1 | 132.2 | 132.2 | - | 119.9 | 90.7 | 591 | 132.2 | - | 106.6 | 80.6 | 692 | -10.1 | 2025 | 2027 | 2 |  | 132.2 | 163.5 | 132.2 | FERRELL BL | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | 132.2 | - | 93.1 | 70.4 | 26.8 | 20.3 | 88.2 | 88.2 | 90.7 | 71 | 87 | 88 | 87.8 | 70.2
CAT1GM | CAT2 | - | - | - | - | - | 1989 | 1LONVIEW | 2022 | 1QUAKER | 1 | 1989-2022-1 | 38.1 | 38.1 | - | 35.3 | 92.6 | 591 | 38.1 | - | 31.4 | 82.5 | 692 | -10.1 | 2023 | 2026 | 3 |  | 38.1 | 41.7 | 38.1 | PONS | 44 kV Line | 0 | 0 | 0 | 38.1 | - | 27.9 | 73.3 | 7.4 | 19.3 | - | 90.1 | 92.6 | 82 | 89 | 89.6 | 89.6 | 81.2
MAR3GM | MAR4 | - | - | - | - | - | 928 | JESUPTWN | 943 | N GREENS | 1 | 928-943-1 | 177.9 | 177.9 | - | 180 | 101.2 | 591 | 177.9 | - | 162.2 | 91.2 | 692 | -10 | 2018 | 2019 | 1 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 163.5 | - | 147.1 | 90 | 32.9 | 11.2 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
OCO1GM | OCO2 | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 30 | 30 | - | 29.3 | 97.6 | 1182 | 30 | - | 26.4 | 87.9 | 1384 | -9.7 | 2020 | 2022 | 2 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 30 | - | 25.7 | 85.7 | 3.6 | 11.9 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
CAT1GM | CAT2 | - | - | - | - | - | 1545 | 1PETRS+C | 1621 | 1CLF_THY | 1 | 1545-1621-1 | 44.7 | 44.7 | - | 40.9 | 91.5 | 591 | 44.7 | - | 36.7 | 82 | 692 | -9.5 | 2024 | 2026 | 2 |  | 44.7 | 49.2 | 44.7 | THICKETTY | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 32.6 | 73 | 8.3 | 18.5 | 89.5 | 89.5 | 91.5 | 81.1 | 88.8 | 89.5 | 89.3 | 80.5
CAT1GM | CAT2 | - | - | - | - | - | 1554 | 1RRDON T | 1621 | 1CLF_THY | 1 | 1554-1621-1 | 44.7 | 44.7 | - | 40.9 | 91.5 | 591 | 44.7 | - | 36.7 | 82 | 692 | -9.5 | 2024 | 2026 | 2 |  | 44.7 | 49.2 | 44.7 | THICKETTY | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 32.6 | 73 | 8.3 | 18.5 | 89.5 | 89.5 | 91.5 | 81.1 | 88.8 | 89.5 | 89.3 | 80.5
MCG1GM | CLI5 | - | - | - | - | - | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 254-324-1 | 125.6 | 125.6 | - | 129.9 | 103.4 | 1182 | 125.6 | - | 118.1 | 94 | 1384 | -9.4 | 2018 | 2017 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 125.6 | - | 106.4 | 84.7 | 23.5 | 18.7 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
CAT1GM | CAT2 | - | - | - | - | - | 1291 | 1JPS SLA | 1352 | 1TIGERVT | 1 | 1291-1352-1 | 25.8 | 25.8 | - | 24.4 | 94.8 | 591 | 25.8 | - | 22 | 85.4 | 692 | -9.4 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 20.5 | 79.5 | 3.9 | 15.3 | - | 93.4 | 94.8 | 76.6 | 92.5 | 93.5 | 93 | 76
CAT1GM | CAT2 | - | - | - | - | - | 1280 | 1HEND MN | 1295 | 1KANUGA | 1 | 1280-1295-1 | 25.8 | 25.8 | - | 24.7 | 95.7 | 591 | 25.8 | - | 22.3 | 86.6 | 692 | -9.1 | 2021 | 2023 | 2 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.4 | 83 | 3.3 | 12.7 | - | 94.5 | 95.7 | 77.6 | 94.5 | 94.9 | 94.7 | 77.7
CAT1GM | CAT2 | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37.2 | 93.1 | 591 | 40 | - | 33.6 | 84 | 692 | -9.1 | 2023 | 2024 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 30.7 | 76.7 | 6.5 | 16.4 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
CAT1GM | CAT2 | - | - | - | - | - | 1271 | 1GEN ELE | 1280 | 1HEND MN | 1 | 1271-1280-1 | 25.8 | 25.8 | - | 24.7 | 95.6 | 591 | 25.8 | - | 22.3 | 86.5 | 692 | -9.1 | 2021 | 2023 | 2 |  | 25.8 | 31.3 | 25.8 | HENDERSONVILLE #1 | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.4 | 83 | 3.3 | 12.6 | - | 94.5 | 95.6 | 77.6 | 94.4 | 94.9 | 94.7 | 77.7
CAT1GM | CAT2 | - | - | - | - | - | 2413 | 1AO SMIT | 2456 | 1WLTR KI | 1 | 2413-2456-1 | 40 | 40 | - | 36.1 | 90.3 | 591 | 40 | - | 32.5 | 81.4 | 692 | -8.9 | 2025 | 2026 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 29.6 | 73.9 | 6.5 | 16.4 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
BEL1GM | BEL2 | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 128 | 128 | - | 123 | 96.1 | 591 | 128 | - | 111.6 | 87.2 | 692 | -8.9 | 2021 | 2022 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 100.7 | 78.6 | 22.3 | 17.5 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
CAT1GM | CAT2 | - | - | - | - | - | 1309 | 1MARIETA | 1322 | 1MRRTTA | 1 | 1309-1322-1 | 44.7 | 44.7 | - | 41.9 | 93.9 | 591 | 44.7 | - | 38 | 85.2 | 692 | -8.7 | 2022 | 2024 | 2 |  | 44.6532 | 49.149 | 44.6532 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 35.4 | 79.3 | 6.5 | 14.6 | - | 92.6 | 93.9 | 83.7 | 91.7 | 92.7 | 92.3 | 83.1
CAT1GM | CAT2 | - | - | - | - | - | 189 | MICH_PRI | 195 | SHADY GR | 1 | 189-195-1 | 126.4 | 126.4 | - | 114.7 | 90.7 | 591 | 126.4 | - | 103.8 | 82.1 | 692 | -8.6 | 2025 | 2026 | 1 |  | 126.436 | 139.426 | 126.436 | GREENBRIAR BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | 89.8 | 89.8 | 90.7 | 81.3 | 88.8 | 89.8 | 89.2 | 80.4
CAT1GM | CAT2 | - | - | - | - | - | 894 | GILBRTHT | 10968 | TROLNGWB | 1 | 894-10968-1 | 118.8 | 118.8 | - | 111.5 | 93.9 | 591 | 118.8 | - | 101.3 | 85.3 | 692 | -8.6 | 2022 | 2024 | 2 |  | 118.8 | 130.8 | 118.8 | SWEPSONVILLE BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 118.8 | - | 91.4 | 77 | 20.1 | 16.9 | - | 93.8 | 93.9 | 84.9 | 94.5 | 94.6 | 94.5 | 85.4
CAT1GM | CAT2 | - | - | - | - | - | 195 | SHADY GR | 10181 | MOONVI W | 1 | 195-10181-1 | 126.4 | 126.4 | - | 119.7 | 94.7 | 591 | 126.4 | - | 109 | 86.3 | 692 | -8.4 | 2022 | 2023 | 1 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 94.9 | 75.1 | 24.8 | 19.6 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
CAT1GM | CAT2 | - | - | - | - | - | 10180 | MICHMV W | 10181 | MOONVI W | 1 | 10180-10181-1 | 126.4 | 126.4 | - | 119.7 | 94.7 | 591 | 126.4 | - | 109.1 | 86.3 | 692 | -8.4 | 2022 | 2023 | 1 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 94.9 | 75.1 | 24.8 | 19.6 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
CAT1GM | CAT2 | - | - | - | - | - | 103 | 3M TAP | 10180 | MICHMV W | 1 | 103-10180-1 | 126.1 | 126.1 | - | 119.7 | 94.9 | 591 | 126.1 | - | 109.1 | 86.5 | 692 | -8.4 | 2022 | 2023 | 1 |  | 126.1 | 139.4 | 126.1 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.1 | - | 94.9 | 75.3 | 24.8 | 19.6 | - | 93.8 | 94.9 | 84.7 | 92.6 | 93.9 | 93.1 | 83.7
CAT1GM | CLI5 | - | - | - | - | - | 1331 | 1PENROS | 1335 | 1PISGAH | 1 | 1331-1335-1 | 25.8 | 25.8 | - | 23.8 | 92.1 | 591 | 25.8 | - | 21.6 | 83.9 | 692 | -8.2 | 2024 | 2025 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 19.8 | 76.8 | 4 | 15.3 | - | 91.7 | 92.1 | 75.4 | 91.5 | 92 | 91.7 | 75.2
OCO1GM | OCO2 | - | - | - | - | - | 1030 | 1BLREC 7 | 1206 | 1BEACON | 1 | 1030-1206-1 | 31 | 31 | - | 28.8 | 92.9 | 591 | 31 | - | 26.3 | 85 | 692 | -7.9 | 2023 | 2024 | 1 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | - | 24.8 | 79.9 | 4 | 13 | - | 91.1 | 92.9 | 85.4 | 90.4 | 91.2 | 91 | 84.8
OCO1GM | OCO2 | - | - | - | - | - | 1034 | 1BLREC13 | 1206 | 1BEACON | 1 | 1034-1206-1 | 31 | 31 | - | 28 | 90.5 | 591 | 31 | - | 25.6 | 82.7 | 692 | -7.8 | 2025 | 2025 | 0 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | - | 24.1 | 77.8 | 3.9 | 12.7 | 88.7 | 88.7 | 90.5 | 83.2 | 88 | 88.7 | 88.6 | 82.5
CAT1GM | CAT2 | - | - | - | - | - | 164 | HORSESHO | 2471 | NIXRDTAP | 1 | 164-2471-1 | 126.4 | 126.4 | - | 121 | 95.7 | 591 | 126.4 | - | 111.2 | 88 | 692 | -7.7 | 2021 | 2022 | 1 |  | 126.4 | 138.6 | 126.4 | ECHO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 22.2 | 17.6 | - | 89.6 | 95.7 | 82 | 95.7 | 88.5 | 89.4 | 77.4
CAT1GM | MCG1 | - | - | - | - | - | 1382 | 1NEWBERY | 1390 | 1NWBYC3 | 1 | 1382-1390-1 | 22 | 22 | - | 20 | 90.7 | 591 | 22 | - | 18.3 | 83.1 | 692 | -7.6 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | 22 | - | 17.8 | 81 | 2.2 | 9.7 | - | 90.2 | 90.7 | 90.2 | 89.5 | 90.2 | 89.9 | 89.6
BEL1GM | BEL2 | - | - | - | - | - | 925 | IMPERALW | 10944 | NORTEL W | 1 | 925-10944-1 | 130.6 | 130.6 | - | 120 | 91.9 | 591 | 130.6 | - | 110.1 | 84.3 | 692 | -7.6 | 2024 | 2024 | 0 |  | 130.6 | 161.4 | 130.6 | PANTHER WH | 100 kV Line | 130.5928 | 161.4224 | 130.5928 | 130.6 | - | 106.3 | 81.4 | 13.7 | 10.5 | - | 91.6 | 91.9 | 73.9 | 92.2 | 92.4 | 92.3 | 74.3
BEL1GM | BEL2 | - | - | - | - | - | 2271 | 1PKDL25T | 2356 | 1SRYYDN3 | 1 | 2271-2356-1 | 25.8 | 25.8 | - | 23.3 | 90.4 | 591 | 25.8 | - | 21.6 | 83.6 | 692 | -6.8 | 2025 | 2025 | 0 |  | 25.8 | 31.3 | 25.8 | ROCKFORD | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 20.9 | 81.1 | 2.4 | 9.3 | 88.9 | 88.9 | 90.4 | 73.1 | 88.6 | 89 | 88.9 | 72.8
MAR3GM | MCG1 | - | - | - | - | - | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737-779-1 | 126.4 | 126.4 | - | 120.1 | 95 | 591 | 126.4 | - | 112 | 88.6 | 692 | -6.4 | 2022 | 2021 | -1 |  | 126.4 | 139.4 | 126.4 | MAYO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 79.9 | 63.2 | 40.2 | 31.8 | - | 93 | 95 | 85.1 | 95.6 | 92.7 | 93.5 | 84
MCG1GM | CLI5 | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 21.2 | 95.5 | 591 | 22.2 | - | 19.9 | 89.7 | 692 | -5.8 | 2021 | 2020 | -1 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.6 | 79 | 3.6 | 16.5 | - | 95.4 | 95.5 | 78.8 | 98 | 96.6 | 96 | 79.3
BEL1GM | BEL2 | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1777.2 | 93.3 | 1182 | 1904.3 | - | 1673.4 | 87.9 | 1384 | -5.4 | 2023 | 2022 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1564.4 | 82.1 | 212.8 | 11.2 | 95 | 85.5 | 93.3 | 80.5 | 88.7 | 90.2 | 87.2 | 75.1
CAT1GM | CAT2 | - | - | - | - | - | 151 | ESTES TB | 195 | SHADY GR | 1 | 151-195-1 | 103.4 | 103.4 | - | 117.2 | 113.4 | 475 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 105.6 | 113.4 | 111.7 | - | 106.8 | 52.4 | 51.6
CAT1GM | CAT2 | - | - | - | - | - | 124 | BAINBRIG | 195 | SHADY GR | 1 | 124-195-1 | 103.9 | 103.9 | - | 93.9 | 90.4 | 425 | - | - | - | - | - | - | 2025 | - | - |  | 103.9 | 103.9 | 103.9 | BAINBRIDGE | 100 kV Line | 126.436 | 139.426 | 126.436 | 103.9 | - | 55.8 | 53.7 | 38.1 | 36.7 | - | 83.3 | 90.4 | 84.8 | - | 84.8 | 50.6 | -
BEL1GM | BEL2 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 117 | 114 | 591 | 102.7 | - | 103 | 100.3 | 692 | -13.7 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
CAT1GM | CAT2 | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 108.3 | 108.3 | - | 127.4 | 117.6 | 591 | 108.3 | - | 109 | 100.6 | 692 | -17 | 2018 | 2013 | -5 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 92.9 | 85.8 | 34.5 | 31.8 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
BAD1GM | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 115.3 | 112.3 | 591 | 102.7 | - | 103.4 | 100.7 | 692 | -11.6 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.5 | 26.4 | 25.8 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 18 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 2 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
CAT1GM | BADX | - | - | - | - | - | 41 | LEE | 151 | ESTES TB | 1 | 41-151-1 | 103.4 | 103.4 | - | 148 | 143.1 | 48 | 103.4 | - | 73.7 | 71.3 | 50 | -71.8 | 2018 | 2035 | 17 |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | 103.4 | - | 77.1 | 74.5 | 70.9 | 68.6 | - | 137.3 | 145.8 | 143.1 | 93.2 | 138.5 | 84.8 | 83.5
CAT1GM | BADX | - | - | - | - | - | 41 | LEE | 195 | SHADY GR | 1 | 41-195-1 | 103.4 | 103.4 | - | 140 | 135.4 | 144 | 103.4 | - | 66.3 | 64.1 | 150 | -71.3 | 2018 | 2042 | 24 |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | 103.4 | - | 70.6 | 68.2 | 69.4 | 67.2 | - | 129.5 | 137.9 | 135.4 | 85 | 130.7 | 76.9 | 75.6
CAT1GM | BADX | - | - | - | - | - | 687 | WINECOFF | 10642 | POPLRT B | 1 | 687-10642-1 | 129.9 | 129.9 | - | 119.4 | 91.9 | 24 | 129.9 | - | 101.6 | 78.2 | 26 | -13.7 | 2024 | 2029 | 5 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | 129.9 | - | 79.5 | 61.2 | 39.9 | 30.7 | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
BEL1GM | BADX | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 110.8 | 110.8 | - | 111.8 | 100.9 | 24 | 110.8 | - | 96.8 | 87.3 | 26 | -13.6 | 2018 | 2022 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
BEL1GM | BADX | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 110.8 | 110.8 | - | 108.9 | 98.3 | 24 | 110.8 | - | 94.5 | 85.3 | 26 | -13 | 2020 | 2024 | 4 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
CAT1GM | BADX | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 118.6 | 118.6 | - | 120.4 | 101.5 | 24 | 118.6 | - | 106 | 89.3 | 26 | -12.2 | 2018 | 2021 | 3 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.6 | - | 88.2 | 74.4 | 32.2 | 27.1 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
BEL1GM | BADX | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 110.8 | 110.8 | - | 103.9 | 93.8 | 24 | 110.8 | - | 90.6 | 81.8 | 26 | -12 | 2023 | 2026 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
BEL1GM | BADX | - | - | - | - | - | 304615 | BARN CRK | 304616 | BARNARD | 1 | 304615-304616-1 | 150 | 150 | - | 137.6 | 91.8 | 24 | 150 | - | 120.4 | 80.3 | 26 | -11.5 | 2024 | 2027 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
CAT1GM | BADX | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 129.9 | 129.9 | - | 123.5 | 95.1 | 24 | 129.9 | - | 108.7 | 83.7 | 26 | -11.4 | 2022 | 2025 | 3 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 129.9 | - | 88.2 | 67.9 | 35.3 | 27.2 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
CAT1GM | BADX | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 118.6 | 118.6 | - | 112.8 | 95.1 | 24 | 118.6 | - | 99.5 | 83.9 | 26 | -11.2 | 2022 | 2025 | 3 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.6 | - | 88.2 | 74.3 | 24.6 | 20.8 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
JOC1GM | BADX | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 113.1 | 113.1 | - | 113.7 | 100.6 | 24 | 113.1 | - | 101.8 | 90 | 26 | -10.6 | 2018 | 2020 | 2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 87.1 | 77 | 26.6 | 23.6 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
JOC1GM | BADX | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 113.1 | 113.1 | - | 108.6 | 96 | 48 | 113.1 | - | 97.1 | 85.9 | 52 | -10.1 | 2021 | 2023 | 2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 82.4 | 72.9 | 26.2 | 23.1 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
CAT1GM | BADX | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 30 | 30 | - | 29.1 | 97.1 | 48 | 30 | - | 26.3 | 87.7 | 52 | -9.4 | 2020 | 2022 | 2 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 30 | - | 25.6 | 85.4 | 3.5 | 11.7 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
CAT1GM | BADX | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37 | 92.5 | 24 | 40 | - | 33.4 | 83.6 | 26 | -8.9 | 2023 | 2025 | 2 |  | - | - | - | - | - | - | - | - | 40 | - | 30.5 | 76.2 | 6.5 | 16.3 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
MAR3GM | BADX | - | - | - | - | - | 928 | JESUPTWN | 943 | N GREENS | 1 | 928-943-1 | 196.8 | 196.8 | - | 177.1 | 90 | 24 | 196.8 | - | 160 | 81.3 | 26 | -8.7 | 2025 | 2027 | 2 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 180.5 | - | 145.1 | 80.4 | 32 | 9.6 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
MCG1GM | BADX | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 129.9 | 129.9 | - | 122.2 | 94.1 | 24 | 129.9 | - | 111.2 | 85.6 | 26 | -8.5 | 2022 | 2023 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 129.9 | - | 100.1 | 77.1 | 22.1 | 17 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
CAT1GM | BADX | - | - | - | - | - | 1382 | 1NEWBERY | 1390 | 1NWBYC3 | 1 | 1382-1390-1 | 22 | 22 | - | 19.8 | 90.2 | 24 | 22 | - | 18.2 | 82.7 | 26 | -7.5 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | 22 | - | 17.7 | 80.6 | 2.1 | 9.6 | - | 90.2 | 90.7 | 90.2 | 89.5 | 90.2 | 89.9 | 89.6
CLI5GM | BADX | - | - | - | - | - | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 254-324-1 | 129.9 | 129.9 | - | 121.7 | 93.7 | 48 | 129.9 | - | 112.8 | 86.8 | 52 | -6.9 | 2023 | 2022 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 129.9 | - | 99.8 | 76.9 | 21.9 | 16.8 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
CAT1GM | BADX | - | - | - | - | - | 151 | ESTES TB | 195 | SHADY GR | 1 | 151-195-1 | 103.4 | 103.4 | - | 115.5 | 111.7 | 22 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 105.6 | 113.4 | 111.7 | - | 106.8 | 52.4 | 51.6
ALL5GM | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 72.7 | 145.4 | 48 | 50 | - | 52.4 | 104.8 | 52 | -40.6 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 198 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 56 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 254 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDYHAR1VRS | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304047 | WSPN115 TT 115.00 | 304406 | ST PAULS 115.00 | 1 | 304047-304406-1 | 119 | 119 | 104.8 | 130.7 | 109.3 | 427 | 119 | 75.7 | 96.1 | 80.7 | 43 | -28.6 | 2018 | 2027 | 9 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.3 | 84.3 | - | 88.1 | 109.3 | 91.1 | - | 92.2
STUDYHAR1VRS | SINGLE 146 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304099 | E18-POCO 115.00 | 304105 | FRANKLIN 115.00 | 1 | 304099-304105-1 | 170 | 170 | 49.9 | 166.6 | 105.4 | 13 | 170 | 18.7 | 122.2 | 78.2 | 13 | -27.2 | 2018 | 2029 | 11 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.9 | - | - | - | 105.4 | - | - | -
STUDYASH1VRS | AB_SHADBK2_L | 109 | 6SHADY G | 2675 | SHADY 2 | 2 | 41 | LEE 100.00 | 195 | SHADY GR 100.00 | 2 | 41-195-2 | 86.2 | 86.2 | 78.5 | 94 | 109.5 | 287 | 86.2 | 56.7 | 72.2 | 82.9 | 72 | -26.6 | 2018 | 2025 | 7 |  | 86.2 | 94.2 | 86.2 | LEE BL | 100 kV Line | 126.436 | 139.426 | 126.436 | 86.2 | 64.8 | 77.9 | 86.7 | 16.1 | 22.8 | - | - | - | - | 109.5 | - | - | -
STUDYASH1VRS | AB_SHADBK2_L | 109 | 6SHADY G | 2675 | SHADY 2 | 2 | 41 | LEE 100.00 | 195 | SHADY GR 100.00 | 3 | 41-195-3 | 86.2 | 86.2 | 78.5 | 94 | 109.5 | 300 | 86.2 | 56.7 | 72.2 | 82.9 | 73 | -26.6 | 2018 | 2025 | 7 |  | 86.2 | 94.2 | 86.2 | LEE WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 86.2 | 64.8 | 77.9 | 86.7 | 16.1 | 22.8 | - | - | - | - | 109.5 | - | - | -
STUDYROX4VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 611 | LAKEWOOD 100.00 | 10680 | BFORDRET 100.00 | 1 | 611-10680-1 | 110.8 | 110.8 | 113.7 | 135.1 | 120.5 | 309 | 110.8 | 90.3 | 107.2 | 94.4 | 193 | -26.1 | 2018 | 2017 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
STUDYHAR1VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 611 | LAKEWOOD 100.00 | 652 | RIVERBEN 100.00 | 2 | 611-652-2 | 110.8 | 110.8 | 110.7 | 132.1 | 117.9 | 296 | 110.8 | 88 | 104.8 | 92.3 | 147 | -25.6 | 2018 | 2019 | 1 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 83 | 65.4 | 76.3 | 90.6 | 55.8 | 27.3 | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
STUDYROX4VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 652 | RIVERBEN 100.00 | 10680 | BFORDRET 100.00 | 1 | 652-10680-1 | 110.8 | 110.8 | 105.6 | 126.7 | 113.2 | 306 | 110.8 | 84.4 | 101.2 | 88.7 | 128 | -24.5 | 2018 | 2021 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 177 | MARIETTA 100.00 | 10135 | DANIELWH 100.00 | 1 | 177-10135-1 | 86.6 | 86.6 | 17.9 | 88.1 | 101.1 | 10 | 86.6 | 13.9 | 68 | 77 | 1 | -24.1 | 2018 | 2030 | 12 |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER WH | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | 83.4 | - | - | - | 101.1 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 177 | MARIETTA 100.00 | 230 | BLREC23 100.00 | 1 | 177-230-1 | 86.6 | 86.6 | 17.7 | 87.6 | 100.9 | 9 | 86.6 | 13.9 | 67.2 | 77 | 1 | -23.9 | 2018 | 2030 | 12 |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER WH | 100 kV Line | 86.6 | 105.9984 | 86.6 | - | - | - | - | - | - | 83.3 | - | - | - | 100.9 | - | - | -
STUDYROX4VRS | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 718 | 6SADLER 230.00 | 2679 | SADLE 3 1.0000 | 3 | 718-2679-3 | 553.7 | 553.7 | 326.7 | 562.1 | 101.5 | 13 | 553.7 | 249.7 | 431 | 77.8 | 13 | -23.7 | 2018 | 2029 | 11 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 246.8 | 436.1 | 78.8 | 126 | 22.7 | 116.8 | - | 75.1 | 64.3 | 101.5 | - | 70.9 | 56
STUDYROX4VRS | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 718 | 6SADLER 230.00 | 2673 | SADLE 4 1.0000 | 4 | 718-2673-4 | 553.7 | 553.7 | 336.5 | 547.9 | 99 | 13 | 553.7 | 259 | 417.5 | 75.4 | 13 | -23.6 | 2019 | 2031 | 12 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 256 | 423.7 | 76.5 | 124.2 | 22.5 | 114.4 | 70.7 | 76.9 | 61.5 | 99 | 72.3 | 72.7 | 53.8
STUDYROX4VRS | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 790 | SADLER 100.00 | 2673 | SADLE 4 1.0000 | 4 | 790-2673-4 | 553.7 | 553.7 | 336.5 | 547.9 | 99 | 13 | 553.7 | 259 | 417.5 | 75.4 | 13 | -23.6 | 2019 | 2031 | 12 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 256 | 423.7 | 76.5 | 124.2 | 22.5 | 114.4 | 71.1 | 77.3 | 61.8 | 99 | 72.7 | 73.1 | 54.1
STUDYHAR1VRS | SINGLE 462 | 304378 | RICH230 | 304415 | RAEFORD | 1 | 304047 | WSPN115 TT 115.00 | 304432 | PA-LUMB#2 115.00 | 1 | 304047-304432-1 | 133 | 133 | 101.2 | 131.5 | 101.7 | 272 | 133 | 72.1 | 103.3 | 78.9 | 24 | -22.8 | 2018 | 2028 | 10 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.8 | 75.6 | - | 79.5 | 101.7 | 78.6 | - | 81.1
STUDYRCH1VRS | INDIANTRAB | 627 | MONROE | 10531 | MONROC4B | 1 | 531 | MNROE_C4 100.00 | 10668 | STOUTS W 100.00 | 1 | 531-10668-1 | 167 | 167 | 124.8 | 177.5 | 110.5 | 313 | 205 | 125.7 | 179.5 | 88.2 | 29 | -22.3 | 2018 | 2013 | -5 |  | 102.7 | 113.1 | 102.7 | INDIAN TRAIL WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 110.2 | 135.4 | 121.2 | 42.1 | -10.7 | - | 76.6 | 77.3 | 74.8 | 110.5 | 78.7 | 77.4 | 75.2
STUDYBRN1VRS | SINGLE 718 | 304631 | MARION23 | 305001 | E1-CHAD | 1 | 304630 | MULLINS 115.00 | 304632 | MARION115 TT115.00 | 1 | 304630-304632-1 | 179 | 179 | 123.4 | 177.7 | 101.8 | 42 | 179 | 100.9 | 144.3 | 79.8 | 3 | -22 | 2018 | 2028 | 10 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89 | - | - | 62.8 | 101.8 | 71.7 | - | 71.3
STUDYASH1VRS | RIVBD100_CAP | 5652 | RIVERCAP | 652 | RIVERBEN | 1 | 642 | POPLR TN 100.00 | 687 | WINECOFF 100.00 | 1 | 642-687-1 | 125.6 | 125.6 | 105.5 | 116.3 | 94.9 | 221 | 125.6 | 85.3 | 94.2 | 73.3 | 39 | -21.6 | 2022 | 2033 | 11 |  | 120 | 129.9 | 125.6 | HOPEWHELL WH | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 91.4 | 97.1 | 85.2 | 94.9 | 90.5 | 87.3 | 81.6
STUDYASH1VRS | AB_SHADBK2_S | 105 | 6SHADYTW | 109 | 6SHADY G | 2 | 41 | LEE 100.00 | 151 | ESTES TB 100.00 | 1 | 41-151-1 | 103.4 | 103.4 | 81.6 | 96.2 | 93.2 | 221 | 103.4 | 60.6 | 75.3 | 71.9 | 4 | -21.3 | 2023 | 2034 | 11 |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | 103.4 | 66.5 | 78.3 | 73.9 | 17.9 | 19.3 | - | 137.3 | 145.8 | 143.1 | 93.2 | 138.5 | 84.8 | 83.5
STUDYASH1VRS | RIVBD100_CAP | 5652 | RIVERCAP | 652 | RIVERBEN | 1 | 687 | WINECOFF 100.00 | 10642 | POPLRT B 100.00 | 1 | 687-10642-1 | 125.6 | 125.6 | 114.3 | 124 | 101.1 | 221 | 125.6 | 93.6 | 102.8 | 80 | 125 | -21.1 | 2018 | 2028 | 10 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
STUDYASH1VRS | INMANK3 | 3260 | INMAN 2 | 1479 | 1INMAN | 3 | 1479 | 1INMAN 44.000 | 3260 | INMAN 2 100.00 | 1 | 1479-3260-1 | 25.3 | 25.3 | 20 | 25.4 | 100.3 | 65 | 23.6 | 18.7 | 18.7 | 79.3 | 38 | -21 | 2018 | 2032 | 14 |  | 23.6 | 26.2 | 25.3 | INMAN TIE 01 | 100/44 kV Transformer | 23.6 | 26.2 | 25.3 | 25.3 | 18.4 | 18.4 | 72.7 | 7 | 27.6 | - | 84.5 | 79.4 | 75.5 | 100.3 | 86 | 79.4 | 76
STUDYASH1VRS | RIVBD100_CAP | 5652 | RIVERCAP | 652 | RIVERBEN | 1 | 2259 | EASTFLDR 100.00 | 10642 | POPLRT B 100.00 | 1 | 2259-10642-1 | 126.7 | 126.7 | 112.2 | 120.7 | 100.3 | 221 | 126.7 | 92.3 | 101.3 | 79.3 | 69 | -21 | 2018 | 2028 | 10 |  | 126.4 | 139.4 | 126.7 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 93.7 | 103.4 | 85.7 | 100.3 | 92.9 | 93.5 | 82.3
STUDYHAR1VRS | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 382 | MCADENVL 100.00 | 647 | RANKIN T 100.00 | 1 | 382-647-1 | 177.9 | 177.9 | 147.4 | 167.9 | 93.9 | 437 | 177.9 | 115.7 | 134.5 | 74.1 | 28 | -19.8 | 2022 | 2032 | 10 |  | 170.1 | 196.8 | 177.9 | MOUNTAIN ISLAND | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 177.9 | 105.8 | 126.7 | 70.5 | 41.2 | 23.4 | - | 95.5 | 97.4 | 81.1 | 93.9 | 93.8 | 87.6 | 73
STUDYNAN1VRS | PISGHBK1 | 108 | 6PISGAH | 2665 | PISGA 1 | 1 | 108 | 6PISGAH 230.00 | 2666 | PISGA 2 1.0000 | 2 | 108-2666-2 | 239 | 239 | 152.9 | 231.6 | 96.9 | 57 | 239 | 123 | 184.7 | 77.3 | 13 | -19.6 | 2020 | 2030 | 10 |  | 239 | 239 | 239 | PISGAH TIE 02 | 230/100/44 kV Transformer | 258 | 288.4 | 281.1 | 239 | 115.5 | 173.9 | 72.8 | 57.7 | 24.1 | - | - | 62.2 | 58.6 | 96.9 | - | 61.9 | 58.3
STUDYNAN1VRS | PISGHBK1 | 108 | 6PISGAH | 2665 | PISGA 1 | 1 | 190 | PISGAH 100.00 | 2666 | PISGA 2 1.0000 | 2 | 190-2666-2 | 239 | 239 | 152.9 | 231.6 | 96.9 | 57 | 239 | 123 | 184.7 | 77.3 | 13 | -19.6 | 2020 | 2030 | 10 |  | 239 | 239 | 239 | PISGAH TIE 02 | 230/100/44 kV Transformer | 258 | 288.4 | 281.1 | 239 | 115.5 | 173.8 | 72.7 | 57.8 | 24.2 | - | - | 62.6 | 59 | 96.9 | - | 62.3 | 58.7
STUDYBRN1VRS | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 72.5 | 102.6 | 106.1 | 174 | 97 | 63 | 85 | 86.7 | 36 | -19.4 | 2018 | 2022 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.8 | - | - | 74.4 | 106.1 | 79.8 | - | 80
STUDYNAN1VRS | PISGHBK2 | 108 | 6PISGAH | 2666 | PISGA 2 | 2 | 108 | 6PISGAH 230.00 | 2665 | PISGA 1 1.0000 | 1 | 108-2665-1 | 239 | 239 | 149.6 | 229.3 | 95.9 | 40 | 239 | 120.6 | 183 | 76.6 | 13 | -19.3 | 2021 | 2030 | 9 |  | 239 | 239 | 239 | PISGAH TIE 01 | 230/100/44 kV Transformer | 249.6 | 279.3 | 272.2 | 239 | 113.2 | 171.8 | 71.9 | 57.5 | 24 | - | - | 61 | 57.4 | 95.9 | - | 60.7 | 57.1
STUDYNAN1VRS | PISGHBK2 | 108 | 6PISGAH | 2666 | PISGA 2 | 2 | 190 | PISGAH 100.00 | 2665 | PISGA 1 1.0000 | 1 | 190-2665-1 | 239 | 239 | 149.6 | 229.3 | 95.9 | 40 | 239 | 120.6 | 183 | 76.6 | 13 | -19.3 | 2021 | 2030 | 9 |  | 239 | 239 | 239 | PISGAH TIE 01 | 230/100/44 kV Transformer | 249.6 | 279.3 | 272.2 | 239 | 113.2 | 172.5 | 72.2 | 56.8 | 23.7 | - | - | 61.3 | 57.7 | 95.9 | - | 61 | 57.5
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 135 | DANIEL 100.00 | 182 | N GRNVLE 100.00 | 1 | 135-182-1 | 118.8 | 118.8 | 65.8 | 135.8 | 112.8 | 13 | 118.8 | 58.9 | 113.5 | 93.6 | 12 | -19.2 | 2018 | 2018 | 0 |  | 118.8 | 129.9 | 118.8 | DAVIDSON RIVER BL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.8 | 101.6 | 109.4 | 90 | 26.4 | 22.8 | - | - | 53 | - | 112.8 | - | 54.7 | -
STUDYHAR1VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 611 | LAKEWOOD 100.00 | 10555 | BELHAV W 100.00 | 1 | 611-10555-1 | 196.8 | 196.8 | 169.2 | 193.4 | 97.2 | 311 | 196.8 | 138.5 | 157.5 | 78.1 | 126 | -19.1 | 2020 | 2029 | 9 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
STUDYHAR1VRS | RIVERBENDB | 611 | LAKEWOOD | 555 | BELHAVEN | 1 | 673 | THRIFT T 100.00 | 10555 | BELHAV W 100.00 | 1 | 673-10555-1 | 196.8 | 196.8 | 168.4 | 192.4 | 97.2 | 304 | 196.8 | 138.3 | 157.3 | 78.1 | 120 | -19.1 | 2020 | 2029 | 9 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
STUDYVCS1VRS | BASE CASE | 0 |  | 0 |  |  | 465 | HICKORY 100.00 | 483 | NEWTON T 100.00 | 1 | 465-483-1 | 103.9 | 103.9 | 122.9 | 122.9 | 117.5 | 230 | 103.9 | 104.7 | 104.7 | 98.5 | 156 | -19 | 2018 | 2014 | -4 |  | 103.9 | 141.2 | 128 | MULL WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 141 | 97.1 | 132.1 | 92.7 | -9.2 | 24.8 | - | 117.8 | 103.4 | 86.4 | 117.5 | 121.1 | 98.4 | 86.4
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 182 | N GRNVLE 100.00 | 10135 | DANIELWH 100.00 | 1 | 182-10135-1 | 118.8 | 118.8 | 63.4 | 132.9 | 110.4 | 13 | 118.8 | 58 | 110.8 | 91.5 | 10 | -18.9 | 2018 | 2019 | 1 |  | 118.8 | 129.9 | 118.8 | DAVIDSON RIVER WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 129.9 | 23.1 | 95.1 | 71.6 | 37.8 | 38.8 | - | - | 50.9 | - | 110.4 | - | 52.7 | -
STUDYBRN1VRS | SINGLE 48 | 304035 | SUT 1-2F | 304545 | CASTLE H | 1 | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 2 | 304035-304545-2 | 131 | 131 | 79.1 | 138.5 | 103.9 | 80 | 131 | 54.1 | 113.8 | 85.4 | 18 | -18.5 | 2018 | 2023 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.1 | - | - | 54.2 | 103.9 | - | - | -
STUDYHAR1VRS | RIVERBENDW | 611 | LAKEWOOD | 10555 | BELHAV W | 1 | 555 | BELHAVEN 100.00 | 611 | LAKEWOOD 100.00 | 1 | 555-611-1 | 196.8 | 196.8 | 164.3 | 186.1 | 93.3 | 319 | 196.8 | 134.5 | 151.1 | 74.9 | 89 | -18.4 | 2023 | 2032 | 9 |  | 177.9 | 196.8 | 177.9 | RIVERBEND | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 196.8 | 103.7 | 144.9 | 72.5 | 41.2 | 20.8 | - | 91.9 | 94.7 | 82.3 | 93.3 | 94 | 94.3 | 82.1
STUDYASH1VRS | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 681 | WESTFORK 100.00 | 687 | WINECOFF 100.00 | 1 | 681-687-1 | 108.3 | 108.3 | 121.2 | 128.3 | 114.9 | 175 | 108.3 | 103.9 | 110.3 | 97.5 | 154 | -17.4 | 2018 | 2015 | -3 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | 81 | 88.2 | 81.8 | 40.1 | 33.1 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
STUDYHAR1VRS | CPL6 | 304183 | WAKE 500 | 304391 | CUMB500 | 1 | 304196 | ERWIN 230.00 | 304389 | P2-FAY EAST 230.00 | 1 | 304196-304389-1 | 478 | 478 | 330.1 | 441.5 | 94 | 224 | 478 | 266.8 | 368.2 | 77.6 | 10 | -16.4 | 2022 | 2029 | 7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 88.1 | - | - | 64.5 | 94 | 72.6 | - | 69.5
STUDYHAR1VRS | SINGLE 190 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 34.3 | 170.2 | 116.2 | 13 | 158 | 20.6 | 149.2 | 99.8 | 13 | -16.4 | 2018 | 2014 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.4 | - | - | - | 116.2 | - | - | -
STUDYRCH1VRS | FISHINGCKBS | 366 | FISHNG C | 2254 | BELTWNTP | 1 | 375 | GT FALL1 100.00 | 380 | LANCASTR 100.00 | 1 | 375-380-1 | 162.3 | 162.3 | 83.6 | 155.4 | 98.5 | 26 | 162.3 | 72.4 | 131.3 | 82.7 | 26 | -15.8 | 2019 | 2025 | 6 |  | 147.8 | 162.3 | 147.8 | FISHING CRK | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 162.3 | 68.6 | 122.8 | 76.6 | 32.6 | 21.9 | - | - | 58 | 51.7 | 98.5 | - | 57.2 | 50.9
STUDYHAR1VRS | FISHINGCKW | 380 | LANCASTR | 375 | GT FALL1 | 1 | 380 | LANCASTR 100.00 | 2254 | BELTWNTP 100.00 | 1 | 380-2254-1 | 172.3 | 172.3 | 95 | 158.3 | 94.1 | 13 | 172.3 | 77.2 | 132.6 | 78.4 | 13 | -15.7 | 2022 | 2029 | 7 |  | 172.3 | 172.3 | 172.3 | FISHING CRK | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 172.3 | 71.4 | 122.8 | 72 | 35.5 | 22.1 | - | - | 56.5 | 55.4 | 94.1 | - | 55.7 | 54.5
STUDYRCH1VRS | FISHINGCKW | 380 | LANCASTR | 375 | GT FALL1 | 1 | 366 | FISHNG C 100.00 | 2254 | BELTWNTP 100.00 | 1 | 366-2254-1 | 172.3 | 172.3 | 96.1 | 161.5 | 94 | 13 | 172.3 | 77.9 | 135 | 78.4 | 13 | -15.6 | 2022 | 2029 | 7 |  | 172.3 | 172.3 | 172.3 | FISHING CRK | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 172.3 | 75 | 127.4 | 73.8 | 34.1 | 20.2 | - | - | 56.4 | 55.4 | 94 | - | 55.7 | 54.5
STUDYNAN1VRS | SINGLE 878 | 304761 | I-SOUTHE | 304762 | ENKA SW | 1 | 304790 | VANDERBILT 115.00 | 304791 | W ASHEVILE 115.00 | 1 | 304790-304791-1 | 123 | 123 | 79.5 | 119.9 | 97.6 | 150 | 123 | 66.7 | 101.3 | 82 | 60 | -15.6 | 2020 | 2026 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.3 | - | - | 57.5 | 97.6 | - | - | 56.4
STUDYVCS1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 758 | MADISON 100.00 | 821 | DANVALYT 100.00 | 1 | 758-821-1 | 118.6 | 118.6 | 79.4 | 125.6 | 105.1 | 126 | 118.6 | 66.9 | 106.8 | 89.6 | 13 | -15.5 | 2018 | 2020 | 2 |  | 108.3 | 118.6 | 108.3 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 73.7 | 75.9 | 68.4 | 105.1 | 73.4 | 74.3 | 67.1
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 1 | 304035-304545-1 | 159 | 159 | 80.9 | 147.1 | 93.2 | 29 | 159 | 59.4 | 123.8 | 77.9 | 13 | -15.3 | 2023 | 2029 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.2 | - | - | - | 93.2 | - | - | 55
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 163 | HNDRSNVL 100.00 | 1 | 132-163-1 | 64.8 | 64.8 | 18.6 | 58.1 | 91.2 | 1 | 64.8 | 18.7 | 49.2 | 76.1 | 1 | -15.1 | 2024 | 2031 | 7 |  | 64.8 | 70.7 | 64.8 | HOGBACK | 100 kV Line | 69.6264 | 75.6884 | 69.6264 | - | - | - | - | - | - | - | - | - | - | 91.2 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 163 | HNDRSNVL 100.00 | 2 | 132-163-2 | 64.8 | 64.8 | 18.6 | 58.1 | 91.2 | 1 | 64.8 | 18.7 | 49.2 | 76.1 | 1 | -15.1 | 2024 | 2031 | 7 |  | 64.8 | 70.7 | 64.8 | HOGBACK | 100 kV Line | 69.6264 | 75.6884 | 69.6264 | - | - | - | - | - | - | - | - | - | - | 91.2 | - | - | -
STUDYHAR1VRS | SINGLE 647 | 304550 | CASTLE H | 304564 | SCOTT T | 1 | 304545 | CASTLE HAYNE115.00 | 305063 | E9-ELECTRIC 115.00 | 1 | 304545-305063-1 | 179 | 179 | 92 | 163.1 | 94.1 | 39 | 179 | 110.7 | 139.6 | 79.7 | 93 | -14.4 | 2022 | 2028 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.5 | - | - | 51.9 | 94.1 | - | - | 52.7
STUDYBTH1VRS | SINGLE 232 | 304182 | FALLS230 | 304185 | FALLS115 | 2 | 304182 | FALLS230 TT 230.00 | 304185 | FALLS115 TT 115.00 | 1 | 304182-304185-1 | 300 | 300 | 198.9 | 277.8 | 92.6 | 273 | 300 | 168.7 | 235.4 | 78.5 | 59 | -14.1 | 2023 | 2029 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | 66 | 92.6 | - | - | 66.5
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 198 | TIGER 100.00 | 10016 | NEWCUTRET 100.00 | 2 | 198-10016-2 | 86.6 | 86.6 | 55.4 | 86.8 | 99.2 | 39 | 86.6 | 50.4 | 74.3 | 85.3 | 10 | -13.9 | 2019 | 2024 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 71.4 | 57.6 | 99.2 | 71.6 | 68.9 | 55.1
STUDYHAR1VRS | SINGLE 252 | 304196 | ERWIN | 304389 | P2-FAY E | 1 | 304408 | BEARD 115.00 | 304427 | SLOC TAP 115.00 | 1 | 304408-304427-1 | 119 | 119 | 80.9 | 109 | 93 | 67 | 119 | 70.4 | 93.3 | 79.2 | 13 | -13.8 | 2023 | 2028 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 84.3 | - | - | 62.3 | 93 | 72 | - | 69.4
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 198 | TIGER 100.00 | 1 | 132-198-1 | 86.6 | 86.6 | 52.2 | 84.1 | 96.1 | 14 | 86.6 | 47.3 | 71.2 | 82.3 | 1 | -13.8 | 2021 | 2026 | 5 |  | 86.6 | 94.7 | 86.6 | HARLEY | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | - | 68.1 | 54.5 | 96.1 | - | 65.6 | 52.1
STUDYHAR1VRS | SINGLE 179 | 304137 | METHOD | 304150 | I-NCSU S | 1 | 304163 | MILB115 TT 115.00 | 304168 | YONKERS 115.00 | 1 | 304163-304168-1 | 190 | 190 | 63.9 | 178.2 | 98.6 | 52 | 190 | 52.3 | 155.8 | 84.8 | 13 | -13.8 | 2019 | 2024 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.9 | - | - | - | 98.6 | - | - | -
STUDYVCS1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737 | DAN RIV 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 737-10779-1 | 139.4 | 139.4 | 105.2 | 153.4 | 106.2 | 182 | 139.4 | 92 | 134 | 92.5 | 30 | -13.7 | 2018 | 2018 | 0 |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | 139.4 | 57.1 | 101.2 | 71 | 52.2 | 35.2 | - | 81.7 | 83.8 | 75 | 106.2 | 81.5 | 82.3 | 73.8
STUDYVCS1VRS | MAYOW | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 821 | DANVALYT 100.00 | 10779 | RIDGVDUM 100.00 | 1 | 821-10779-1 | 139.4 | 139.4 | 104.3 | 151.5 | 106.2 | 182 | 139.4 | 91.2 | 132.3 | 92.5 | 30 | -13.7 | 2018 | 2018 | 0 |  | 126.4 | 139.4 | 126.4 | MAYO BL | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 81.7 | 83.8 | 75 | 106.2 | 81.5 | 82.3 | 73.8
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 10016 | NEWCUTRET 100.00 | 2 | 132-10016-2 | 86.6 | 86.6 | 46.7 | 77.2 | 90 | 14 | 86.6 | 42.1 | 66.7 | 76.6 | 1 | -13.4 | 2025 | 2030 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 84.8 | - | 61.8 | - | 90 | - | 59.2 | -
STUDYROX4VRS | SINGLE 240 | 304190 | WAKE 230 | 304191 | WENDELL | 1 | 304156 | ROL/SQD TAP 230.00 | 304190 | WAKE 230 230.00 | 1 | 304156-304190-1 | 797 | 797 | 559.6 | 745.2 | 92.4 | 639 | 797 | 461.7 | 641.4 | 79 | 45 | -13.4 | 2023 | 2028 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.1 | - | - | 69.2 | 92.4 | 72.4 | - | 70.2
STUDYHAR1VRS | SINGLE 213 | 304163 | MILB115 | 304168 | YONKERS | 1 | 304137 | METHOD 115.00 | 304150 | I-NCSU S 115.00 | 1 | 304137-304150-1 | 190 | 190 | 115 | 177.4 | 95.9 | 164 | 190 | 104.6 | 155.4 | 82.9 | 16 | -13 | 2021 | 2025 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | - | - | 64.6 | 95.9 | - | - | 67
STUDYRCH1VRS | SINGLE 840 | 304332 | ASHEB230 | 848 | 6PL GRDN | 1 | 536 | 6BUCK 230.00 | 561 | BUCK TIE 100.00 | A4 | 536-561-A4 | 509 | 509 | 455.2 | 464.8 | 91.3 | 705 | 509 | 389.6 | 399 | 78.4 | 229 | -12.9 | 2024 | 2029 | 5 |  | 509 | 584.2 | 547.9 | BUCK TIE AT4 | 230/100 kV Transformer | 509 | 584.2 | 547.9 | - | - | - | - | - | - | - | 91.9 | 91.7 | 79.6 | 91.3 | 92.5 | 86.5 | 74.7
STUDYHAR1VRS | SINGLE 215 | 304163 | MILB115 | 304174 | I-PERSTO | 1 | 304137 | METHOD 115.00 | 304153 | TRYON HILLS 115.00 | 1 | 304137-304153-1 | 108 | 108 | 57 | 97.6 | 94.7 | 95 | 108 | 53.6 | 85.8 | 81.9 | 67 | -12.8 | 2022 | 2026 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.9 | - | - | 57.7 | 94.7 | - | - | 60.4
STUDYASH1VRS | OAKVALEB | 183 | OAKVALE | 195 | SHADY GR | 1 | 183 | OAKVALE 100.00 | 195 | SHADY GR 100.00 | 2 | 183-195-2 | 311.8 | 311.8 | 175.3 | 305.2 | 99.2 | 38 | 311.8 | 155.4 | 270.9 | 86.6 | 26 | -12.6 | 2019 | 2023 | 4 |  | 207.8 | 284.9 | 240.7 | OAKVALE WH | 100 kV Line | 264.3032 | 327.0016 | 264.3032 | 327 | 149.2 | 257.1 | 77.5 | 48.1 | 21.7 | - | - | - | - | 99.2 | - | - | -
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 737 | DAN RIV 100.00 | 810 | WENTWRTH 100.00 | 1 | 737-810-1 | 86.6 | 86.6 | 88.9 | 98.5 | 110 | 212 | 86.6 | 79.1 | 87.8 | 97.7 | 183 | -12.3 | 2018 | 2015 | -3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 100 | 101.4 | 92.2 | 110 | 99.9 | 100.6 | 91.5
STUDYHAR1VRS | SINGLE 208 | 304162 | MILB230 | 304163 | MILB115 | 2 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 1 | 304162-304163-1 | 300 | 300 | 216.8 | 293.1 | 97.7 | 627 | 300 | 194.8 | 257.1 | 85.7 | 126 | -12 | 2020 | 2023 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.5 | 71.6 | - | 71.7 | 97.7 | 73.2 | - | 72.9
STUDYHAR1VRS | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 490.3 | 843.8 | 104.9 | 39 | 796.7 | 439.2 | 757.3 | 92.9 | 39 | -12 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 351.1 | 614.5 | 75.7 | 229.3 | 29.2 | 103.6 | - | - | - | 104.9 | - | - | -
STUDYHAR1VRS | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 735 | 735 | 490.3 | 764.4 | 103.1 | 26 | 735 | 439.2 | 685.1 | 91.2 | 26 | -11.9 | 2018 | 2019 | 1 |  | 735 | 796.7 | 735 | PINOCA BL | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 351.1 | 614.5 | 75.7 | 149.9 | 27.4 | 101.9 | - | 66.4 | 59.2 | 103.1 | - | 67.1 | 59.9
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 2089 | WAYNICKR 100.00 | 10810 | WENTW WH 100.00 | 1 | 2089-10810-1 | 86.6 | 86.6 | 80.2 | 89.8 | 101.1 | 210 | 86.6 | 70.8 | 79.6 | 89.3 | 160 | -11.8 | 2018 | 2021 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 90.9 | 92.3 | 83.9 | 101.1 | 90.8 | 91.6 | 83.2
STUDYVCS1VRS | NGBORO3 | 846 | 6N GRNSB | 2644 | N GRNB 3 | 3 | 737 | DAN RIV 100.00 | 10810 | WENTW WH 100.00 | 1 | 737-10810-1 | 86.6 | 86.6 | 80.9 | 90.7 | 101.2 | 212 | 86.6 | 71.5 | 80.3 | 89.4 | 167 | -11.8 | 2018 | 2021 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 91 | 92.4 | 84 | 101.2 | 90.9 | 91.6 | 83.3
STUDYHAR1VRS | LOOKOUT3 | 3472 | LOOKOUT2 | 1992 | 1LOOKOUT | 3 | 1992 | 1LOOKOUT 44.000 | 3472 | LOOKOUT2 100.00 | 2 | 1992-3472-2 | 42.2 | 42.2 | 27.8 | 46 | 109 | 39 | 42.2 | 25.2 | 41 | 97.2 | 26 | -11.8 | 2018 | 2015 | -3 |  | 39.3 | 43.7 | 42.2 | LOOKOUT TIE 02 | 100/44 kV Transformer | 39.3 | 43.7 | 42.2 | 42.2 | 22.8 | 36.7 | 87.1 | 9.3 | 21.9 | - | - | - | - | 109 | - | - | -
STUDYASH1VRS | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 364.8 | 463.5 | 99 | 634 | 478 | 323 | 414 | 87.5 | 100 | -11.5 | 2019 | 2022 | 3 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 303.1 | 386 | 81 | 77.5 | 18 | 100.5 | 83.3 | 89.3 | 76.1 | 99 | 84.6 | 85.7 | 73.6
STUDYRCH1VRS | BUCKA4 | 536 | 6BUCK | 561 | BUCK TIE | A4 | 884 | FAIRFX B 100.00 | 902 | GREENSBR 100.00 | 1 | 884-902-1 | 183.9 | 183.9 | 157.1 | 166.8 | 90.9 | 156 | 183.9 | 138.7 | 146.9 | 79.6 | 67 | -11.3 | 2025 | 2028 | 3 |  | 183.9384 | 228.1044 | 183.9384 | GREENSBORO BL | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 183.9 | 128.4 | 134 | 72.9 | 32.8 | 18 | - | 86.1 | 87.4 | 69.4 | 90.9 | 86.2 | 86.5 | 68.8
STUDYRCH1VRS | BASE CASE | 0 |  | 0 |  |  | 304615 | BARN CRK E 230.00 | 304616 | BARNARD 115.00 | 1 | 304615-304616-1 | 150 | 150 | 139.5 | 139.5 | 93 | 26 | 150 | 122.6 | 122.6 | 81.7 | 26 | -11.3 | 2023 | 2026 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
STUDYHAR1VRS | SINGLE 207 | 304162 | MILB230 | 304163 | MILB115 | 1 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 2 | 304162-304163-2 | 300 | 300 | 203.7 | 274.6 | 91.5 | 208 | 300 | 184.8 | 240.9 | 80.3 | 39 | -11.2 | 2024 | 2027 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.5 | - | - | - | 91.5 | - | - | -
STUDYVCS1VRS | SINGLE 659 | 304563 | LELAND I | 304568 | DELCO | 1 | 304035 | SUT 1-2F 115.00 | 304560 | I-ASMPCS 115.00 | 1 | 304035-304560-1 | 159 | 159 | 77.8 | 151.2 | 94.1 | 26 | 159 | 63.9 | 133.5 | 83 | 13 | -11.1 | 2022 | 2025 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.1 | - | - | - | 94.1 | - | - | -
STUDYASH1VRS | RURAL3 | 717 | 6RURAL H | 2672 | RURAL 3 | 3 | 737 | DAN RIV 100.00 | 779 | RIDGVEWT 100.00 | 1 | 737-779-1 | 126.4 | 126.4 | 119.9 | 125 | 95.6 | 221 | 139.4 | 104.7 | 120.6 | 84.6 | 117 | -11 | 2021 | 2018 | -3 |  | 126.4 | 139.4 | 126.4 | MAYO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 93 | 95 | 85.1 | 95.6 | 92.7 | 93.5 | 84
STUDYVCS1VRS | PAGEB | 943 | N GREENS | 902 | GREENSBR | 2 | 902 | GREENSBR 100.00 | 943 | N GREENS 100.00 | 3 | 902-943-3 | 207.8 | 207.8 | 159.3 | 212.1 | 99.4 | 136 | 207.8 | 141.7 | 188.6 | 88.4 | 26 | -11 | 2019 | 2021 | 2 |  | 205.7616 | 207.84 | 205.7616 | PAGE WH | 100 kV Line | 205.7616 | 255.8164 | 205.7616 | 207.8 | 134.9 | 179.2 | 84.2 | 32.9 | 15.2 | - | - | - | - | 99.4 | - | - | -
STUDYHAR1VRS | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304550 | CASTLE HAYNE230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304550-304564-1 | 478 | 478 | 376.4 | 486.9 | 102.8 | 1169 | 478 | 331.5 | 438.7 | 91.9 | 240 | -10.9 | 2018 | 2019 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.5 | 77 | - | 78.1 | 102.8 | 79.5 | - | 79.8
STUDYRCH1VRS | LAKEWOODBK2 | 539 | 6LAKEWOD | 2628 | LAKEW 2 | 2 | 539 | 6LAKEWOD 230.00 | 2695 | 1LAKEWOOD 1.0000 | 1 | 539-2695-1 | 415.7 | 415.7 | 335.9 | 449.1 | 108 | 699 | 415.7 | 302.3 | 404.5 | 97.3 | 571 | -10.7 | 2018 | 2015 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.4 | 82 | 77.6 | 108 | 81.1 | 81.1 | 78.6
STUDYRCH1VRS | LAKEWOODBK2 | 539 | 6LAKEWOD | 2628 | LAKEW 2 | 2 | 611 | LAKEWOOD 100.00 | 2695 | 1LAKEWOOD 1.0000 | 1 | 611-2695-1 | 415.7 | 415.7 | 335.9 | 449.1 | 108 | 712 | 415.7 | 302.3 | 404.5 | 97.3 | 571 | -10.7 | 2018 | 2015 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.9 | 82.5 | 78.1 | 108 | 81.6 | 81.6 | 79.1
STUDYHAR1VRS | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 413.4 | 497.4 | 102.1 | 442 | 478 | 371.5 | 445.5 | 91.5 | 420 | -10.6 | 2018 | 2019 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 358.3 | 435.2 | 89.8 | 62.2 | 12.3 | 99.8 | 82.6 | 83 | 81.7 | 102.1 | 85.1 | 85.2 | 83.7
STUDYHAR1VRS | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 413.4 | 497.4 | 102.1 | 455 | 478 | 371.5 | 445.5 | 91.5 | 433 | -10.6 | 2018 | 2019 | 1 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 358.3 | 435.2 | 89.8 | 62.2 | 12.3 | 99.8 | 82.6 | 83 | 81.7 | 102.1 | 85.1 | 85.2 | 83.7
STUDYROX4VRS | NGBORO2 | 846 | 6N GRNSB | 2643 | N GRNB 2 | 2 | 846 | 6N GRNSB 230.00 | 2644 | N GRNB 3 1.0000 | 3 | 846-2644-3 | 500 | 500 | 406.2 | 543.1 | 108.6 | 502 | 500 | 367 | 490.1 | 98 | 390 | -10.6 | 2018 | 2015 | -3 |  | 500 | 500 | 500 | N GREENSBORO TIE 03 | 230/100/44 kV Transformer | 522.7 | 546.4 | 546.4 | 597.3 | 347.3 | 472.4 | 79.1 | 70.7 | 29.5 | - | 81.1 | 84.3 | 80.8 | 108.6 | 81.3 | 82.7 | 78.2
STUDYROX4VRS | NGBORO2 | 846 | 6N GRNSB | 2643 | N GRNB 2 | 2 | 943 | N GREENS 100.00 | 2644 | N GRNB 3 1.0000 | 3 | 943-2644-3 | 500 | 500 | 406.2 | 543.1 | 108.6 | 501 | 500 | 367 | 490.1 | 98 | 390 | -10.6 | 2018 | 2015 | -3 |  | 500 | 500 | 500 | N GREENSBORO TIE 03 | 230/100/44 kV Transformer | 522.7 | 546.4 | 546.4 | 597.3 | 347.3 | 472.5 | 79.1 | 70.6 | 29.5 | - | 81.6 | 84.8 | 81.3 | 108.6 | 81.8 | 83.2 | 78.7
STUDYROX4VRS | PARKWOOD | 849 | 8PARKWOD | 850 | 8PL GRDN | 1 | 858 | BURL T W 100.00 | 897 | GLEN RVN 100.00 | 1 | 858-897-1 | 207.8 | 207.8 | 171.6 | 203.6 | 99.2 | 291 | 207.8 | 155.4 | 185.9 | 88.7 | 145 | -10.5 | 2019 | 2021 | 2 |  | 207.8 | 207.8 | 207.8 | ALAMANCE WH | 100 kV Line | 282.4892 | 327.0016 | 282.4892 | 207.8 | 124.4 | 208 | 99 | -4.4 | 0.2 | - | 77.2 | 77.1 | 74.9 | 99.2 | 82.4 | 82.1 | 79.8
STUDYROX4VRS | LOOKOUT3 | 3472 | LOOKOUT2 | 1992 | 1LOOKOUT | 3 | 1992 | 1LOOKOUT 44.000 | 3472 | LOOKOUT2 100.00 | 1 | 1992-3472-1 | 68 | 68 | 39.5 | 65.3 | 96 | 26 | 68 | 35.8 | 58.2 | 85.6 | 26 | -10.4 | 2021 | 2023 | 2 |  | 64.1 | 69 | 68 | LOOKOUT TIE 01 | 100/44 kV Transformer | 64.1 | 69.1 | 68 | 68 | 32.4 | 52.2 | 76.7 | 13.1 | 19.3 | - | - | 57.5 | 55.7 | 96 | - | 56.5 | 55.1
STUDYHAR1VRS | LOOKOUT1 | 3472 | LOOKOUT2 | 1992 | 1LOOKOUT | 1 | 1992 | 1LOOKOUT 44.000 | 3472 | LOOKOUT2 100.00 | 3 | 1992-3472-3 | 67.9 | 67.9 | 39.5 | 65.3 | 96.2 | 26 | 67.9 | 35.8 | 58.2 | 85.8 | 26 | -10.4 | 2021 | 2023 | 2 |  | 64.1 | 69 | 67.9 | LOOKOUT TIE 03 | 100/44 kV Transformer | 64.1 | 69 | 67.9 | 67.9 | 32.4 | 52.2 | 76.8 | 13.1 | 19.4 | - | - | - | - | 96.2 | - | - | -
STUDYVCS1VRS | GUILFORD2 | 943 | N GREENS | 902 | GREENSBR | 1 | 902 | GREENSBR 100.00 | 943 | N GREENS 100.00 | 2 | 902-943-2 | 207.8 | 207.8 | 159.3 | 199.2 | 93.3 | 123 | 207.8 | 141.7 | 177.1 | 83 | 13 | -10.3 | 2023 | 2025 | 2 |  | 205.7616 | 207.84 | 205.7616 | PAGE BL | 100 kV Line | 205.7616 | 255.8164 | 205.7616 | 207.8 | 134.9 | 168.4 | 79.1 | 30.8 | 14.2 | - | 76.2 | - | - | 93.3 | 76 | - | -
STUDYHAR1VRS | AB_MORNBK4_L | 541 | 6MORN ST | 630 | MORN STR | 4 | 385 | NEWPORT 100.00 | 10119 | ROCK H7 100.00 | 2 | 385-10119-2 | 196.8 | 196.8 | 173.2 | 193.5 | 97.3 | 413 | 196.8 | 155.6 | 174.7 | 87 | 269 | -10.3 | 2020 | 2022 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 94.3 | 100 | 80.6 | 97.3 | 93.3 | 93.9 | 74.1
STUDYVCS1VRS | HARRIS2 | 538 | 6HARRISB | 2623 | HARRI 2 | 2 | 538 | 6HARRISB 230.00 | 2625 | HARRI 4 1.0000 | 4 | 538-2625-4 | 500 | 500 | 401.3 | 499 | 99.8 | 952 | 500 | 360.4 | 447.9 | 89.6 | 602 | -10.2 | 2019 | 2020 | 1 |  | 246.4 | 275.4 | 268.5 | HARRISBURG TIE 04 | 230/100/44 kV Transformer | 246.4 | 275.4 | 268.5 | 268.5 | 192.7 | 250.3 | 93.2 | 248.7 | 6.6 | - | 83.1 | 90.5 | 83.1 | 99.8 | 83 | 83.6 | 79.7
STUDYVCS1VRS | HARRIS4 | 538 | 6HARRISB | 2625 | HARRI 4 | 4 | 538 | 6HARRISB 230.00 | 2624 | HARRI 3 1.0000 | 3 | 538-2624-3 | 270.1 | 270.1 | 194.1 | 269.9 | 99.9 | 312 | 270.1 | 174.3 | 242.2 | 89.7 | 28 | -10.2 | 2019 | 2020 | 1 |  | 247.9 | 277.1 | 270.1 | HARRISBURG TIE 03 | 230/100/44 kV Transformer | 247.9 | 277.1 | 270.1 | 270.1 | 194.2 | 252.2 | 93.4 | 17.7 | 6.5 | - | 81.1 | 81.1 | 72.5 | 99.9 | 81 | 74.9 | 69.6
STUDYHAR1VRS | CLOVER2 | 3354 | CLOVER2 | 1663 | 1CLOVER | 2 | 1721 | 1KING CK 44.000 | 1798 | 1SHRN GT 44.000 | 1 | 1721-1798-1 | 33 | 33 | 17.7 | 28.4 | 90.7 | 26 | 33 | 16.3 | 25.9 | 80.7 | 26 | -10 | 2025 | 2027 | 2 |  | 32.9946 | 36.2712 | 32.9946 | CLOVER | 44 kV Line | 0 | 0 | 0 | 33 | 15 | 23.2 | 72.2 | 5.2 | 18.5 | - | - | 61.6 | 52.2 | 90.7 | - | 57.6 | -
STUDYHAR1VRS | AB_MORNBK4_L | 541 | 6MORN ST | 630 | MORN STR | 4 | 385 | NEWPORT 100.00 | 417 | WYLIE HY 100.00 | 1 | 385-417-1 | 196.8 | 196.8 | 166.3 | 186.4 | 94.1 | 355 | 196.8 | 149.3 | 168.2 | 84.1 | 208 | -10 | 2022 | 2024 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 91.1 | 96.7 | 77.8 | 94.1 | 90.1 | 90.7 | 71.4
STUDYHAR1VRS | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304556 | TOPSAIL TAP 230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304556-304564-1 | 478 | 478 | 347.4 | 457.2 | 96.9 | 667 | 478 | 306.9 | 413.5 | 87 | 113 | -9.9 | 2020 | 2022 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.7 | 71.3 | - | 72.3 | 96.9 | 73.7 | - | 74
STUDYASH1VRS | BECKERD4 | 713 | 6BECKRDT | 726 | BECKRDIT | 4 | 928 | JESUPTWN 100.00 | 943 | N GREENS 100.00 | 1 | 928-943-1 | 177.9 | 177.9 | 171.8 | 178.5 | 101.8 | 169 | 177.9 | 155.1 | 161.5 | 91.9 | 169 | -9.9 | 2018 | 2019 | 1 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 180.5 | 141.4 | 177.2 | 99.6 | 1.3 | 2.2 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
STUDYHAR1VRS | LOOKOT44_CAP | 6992 | 1LOOKCAP | 1992 | 1LOOKOUT | 1 | 472 | LOOKOUT 100.00 | 3472 | LOOKOUT2 100.00 | 1 | 472-3472-1 | 129.9 | 129.9 | 106.8 | 124.5 | 93.8 | 52 | 129.9 | 96.9 | 111.9 | 84 | 61 | -9.8 | 2023 | 2024 | 1 |  | 129.9 | 129.9 | 129.9 | LOOKOUT TIE | High Side 100\44 kV Xfmr Breaker | 0 | 0 | 0 | 129.9 | 87.7 | 92.7 | 70.1 | 31.8 | 23.7 | - | 80.4 | 82.8 | 80 | 93.8 | 80.1 | 80 | 79.1
STUDYROX4VRS | WEBSTERBK2 | 2488 | 5WEBSTER | 2555 | 2WEBSTER | 2 | 2488 | 5WEBSTER 161.00 | 2555 | 2WEBSTER 66.000 | 1 | 2488-2555-1 | 100.4 | 100.4 | 54.5 | 109.4 | 109 | 13 | 100.4 | 50.2 | 99.6 | 99.2 | 13 | -9.8 | 2018 | 2014 | -4 |  | 94.4 | 103.2 | 100.4 | WEBSTER TIE BK 01 | 161/66 kV Transformer | 94.4 | 103.2 | 100.4 | 100.4 | 45.7 | 91.2 | 90.9 | 18.2 | 18.1 | - | - | 53.6 | 51.6 | 109 | - | 53.2 | 51.5
STUDYHAR1VRS | CLOVER2 | 3354 | CLOVER2 | 1663 | 1CLOVER | 2 | 1748 | 1NINE 9 44.000 | 1798 | 1SHRN GT 44.000 | 1 | 1748-1798-1 | 44.7 | 44.7 | 30 | 41.5 | 94 | 26 | 44.7 | 27.7 | 37.8 | 84.3 | 26 | -9.7 | 2022 | 2024 | 2 |  | 44.7 | 45.7 | 44.7 | CLOVER | 44 kV Line | 0 | 0 | 0 | 44.7 | 25.9 | 34.4 | 77.1 | 7.1 | 16.9 | - | - | 78.4 | 67.3 | 94 | 70 | 68.9 | 63.5
STUDYVCS1VRS | HARRIS4 | 538 | 6HARRISB | 2625 | HARRI 4 | 4 | 600 | HARRISBG 100.00 | 2624 | HARRI 3 1.0000 | 3 | 600-2624-3 | 270.1 | 270.1 | 190.8 | 262.6 | 97.2 | 289 | 270.1 | 171.6 | 236.4 | 87.5 | 26 | -9.7 | 2020 | 2022 | 2 |  | 247.9 | 277.1 | 270.1 | HARRISBURG TIE 03 | 230/100/44 kV Transformer | 247.9 | 277.1 | 270.1 | 270.1 | 189.1 | 242.8 | 89.9 | 19.8 | 7.3 | - | 81.1 | 81.1 | 72.5 | 97.2 | 81 | 74.9 | 69.6
STUDYVCS1VRS | HARRIS2 | 538 | 6HARRISB | 2623 | HARRI 2 | 2 | 600 | HARRISBG 100.00 | 2625 | HARRI 4 1.0000 | 4 | 600-2625-4 | 500 | 500 | 394.1 | 487.2 | 97.4 | 929 | 500 | 354.6 | 438.5 | 87.7 | 486 | -9.7 | 2020 | 2022 | 2 |  | 246.4 | 275.4 | 268.5 | HARRISBURG TIE 04 | 230/100/44 kV Transformer | 246.4 | 275.4 | 268.5 | 268.5 | 187.7 | 241 | 89.8 | 246.2 | 7.6 | - | 83.1 | 90.5 | 83.1 | 97.4 | 83 | 83.6 | 79.7
STUDYVCS1VRS | HARRIS4 | 538 | 6HARRISB | 2625 | HARRI 4 | 4 | 538 | 6HARRISB 230.00 | 2623 | HARRI 2 1.0000 | 2 | 538-2623-2 | 416.1 | 416.1 | 280.1 | 389.3 | 93.6 | 102 | 416.1 | 251.5 | 349.4 | 84 | 13 | -9.6 | 2023 | 2024 | 1 |  | 386.6 | 443.6 | 416.1 | HARRISBURG TIE 02 | 230/100/44 kV Transformer | 386.6 | 443.6 | 416.1 | 416.1 | 280.1 | 333.3 | 80.1 | 56 | 13.5 | - | 75 | 75.9 | 65.3 | 93.6 | 74.9 | 70.1 | 62.7
STUDYHAR1VRS | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304360 | ELLERBE 230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304360-304638-1 | 507 | 507 | 287.7 | 496.7 | 98.5 | 13 | 507 | 262.5 | 452.4 | 88.9 | 13 | -9.6 | 2019 | 2021 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 86.6 | - | - | - | 98.5 | - | - | 55.8
STUDYROX4VRS | BASE CASE | 0 |  | 0 |  |  | 648 | REAMES R 100.00 | 10590 | GERDAU W 100.00 | 1 | 648-10590-1 | 91.2 | 91.2 | 92.8 | 92.8 | 104.8 | 39 | 91.2 | 86.3 | 86.3 | 95.2 | 39 | -9.6 | 2018 | 2017 | -1 |  | 91.2 | 112.3 | 91.2 | REAMES RD. RET. TAP | 100 kV Line | 106 | 130.6 | 106 | 91.2 | 93 | 93 | 105.6 | -0.2 | -0.8 | - | 106.2 | 110.3 | 85.9 | 104.8 | 105.9 | 105.6 | 84.9
STUDYHAR1VRS | MEBANE3 | 3938 | MEBANE2 | 2433 | 1MEBANE | 3 | 2433 | 1MEBANE 44.000 | 3938 | MEBANE2 100.00 | 4 | 2433-3938-4 | 25.1 | 25.1 | 19.5 | 26.6 | 106 | 78 | 25.1 | 17.9 | 24.2 | 96.4 | 65 | -9.6 | 2018 | 2016 | -2 |  | 23.4 | 26 | 25.1 | MEBANE TIE 04 | 100/44 kV Transformer | 23.4 | 26 | 25.1 | 25.1 | 16.7 | 22.2 | 88.5 | 4.4 | 17.5 | - | - | - | - | 106 | - | - | -
STUDYHAR1VRS | MEBANE44_CAP | 7433 | 1MEBACAP | 2433 | 1MEBANE | 1 | 938 | MEBANE 100.00 | 3938 | MEBANE2 100.00 | 1 | 938-3938-1 | 86.6 | 86.6 | 76.4 | 82.3 | 95.4 | 52 | 86.6 | 70.1 | 75.3 | 85.9 | 52 | -9.5 | 2021 | 2023 | 2 |  | 86.6 | 86.6 | 86.6 | MEBANE TIE | High Side 100\44 kV Xfmr Breaker | 0 | 0 | 0 | 86.6 | 65.6 | 65.6 | 74.8 | 16.7 | 20.6 | - | 87.4 | 87.4 | 86.9 | 95.4 | 88.2 | 88.1 | 87.6
STUDYHAR1VRS | ACREROCK2 | 3338 | ACRERK 2 | 1631 | 1ACRERCK | 2 | 1631 | 1ACRERCK 44.000 | 3338 | ACRERK 2 100.00 | 3 | 1631-3338-3 | 45.7 | 45.7 | 20.9 | 44.1 | 96.5 | 13 | 45.7 | 19.1 | 39.7 | 87 | 13 | -9.5 | 2021 | 2022 | 1 |  | 44 | 45.7 | 45.7 | ACREROCK TIE 03 | 100/44 kV Transformer | 44 | 48.1 | 46.8 | 45.7 | 16.7 | 33.6 | 73.6 | 10.5 | 22.9 | - | - | - | - | 96.5 | - | - | -
STUDYHAR1VRS | MEBANE4 | 3938 | MEBANE2 | 2433 | 1MEBANE | 4 | 2433 | 1MEBANE 44.000 | 3938 | MEBANE2 100.00 | 1 | 2433-3938-1 | 25 | 25 | 19 | 26.2 | 104.8 | 78 | 25 | 17.4 | 23.8 | 95.3 | 52 | -9.5 | 2018 | 2017 | -1 |  | 23.3 | 25.9 | 25 | MEBANE TIE 01 | 100/44 kV Transformer | 23.3 | 25.9 | 25 | 25 | 16.3 | 21.9 | 87.4 | 4.3 | 17.4 | - | 81.2 | 75.7 | 72.7 | 104.8 | 82 | 76.3 | 73.3
STUDYHAR1VRS | MEBANE4 | 3938 | MEBANE2 | 2433 | 1MEBANE | 4 | 2433 | 1MEBANE 44.000 | 3938 | MEBANE2 100.00 | 3 | 2433-3938-3 | 25 | 25 | 19 | 26.2 | 104.8 | 78 | 25 | 17.4 | 23.8 | 95.3 | 52 | -9.5 | 2018 | 2017 | -1 |  | 23.3 | 25.9 | 25 | MEBANE TIE 03 | 100/44 kV Transformer | 23.3 | 25.9 | 25 | 25 | 16.3 | 21.9 | 87.4 | 4.3 | 17.4 | - | - | - | - | 104.8 | - | - | -
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 2433 | 1MEBANE 44.000 | 2456 | 1WLTR KI 44.000 | 1 | 2433-2456-1 | 40 | 40 | 35.6 | 35.6 | 93.9 | 39 | 40 | 32.9 | 32.9 | 84.5 | 39 | -9.4 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | 40 | 30.2 | 30.2 | 77.3 | 5.4 | 16.6 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
STUDYROX4VRS | ACREROCK3 | 3338 | ACRERK 2 | 1631 | 1ACRERCK | 3 | 1631 | 1ACRERCK 44.000 | 3338 | ACRERK 2 100.00 | 2 | 1631-3338-2 | 45.7 | 45.7 | 20.8 | 44.1 | 96.5 | 13 | 45.7 | 19.1 | 39.8 | 87.1 | 13 | -9.4 | 2021 | 2022 | 1 |  | 44 | 45.7 | 45.7 | ACREROCK TIE 02 | 100/44 kV Transformer | 44 | 48.1 | 46.8 | 45.7 | 16.7 | 33.6 | 73.6 | 10.5 | 22.9 | - | - | - | - | 96.5 | - | - | -
STUDYHAR1VRS | MEBANE4 | 3938 | MEBANE2 | 2433 | 1MEBANE | 4 | 2433 | 1MEBANE 44.000 | 3938 | MEBANE2 100.00 | 2 | 2433-3938-2 | 25 | 25 | 18.9 | 26 | 104.1 | 78 | 25 | 17.3 | 23.7 | 94.7 | 52 | -9.4 | 2018 | 2017 | -1 |  | 23.3 | 25.9 | 25 | MEBANE TIE 02 | 100/44 kV Transformer | 23.3 | 25.9 | 25 | 25 | 16.2 | 21.7 | 86.8 | 4.3 | 17.3 | - | - | - | - | 104.1 | - | - | -
STUDYHAR1VRS | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304360 | ELLERBE 230.00 | 304361 | WESTND230 TT230.00 | 1 | 304360-304361-1 | 507 | 507 | 264 | 472.9 | 93.8 | 13 | 507 | 239.4 | 430.3 | 84.6 | 7 | -9.2 | 2023 | 2024 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 82 | - | - | - | 93.8 | - | - | 51.2
STUDYBRN1VRS | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 82.9 | 211.5 | 104.4 | 13 | 201 | 74.9 | 193.2 | 95.2 | 13 | -9.2 | 2018 | 2017 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.6 | - | - | - | 104.4 | - | - | -
STUDYHAR1VRS | TABLEROCK3 | 3497 | TABL RO2 | 2055 | 1TABL RK | 3 | 2055 | 1TABL RK 44.000 | 3497 | TABL RO2 100.00 | 2 | 2055-3497-2 | 24.1 | 24.1 | 15.7 | 25.1 | 104.2 | 39 | 24.1 | 14.4 | 22.9 | 95.1 | 26 | -9.1 | 2018 | 2017 | -1 |  | 22.3 | 24.1 | 24.1 | TABLE ROCK TIE 02 | 100/44 kV Transformer | 22.3 | 24.1 | 24.1 | 24.1 | 12.2 | 19 | 79 | 6.1 | 25.2 | - | 71.6 | - | - | 104.2 | 71.1 | - | -
STUDYVCS1VRS | HARRIS4 | 538 | 6HARRISB | 2625 | HARRI 4 | 4 | 600 | HARRISBG 100.00 | 2623 | HARRI 2 1.0000 | 2 | 600-2623-2 | 416.1 | 416.1 | 275.1 | 378.6 | 91 | 39 | 416.1 | 247.5 | 340.9 | 81.9 | 13 | -9.1 | 2024 | 2026 | 2 |  | 386.6 | 443.6 | 416.1 | HARRISBURG TIE 02 | 230/100/44 kV Transformer | 386.6 | 443.6 | 416.1 | 416.1 | 272.8 | 322.4 | 77.5 | 56.2 | 13.5 | - | 75 | 75.9 | 65.3 | 91 | 74.9 | 70.1 | 62.7
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 2413 | 1AO SMIT 44.000 | 2456 | 1WLTR KI 44.000 | 1 | 2413-2456-1 | 40 | 40 | 33.9 | 33.9 | 91 | 39 | 40 | 31.5 | 31.5 | 81.9 | 39 | -9.1 | 2024 | 2026 | 2 |  | - | - | - | - | - | - | - | - | 40 | 28.8 | 28.8 | 74.5 | 5.1 | 16.5 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
STUDYRCH1VRS | WINECOFF4 | 544 | 6WINECOF | 2691 | WINEC 4 | 4 | 544 | 6WINECOF 230.00 | 2686 | WINEC 2 1.0000 | 2 | 544-2686-2 | 240.7 | 240.7 | 186.6 | 239.4 | 99.5 | 130 | 240.7 | 169.5 | 217.6 | 90.4 | 104 | -9.1 | 2019 | 2020 | 1 |  | 240.7 | 278.4 | 240.7 | WINECOFF TIE 02 | 230/100/44 kV Transformer | 249.4 | 278.4 | 271.5 | 240.7 | 153.1 | 197.6 | 82.1 | 41.8 | 17.4 | - | 74.9 | 75.7 | 64.7 | 99.5 | 75.1 | 75.2 | 64.2
STUDYASH1VRS | BEULAH1 | 490 | STAMEY | 472 | LOOKOUT | 1 | 454 | ENRG U18 100.00 | 490 | STAMEY 100.00 | 1 | 454-490-1 | 196.8 | 196.8 | 133.1 | 197.3 | 96.7 | 87 | 196.8 | 120.4 | 178.5 | 87.7 | 15 | -9 | 2021 | 2022 | 1 |  | 177.8764 | 196.8 | 177.8764 | BEULAH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 190.5 | 110.4 | 162.6 | 83.2 | 34.7 | 13.5 | - | 76 | 82.2 | 69.6 | 96.7 | 74 | 75.2 | 66.5
STUDYROB2VRS | WINECOFF4 | 544 | 6WINECOF | 2691 | WINEC 4 | 4 | 544 | 6WINECOF 230.00 | 2685 | WINEC 1 1.0000 | 1 | 544-2685-1 | 240.7 | 240.7 | 186.8 | 240.2 | 99.8 | 130 | 240.7 | 169.7 | 218.5 | 90.8 | 104 | -9 | 2019 | 2020 | 1 |  | 240.7 | 279.2 | 240.7 | WINECOFF TIE 01 | 230/100/44 kV Transformer | 250 | 279.2 | 272.2 | 240.7 | 153.3 | 197.8 | 82.2 | 42.4 | 17.6 | - | 75 | 75.8 | 64.6 | 99.8 | 75.2 | 75.3 | 64.1
STUDYROB2VRS | WINECOFF4 | 544 | 6WINECOF | 2691 | WINEC 4 | 4 | 687 | WINECOFF 100.00 | 2685 | WINEC 1 1.0000 | 1 | 687-2685-1 | 240.7 | 240.7 | 186.8 | 240.2 | 99.8 | 130 | 240.7 | 169.7 | 218.5 | 90.8 | 104 | -9 | 2019 | 2020 | 1 |  | 240.7 | 279.2 | 240.7 | WINECOFF TIE 01 | 230/100/44 kV Transformer | 250 | 279.2 | 272.2 | 240.7 | 153.3 | 197.4 | 82 | 42.8 | 17.8 | - | 75.5 | 76.3 | 65 | 99.8 | 75.6 | 75.7 | 64.5
STUDYROX4VRS | TABLEROCK1 | 3497 | TABL RO2 | 2055 | 1TABL RK | 1 | 2055 | 1TABL RK 44.000 | 3497 | TABL RO2 100.00 | 3 | 2055-3497-3 | 25.2 | 25.2 | 17.5 | 26.6 | 105.5 | 39 | 25.2 | 16.1 | 24.3 | 96.5 | 26 | -9 | 2018 | 2016 | -2 |  | 23.6 | 25.9 | 25.2 | TABLE ROCK TIE 03 | 100/44 kV Transformer | 23.6 | 25.9 | 25.2 | 25.2 | 13.6 | 20.2 | 80.3 | 6.4 | 25.2 | - | - | - | - | 105.5 | - | - | -
STUDYHAR1VRS | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304251 | LEE230 SUB 230.00 | 304960 | WYNCO#5 18.000 | 1 | 304251-304960-1 | 220 | 220 | 198.5 | 206.7 | 94 | 113 | 220 | 187.1 | 187.1 | 85.1 | 39 | -8.9 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.9 | 83.7 | 85 | 84.7 | 94 | 87.6 | 88.4 | 88.5
STUDYASH1VRS | MORNSTARBK2 | 541 | 6MORN ST | 630 | MORN STR | 2 | 541 | 6MORN ST 230.00 | 630 | MORN STR 100.00 | 3 | 541-630-3 | 199.2 | 199.2 | 129.9 | 185.9 | 93.3 | 35 | 199.2 | 117.6 | 168.4 | 84.5 | 26 | -8.8 | 2023 | 2024 | 1 |  | 182.6 | 199.2 | 199.2 | MORNING STAR TIE 03 | 230/100 kV Transformer | 182.6 | 202.2 | 200 | 199.2 | 112.4 | 161.2 | 80.9 | 24.7 | 12.4 | - | - | - | - | 93.3 | - | - | -
STUDYHAR1VRS | SINGLE 613 | 304519 | M-TARAWA | 304524 | JACKSV23 | 1 | 304251 | LEE230 SUB 230.00 | 304956 | WYNCO#1 18.000 | 1 | 304251-304956-1 | 220 | 220 | 199.4 | 207.6 | 94.3 | 113 | 220 | 188.1 | 188.1 | 85.5 | 39 | -8.8 | 2022 | 2023 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.3 | 84.1 | 85.4 | 85.1 | 94.3 | 88 | 88.8 | 88.9
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 894 | GILBRTHT 100.00 | 10968 | TROLNGWB 100.00 | 1 | 894-10968-1 | 118.8 | 118.8 | 110.9 | 110.9 | 94.5 | 39 | 118.8 | 102.4 | 102.4 | 85.7 | 39 | -8.8 | 2022 | 2023 | 1 |  | 118.8 | 130.8 | 118.8 | SWEPSONVILLE BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 118.8 | 92.2 | 92.2 | 77.4 | 18.7 | 17.1 | - | 93.8 | 93.9 | 84.9 | 94.5 | 94.6 | 94.5 | 85.4
STUDYROX4VRS | CONCORD8 | 4573 | CONCORD2 | 2132 | 1CONCORD | 8 | 2132 | 1CONCORD 44.000 | 4573 | CONCORD2 100.00 | 7 | 2132-4573-7 | 62.6 | 62.6 | 31.6 | 64.9 | 103.7 | 13 | 62.6 | 29.2 | 59.4 | 94.9 | 13 | -8.8 | 2018 | 2017 | -1 |  | 58.2 | 64.7 | 62.6 | CONCORD MAIN 07 | 100/44 kV Transformer | 58.2 | 64.7 | 62.6 | 62.6 | 32 | 66.7 | 106.6 | -1.8 | -2.9 | - | - | 50.1 | - | 103.7 | - | - | -
STUDYROX4VRS | CONCORD7 | 4573 | CONCORD2 | 2132 | 1CONCORD | 7 | 2132 | 1CONCORD 44.000 | 4573 | CONCORD2 100.00 | 8 | 2132-4573-8 | 62.6 | 62.6 | 31.6 | 64.9 | 103.7 | 13 | 62.6 | 29.2 | 59.4 | 94.9 | 13 | -8.8 | 2018 | 2017 | -1 |  | 58.2 | 64.7 | 62.6 | CONCORD MAIN 08 | 100/44 kV Transformer | 58.2 | 64.7 | 62.6 | 62.6 | 32 | 66.7 | 106.6 | -1.8 | -2.9 | - | - | - | - | 103.7 | - | - | -
STUDYROB2VRS | BUCKA4 | 536 | 6BUCK | 561 | BUCK TIE | A4 | 687 | WINECOFF 100.00 | 2686 | WINEC 2 1.0000 | 2 | 687-2686-2 | 240.7 | 240.7 | 186.5 | 216.5 | 90 | 130 | 240.7 | 169.6 | 195.6 | 81.3 | 104 | -8.7 | 2025 | 2027 | 2 |  | 240.7 | 278.4 | 240.7 | WINECOFF TIE 02 | 230/100/44 kV Transformer | 249.4 | 278.4 | 271.5 | 240.7 | 152 | 196.5 | 81.6 | 20 | 8.4 | - | 75.4 | 76.2 | 65.1 | 90 | 75.5 | 75.6 | 64.6
STUDYASH1VRS | MORNSTARBK2 | 541 | 6MORN ST | 630 | MORN STR | 2 | 541 | 6MORN ST 230.00 | 630 | MORN STR 100.00 | 4 | 541-630-4 | 199.2 | 199.2 | 128.8 | 184.3 | 92.5 | 52 | 199.2 | 116.6 | 167 | 83.8 | 26 | -8.7 | 2023 | 2025 | 2 |  | 182.1 | 199.2 | 199.2 | MORNING STAR TIE 04 | 230/100 kV Transformer | 182.1 | 204.6 | 199.2 | 199.2 | 111.5 | 159.8 | 80.2 | 24.5 | 12.3 | - | - | - | - | 92.5 | - | - | -
STUDYHAR1VRS | SHATTALONB | 798 | SHATTALN | 788 | RURAL HL | 3 | 788 | RURAL HL 100.00 | 798 | SHATTALN 100.00 | 1 | 788-798-1 | 163.3 | 163.3 | 127.3 | 160.5 | 94 | 196 | 163.3 | 115.3 | 145.4 | 85.3 | 132 | -8.7 | 2022 | 2024 | 2 |  | 148.6056 | 163.3276 | 148.6056 | SHATTALON | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 163.3 | 115 | 144.5 | 85.1 | 16 | 8.9 | - | 83.4 | 85.5 | 76 | 94 | 83.5 | 84.7 | 74.6
STUDYHAR1VRS | SHATTALONB | 798 | SHATTALN | 788 | RURAL HL | 3 | 788 | RURAL HL 100.00 | 798 | SHATTALN 100.00 | 2 | 788-798-2 | 163.3 | 163.3 | 127.3 | 160.5 | 94 | 209 | 163.3 | 115.3 | 145.4 | 85.3 | 145 | -8.7 | 2022 | 2024 | 2 |  | 148.6056 | 163.3276 | 148.6056 | SHATTALON | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 163.3 | 115 | 144.5 | 85.1 | 16 | 8.9 | - | - | - | - | 94 | - | - | -
STUDYHAR1VRS | BETHANIA1 | 798 | SHATTALN | 788 | RURAL HL | 1 | 788 | RURAL HL 100.00 | 798 | SHATTALN 100.00 | 3 | 788-798-3 | 162.5 | 162.5 | 127.3 | 160.5 | 94.5 | 206 | 162.5 | 115.3 | 145.4 | 85.8 | 132 | -8.7 | 2022 | 2023 | 1 |  | 147.8 | 162.5 | 147.8 | BETHANIA WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 162.5 | 115 | 144.5 | 85.5 | 16 | 9 | - | - | - | - | 94.5 | - | - | -
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 956 | RNDLPH R 100.00 | 957 | RNDLPH T 100.00 | 1 | 956-957-1 | 128 | 128 | 120.1 | 120.1 | 96.3 | 39 | 128 | 110.8 | 110.8 | 87.6 | 39 | -8.7 | 2021 | 2022 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | 99.4 | 99.4 | 78.9 | 20.7 | 17.4 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
STUDYROB2VRS | SINGLE 855 | 304730 | CAMDEN | 312715 | 6LUGOFF | 1 | 304723 | CAMDEN JCT 115.00 | 304726 | CAMDEN DUSTY115.00 | 1 | 304723-304726-1 | 108 | 108 | 36.5 | 93 | 96.2 | 39 | 108 | 41.2 | 86.7 | 87.6 | 26 | -8.6 | 2021 | 2022 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.2 | - | - | - | 96.2 | - | - | -
STUDYHAR1VRS | GAFFNEY2 | 254 | GAFFNEY | 1465 | 1GAFFNEY | 2 | 254 | GAFFNEY 100.00 | 1465 | 1GAFFNEY 44.000 | 1 | 254-1465-1 | 45.7 | 45.7 | 31.3 | 45.8 | 100.2 | 38 | 45.7 | 28.4 | 41.9 | 91.6 | 13 | -8.6 | 2018 | 2019 | 1 |  | 41.1 | 45.7 | 44.4 | GAFFNEY TIE 01 | 100/44 kV Transformer | 41.1 | 45.7 | 44.4 | 45.7 | 27.1 | 38.6 | 84.5 | 7.2 | 15.7 | - | 79.6 | 79 | 70.7 | 100.2 | 79.3 | 72.3 | 66.9
STUDYHAR1VRS | SINGLE 613 | 304519 | M-TARAWA | 304524 | JACKSV23 | 1 | 304251 | LEE230 SUB 230.00 | 304957 | WYNCO#2 18.000 | 1 | 304251-304957-1 | 220 | 220 | 204 | 211.9 | 96.3 | 106 | 220 | 192.9 | 192.9 | 87.7 | 39 | -8.6 | 2021 | 2022 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.3 | 86.1 | 87.4 | 87.2 | 96.3 | 89.9 | 90.8 | 90.9
STUDYROX4VRS | TABLEROCK3 | 3497 | TABL RO2 | 2055 | 1TABL RK | 3 | 2055 | 1TABL RK 44.000 | 3497 | TABL RO2 100.00 | 1 | 2055-3497-1 | 25.9 | 25.9 | 15.9 | 25.5 | 98.5 | 26 | 25.9 | 14.7 | 23.3 | 90 | 26 | -8.5 | 2019 | 2020 | 1 |  | 25.4 | 25.9 | 25.9 | TABLE ROCK TIE 01 | 100/44 kV Transformer | 25.4 | 25.9 | 25.9 | 25.9 | 12.4 | 19.3 | 74.7 | 6.2 | 23.8 | - | - | 63.5 | 62.3 | 98.5 | - | 62.1 | 61.5
STUDYHAR1VRS | PINKBK2 | 3293 | PNK HAR2 | 1548 | 1PINK HL | 2 | 1548 | 1PINK HL 44.000 | 3293 | PNK HAR2 100.00 | 3 | 1548-3293-3 | 42.4 | 42.4 | 20 | 42.3 | 99.9 | 13 | 42.4 | 18.4 | 38.7 | 91.4 | 13 | -8.5 | 2019 | 2019 | 0 |  | 39.5 | 43.9 | 42.4 | PINK HARRILL TIE 03 | 100/44 kV Transformer | 39.5 | 43.9 | 42.4 | 42.4 | 16.8 | 34.8 | 82.2 | 7.5 | 17.7 | - | - | - | - | 99.9 | - | - | -
STUDYVCS1VRS | PINKBK3 | 3293 | PNK HAR2 | 1548 | 1PINK HL | 3 | 1548 | 1PINK HL 44.000 | 3293 | PNK HAR2 100.00 | 2 | 1548-3293-2 | 42.4 | 42.4 | 20 | 42.3 | 99.8 | 13 | 42.4 | 18.5 | 38.7 | 91.4 | 13 | -8.4 | 2019 | 2019 | 0 |  | 39.5 | 43.8 | 42.4 | PINK HARRILL TIE 02 | 100/44 kV Transformer | 39.5 | 43.8 | 42.4 | 42.4 | 16.8 | 34.8 | 82.2 | 7.5 | 17.6 | - | - | - | - | 99.8 | - | - | -
STUDYHAR1VRS | GAFFNEY1 | 254 | GAFFNEY | 1465 | 1GAFFNEY | 1 | 254 | GAFFNEY 100.00 | 1465 | 1GAFFNEY 44.000 | 2 | 254-1465-2 | 45.7 | 45.7 | 28.2 | 43.4 | 95 | 13 | 45.7 | 25.5 | 39.6 | 86.8 | 13 | -8.2 | 2022 | 2022 | 0 |  | 43.4 | 45.7 | 45.7 | GAFFNEY TIE 02 | 100/44 kV Transformer | 43.4 | 45.7 | 45.7 | 45.7 | 24.4 | 36.4 | 79.6 | 7 | 15.4 | - | - | - | - | 95 | - | - | -
STUDYROX4VRS | BELMONT3 | 3344 | BELMONT2 | 1639 | 1BELMONT | 3 | 1639 | 1BELMONT 44.000 | 3344 | BELMONT2 100.00 | 2 | 1639-3344-2 | 64.8 | 64.8 | 31.4 | 67.1 | 103.5 | 13 | 64.8 | 29.2 | 61.7 | 95.3 | 13 | -8.2 | 2018 | 2017 | -1 |  | 64.8 | 70.7 | 64.8 | BELMONT TIE 02 | 100/44 kV Transformer | 65 | 71 | 69.1 | 64.8 | 28.4 | 59.3 | 91.5 | 7.8 | 12 | - | - | - | - | 103.5 | - | - | -
STUDYVCS1VRS | BELMONT2 | 3344 | BELMONT2 | 1639 | 1BELMONT | 2 | 1639 | 1BELMONT 44.000 | 3344 | BELMONT2 100.00 | 3 | 1639-3344-3 | 64.8 | 64.8 | 31.4 | 67 | 103.5 | 13 | 64.8 | 29.2 | 61.7 | 95.3 | 13 | -8.2 | 2018 | 2017 | -1 |  | 64.8 | 70.7 | 64.8 | BELMONT TIE 03 | 100/44 kV Transformer | 65 | 71 | 69 | 64.8 | 28.4 | 59.3 | 91.5 | 7.7 | 12 | - | - | - | - | 103.5 | - | - | -
STUDYROX4VRS | WILDCAT3 | 3685 | WILDCAT2 | 2221 | 1WILDCAT | 3 | 2221 | 1WILDCAT 44.000 | 3685 | WILDCAT2 100.00 | 2 | 2221-3685-2 | 44.3 | 44.3 | 27.1 | 41.6 | 93.9 | 26 | 44.3 | 25 | 38 | 85.8 | 26 | -8.1 | 2022 | 2023 | 1 |  | 41.7 | 45.6 | 44.3 | WILDCAT TIE 02 | 100/44 kV Transformer | 41.7 | 45.6 | 44.3 | 44.3 | 24.7 | 36.8 | 83 | 4.8 | 10.9 | - | - | - | - | 93.9 | - | - | -
STUDYROX4VRS | ELZBTHBS | 690 | WOODLAWN | 10609 | KENILW B | 1 | 584 | ELIZBETH 100.00 | 631 | N CHARLT 100.00 | 1 | 584-631-1 | 141.2 | 141.2 | 71.1 | 135.8 | 97.6 | 105 | 141.2 | 75.3 | 126.3 | 89.5 | 116 | -8.1 | 2020 | 2020 | 0 |  | 128 | 141.2 | 128 | ELIZABETH BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 141.2 | 53.3 | 116.4 | 82.9 | 19.4 | 14.7 | - | - | 81.6 | 57.7 | 97.6 | - | 70.7 | 53.3
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1291 | 1JPS SLA 44.000 | 1352 | 1TIGERVT 44.000 | 1 | 1291-1352-1 | 25.8 | 25.8 | 23.7 | 23.7 | 92.5 | 39 | 25.8 | 21.9 | 21.9 | 84.5 | 26 | -8 | 2023 | 2024 | 1 |  | 25.8 | 31.3 | 25.8 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 25.8 | 20.8 | 20.8 | 79.2 | 2.9 | 13.3 | - | 93.4 | 94.8 | 76.6 | 92.5 | 93.5 | 93 | 76
STUDYROX4VRS | WILDCAT3 | 3685 | WILDCAT2 | 2221 | 1WILDCAT | 3 | 2221 | 1WILDCAT 44.000 | 3685 | WILDCAT2 100.00 | 1 | 2221-3685-1 | 44.3 | 44.3 | 26.8 | 41.1 | 92.7 | 26 | 44.3 | 24.7 | 37.5 | 84.7 | 26 | -8 | 2023 | 2024 | 1 |  | 41.7 | 45.6 | 44.3 | WILDCAT TIE 01 | 100/44 kV Transformer | 41.7 | 45.6 | 44.3 | 44.3 | 24.3 | 36.3 | 81.9 | 4.8 | 10.8 | - | - | 61.4 | 58.6 | 92.7 | - | 60.2 | 57.8
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1280 | 1HEND MN 44.000 | 1295 | 1KANUGA 44.000 | 1 | 1280-1295-1 | 25.8 | 25.8 | 23.1 | 23.1 | 94.5 | 39 | 25.8 | 21.5 | 21.5 | 86.5 | 39 | -8 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | 20.6 | 20.6 | 83.4 | 2.5 | 11.1 | - | 94.5 | 95.7 | 77.6 | 94.5 | 94.9 | 94.7 | 77.7
STUDYASH1VRS | OAKVALE1 | 3183 | OAKVALE2 | 1328 | 1OAKVALE | 1 | 1328 | 1OAKVALE 44.000 | 3183 | OAKVALE2 100.00 | 2 | 1328-3183-2 | 27 | 27 | 11.9 | 25.8 | 95.5 | 13 | 27 | 11 | 23.6 | 87.5 | 13 | -8 | 2021 | 2022 | 1 |  | 24.1 | 27 | 26.1 | OAKVALE TIE 02 | 100/44 kV Transformer | 24.1 | 27 | 26.1 | - | - | - | - | - | - | - | - | - | - | 95.5 | - | - | -
STUDYHAR1VRS | ELZBTHWN | 631 | N CHARLT | 602 | HIL S RE | 1 | 609 | KENILWTH 100.00 | 690 | WOODLAWN 100.00 | 1 | 609-690-1 | 207.8 | 207.8 | 131.4 | 198.7 | 96.2 | 101 | 207.8 | 115.6 | 184.6 | 88.2 | 13 | -8 | 2021 | 2021 | 0 |  | 207.8 | 207.8 | 207.8 | ELIZABETH WH | 100 kV Line | 255.9896 | 282.4892 | 255.9896 | - | - | - | - | - | - | - | 70.2 | 72.6 | 69.7 | 96.2 | - | 68.2 | 63.2
STUDYBRN1VRS | SINGLE 514 | 304422 | LARNGB C | 304424 | LARNBG 2 | 1 | 304057 | DARLINGTON 230.00 | 304954 | DCP#12 13.800 | 1 | 304057-304954-1 | 150 | 150 | 134.5 | 144.3 | 96.2 | 113 | 150 | 120.7 | 132.3 | 88.2 | 52 | -8 | 2021 | 2021 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | 83.2 | 85.6 | 85.2 | 96.2 | 90.9 | 92 | 92.1
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1331 | 1PENROS 44.000 | 1335 | 1PISGAH 44.000 | 1 | 1331-1335-1 | 25.8 | 25.8 | 23.6 | 23.6 | 91.5 | 39 | 25.8 | 21.5 | 21.5 | 83.6 | 26 | -7.9 | 2024 | 2025 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | 20 | 20 | 77 | 3.6 | 14.5 | - | 91.7 | 92.1 | 75.4 | 91.5 | 92 | 91.7 | 75.2
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1271 | 1GEN ELE 44.000 | 1280 | 1HEND MN 44.000 | 1 | 1271-1280-1 | 25.8 | 25.8 | 23.4 | 23.4 | 94.4 | 39 | 25.8 | 21.7 | 21.7 | 86.5 | 39 | -7.9 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | HENDERSONVILLE #1 | 44 kV Line | 0 | 0 | 0 | 25.8 | 20.8 | 20.8 | 83.4 | 2.6 | 11 | - | 94.5 | 95.6 | 77.6 | 94.4 | 94.9 | 94.7 | 77.7
STUDYHAR1VRS | ELZBTHBN | 631 | N CHARLT | 584 | ELIZBETH | 1 | 584 | ELIZBETH 100.00 | 10609 | KENILW B 100.00 | 1 | 584-10609-1 | 141.2 | 141.2 | 68.8 | 135.7 | 97 | 40 | 141.2 | 56.7 | 126.3 | 89.1 | 13 | -7.9 | 2020 | 2021 | 1 |  | 128 | 141.2 | 128 | ELIZABETH BL | 100 kV Line | 127.9948 | 141.2 | 127.9948 | 141.2 | 65.1 | 116.7 | 82.6 | 19 | 14.4 | - | - | 70.9 | 59.7 | 97 | - | 63.1 | -
STUDYHAR1VRS | WESTWOODB | 465 | HICKORY | 471 | LONGVIEW | 1 | 471 | LONGVIEW 100.00 | 499 | THRD A T 100.00 | 1 | 471-499-1 | 173.2 | 173.2 | 123.4 | 160.4 | 90.7 | 78 | 173.2 | 114.1 | 148.3 | 82.9 | 26 | -7.8 | 2025 | 2025 | 0 |  | 173.2 | 173.2 | 173.2 | LONGVIEW | 100 kV Line | 205.7616 | 255.8164 | 205.7616 | 173.2 | 112.2 | 145.2 | 81.7 | 15.2 | 9 | 89.3 | - | 70.9 | 67.9 | 90.7 | 72 | 71.4 | 69
STUDYROX4VRS | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 83.4 | 115.8 | 98.1 | 218 | 116 | 77.7 | 106.7 | 90.4 | 100 | -7.7 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.3 | - | - | - | 98.1 | - | - | -
STUDYVCS1VRS | SINGLE 941 | 304800 | ASHEVILL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100.00 | 190 | PISGAH 100.00 | 1 | 164-190-1 | 108.2 | 108.2 | 50.8 | 98.3 | 93.4 | 27 | 108.2 | 40.6 | 89.8 | 85.8 | 26 | -7.6 | 2023 | 2023 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 45.1 | 88.4 | 76.9 | 9.9 | 16.5 | - | - | 52.5 | - | 93.4 | - | 55.3 | -
STUDYVCS1VRS | SINGLE 941 | 304800 | ASHEVILL | 209 | 3MILLSRV | 1 | 164 | HORSESHO 100.00 | 190 | PISGAH 100.00 | 2 | 164-190-2 | 108.2 | 108.2 | 50.8 | 98.3 | 93.4 | 28 | 108.2 | 40.6 | 89.8 | 85.8 | 26 | -7.6 | 2023 | 2023 | 0 |  | 108.25 | 118.642 | 108.25 | RUGBY | 100 kV Line | 126.436 | 139.5992 | 126.436 | 118.6 | 45.1 | 88.4 | 76.9 | 9.9 | 16.5 | - | - | - | - | 93.4 | - | - | -
STUDYHAR1VRS | LINDENSTW | 726 | BECKRDIT | 980 | HP_CITY4 | 1 | 726 | BECKRDIT 100.00 | 978 | WILOW CK 100.00 | 1 | 726-978-1 | 138.6 | 138.6 | 105.8 | 134.3 | 96.2 | 213 | 138.6 | 98.1 | 124.2 | 88.6 | 156 | -7.6 | 2021 | 2021 | 0 |  | 128 | 138.6 | 128 | LINDEN ST BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 138.6 | 94.5 | 120.6 | 86.1 | 13.7 | 10.1 | - | 78.7 | 79 | 71.5 | 96.2 | 81.8 | 81.7 | 73.9
STUDYASH1VRS | OAKVALE2 | 3183 | OAKVALE2 | 1328 | 1OAKVALE | 2 | 1328 | 1OAKVALE 44.000 | 3183 | OAKVALE2 100.00 | 1 | 1328-3183-1 | 28.1 | 28.1 | 12.5 | 25.6 | 91.1 | 13 | 28.1 | 11.6 | 23.5 | 83.5 | 13 | -7.6 | 2024 | 2025 | 1 |  | 25.7 | 28.1 | 27.8 | OAKVALE TIE 01 | 100/44 kV Transformer | 25.7 | 28.1 | 27.8 | - | - | - | - | - | - | - | - | - | - | 91.1 | - | - | -
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1041 | 1CLARK H 44.000 | 3022 | CLARK H2 100.00 | 1 | 1041-3022-1 | 28.9 | 28.9 | 28.7 | 28.7 | 99.3 | 39 | 28.9 | 26.5 | 26.5 | 91.7 | 39 | -7.6 | 2019 | 2019 | 0 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 30 | 25.8 | 25.8 | 86 | 2.9 | 13.3 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 925 | IMPERALW 100.00 | 10944 | NORTEL W 100.00 | 1 | 925-10944-1 | 130.6 | 130.6 | 119.8 | 119.8 | 92.2 | 39 | 130.6 | 111.7 | 111.7 | 84.7 | 26 | -7.5 | 2024 | 2024 | 0 |  | 130.6 | 161.4 | 130.6 | PANTHER WH | 100 kV Line | 130.5928 | 161.4224 | 130.5928 | 130.6 | 107.6 | 107.6 | 82 | 12.2 | 10.2 | - | 91.6 | 91.9 | 73.9 | 92.2 | 92.4 | 92.3 | 74.3
STUDYROX4VRS | SHELBY4 | 336 | 6SHELBY | 2678 | SHELB 4 | 4 | 1790 | 1SHELBY 44.000 | 2676 | SHELB 2 1.0000 | 2 | 1790-2676-2 | 75 | 75 | 41.2 | 75.8 | 101.1 | 13 | 75 | 38.2 | 70.2 | 93.6 | 13 | -7.5 | 2018 | 2018 | 0 |  | 60 | 75 | 75 | SHELBY TIE 02 TERT | 230/100/44 kV Transformer | 60 | 75 | 75 | 75 | 30.9 | 56.7 | 75.6 | 19.1 | 25.5 | - | 70.7 | 57.3 | 56.4 | 101.1 | 70.6 | 56.4 | 55.8
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 1309 | 1MARIETA 44.000 | 1322 | 1MRRTTA 44.000 | 1 | 1309-1322-1 | 44.7 | 44.7 | 40.8 | 40.8 | 91.7 | 39 | 44.7 | 38 | 38 | 84.3 | 39 | -7.4 | 2024 | 2024 | 0 |  | 44.6532 | 49.149 | 44.6532 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 44.7 | 36 | 36 | 78.9 | 4.8 | 12.8 | - | 92.6 | 93.9 | 83.7 | 91.7 | 92.7 | 92.3 | 83.1
STUDYVCS1VRS | BELTBK3 | 3013 | BELTON2 | 1015 | 1BELTON | 3 | 1015 | 1BELTON 44.000 | 3013 | BELTON2 100.00 | 2 | 1015-3013-2 | 64.3 | 64.3 | 41.2 | 63 | 97.9 | 26 | 64.3 | 38.3 | 58.3 | 90.6 | 26 | -7.3 | 2020 | 2020 | 0 |  | 61.6 | 64.3 | 64.3 | BELTON TIE 02 | 100/44 kV Transformer | 61.6 | 64.3 | 64.3 | 64.3 | 34.8 | 52.5 | 81.7 | 10.5 | 16.2 | - | - | - | - | 97.9 | - | - | -
STUDYASH1VRS | CAMPBLOA | 1246 | 1CAMPOBL | 1518 | 1MASCOTR | 1 | 1411 | 1BRDRV 4 44.000 | 1479 | 1INMAN 44.000 | 1 | 1411-1479-1 | 26.8 | 26.8 | 21.5 | 27.3 | 98 | 52 | 22.2 | 20.7 | 20.7 | 90.7 | 39 | -7.3 | 2020 | 2032 | 12 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | 16.5 | 16.5 | 72.9 | 10.8 | 25.1 | - | 95.4 | 95.5 | 78.8 | 98 | 96.6 | 96 | 79.3
STUDYHAR1VRS | VANWYCK1 | 415 | VAN WYCK | 1829 | 1VANWYCK | 1 | 415 | VAN WYCK 100.00 | 1829 | 1VANWYCK 44.000 | 2 | 415-1829-2 | 27.8 | 27.8 | 9.6 | 27.6 | 99.5 | 13 | 27.8 | 8.9 | 25.6 | 92.2 | 13 | -7.3 | 2019 | 2019 | 0 |  | 26.1 | 28.5 | 27.8 | VAN WYCK TIE 02 | 100/44 kV Transformer | 26.1 | 28.5 | 27.8 | - | - | - | - | - | - | - | - | - | - | 99.5 | - | - | -
STUDYROX4VRS | TAYLORSV2 | 3502 | TYLRSVI2 | 2066 | 1TYLRSVL | 2 | 2066 | 1TYLRSVL 44.000 | 3502 | TYLRSVI2 100.00 | 1 | 2066-3502-1 | 46.8 | 46.8 | 21.6 | 44.1 | 94.3 | 13 | 46.8 | 20.1 | 40.7 | 87.1 | 13 | -7.2 | 2022 | 2022 | 0 |  | 44 | 48.1 | 46.8 | TAYLORSVILLE TIE 01 | 100/44 kV Transformer | 44 | 48.1 | 46.8 | 46.8 | 18.9 | 37 | 79.1 | 7.1 | 15.2 | - | - | - | - | 94.3 | - | - | -
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 195 | SHADY GR 100.00 | 10181 | MOONVI W 100.00 | 1 | 195-10181-1 | 126.4 | 126.4 | 115.8 | 115.8 | 92.4 | 39 | 126.4 | 108.5 | 108.5 | 85.3 | 39 | -7.1 | 2023 | 2024 | 1 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | 95.8 | 95.8 | 74.4 | 20 | 18 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 10180 | MICHMV W 100.00 | 10181 | MOONVI W 100.00 | 1 | 10180-10181-1 | 126.4 | 126.4 | 115.2 | 115.2 | 92.4 | 39 | 126.4 | 108 | 108 | 85.3 | 39 | -7.1 | 2023 | 2024 | 1 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | 95.5 | 95.5 | 74.5 | 19.7 | 17.9 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
STUDYASH1VRS | BASE CASE | 0 |  | 0 |  |  | 103 | 3M TAP 100.00 | 10180 | MICHMV W 100.00 | 1 | 103-10180-1 | 126.1 | 126.1 | 114.9 | 114.9 | 92.6 | 39 | 126.1 | 107.7 | 107.7 | 85.5 | 39 | -7.1 | 2023 | 2023 | 0 |  | 126.1 | 139.4 | 126.1 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.1 | 95.2 | 95.2 | 74.6 | 19.7 | 18 | - | 93.8 | 94.9 | 84.7 | 92.6 | 93.9 | 93.1 | 83.7
STUDYROX4VRS | BASE CASE | 0 |  | 0 |  |  | 2422 | 1ENO 44.000 | 2621 | ENO 3 1.0000 | 3 | 2422-2621-3 | 40 | 40 | 37.6 | 37.6 | 94 | 39 | 40 | 34.7 | 34.7 | 86.9 | 13 | -7.1 | 2022 | 2022 | 0 |  | 40 | 50 | 50 | ENO TIE 03 TERT | 230/100/44 kV Transformer | 40 | 50 | 50 | 50 | 27.7 | 72.9 | 145.9 | -35.3 | -51.9 | - | 95 | 76 | 75.5 | 94 | 96 | 76.8 | 76.3
STUDYROX4VRS | TAYLORSV1 | 3502 | TYLRSVI2 | 2066 | 1TYLRSVL | 1 | 2066 | 1TYLRSVL 44.000 | 3502 | TYLRSVI2 100.00 | 2 | 2066-3502-2 | 46.8 | 46.8 | 21.6 | 44.1 | 94.3 | 13 | 46.8 | 20.1 | 40.8 | 87.2 | 13 | -7.1 | 2022 | 2022 | 0 |  | 44 | 48.1 | 46.8 | TAYLORSVILLE TIE 02 | 100/44 kV Transformer | 44 | 48.1 | 46.8 | 46.8 | 18.8 | 37 | 79.1 | 7.1 | 15.2 | - | - | - | - | 94.3 | - | - | -
STUDYHAR1VRS | BASE CASE | 0 |  | 0 |  |  | 1030 | 1BLREC 7 44.000 | 1206 | 1BEACON 44.000 | 1 | 1030-1206-1 | 31 | 31 | 28.7 | 28.7 | 90.4 | 39 | 31 | 26.9 | 26.9 | 83.5 | 39 | -6.9 | 2025 | 2025 | 0 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | 25.4 | 25.4 | 78.8 | 3.3 | 11.6 | - | 91.1 | 92.9 | 85.4 | 90.4 | 91.2 | 91 | 84.8
STUDYASH1VRS | FIBERLN1 | 9 | ANDERSON | 66 | TOXAWAY | 1 | 9 | ANDERSON 100.00 | 66 | TOXAWAY 100.00 | 2 | 9-66-2 | 346.4 | 346.4 | 205.8 | 341.7 | 95.5 | 13 | 346.4 | 191.9 | 318.9 | 88.6 | 13 | -6.9 | 2021 | 2021 | 0 |  | 346.4 | 346.4 | 346.4 | FIBER BL | 100 kV Line | 440.6208 | 511.4596 | 440.6208 | - | - | - | - | - | - | - | - | - | - | 95.5 | - | - | -
STUDYVCS1VRS | AB_SHADBK1_S | 104 | 6SHADYTB | 109 | 6SHADY G | 1 | 1346 | 1SHADY G 44.000 | 2675 | SHADY 2 1.0000 | 2 | 1346-2675-2 | 105 | 105 | 47 | 94.9 | 90.4 | 39 | 105 | 43.6 | 87.8 | 83.6 | 39 | -6.8 | 2025 | 2025 | 0 |  | 84 | 105 | 105 | SHADY GROVE TIE 02 TERT | 230/100/44 kV Transformer | 84 | 105 | 105 | - | - | - | - | - | - | - | - | - | - | 90.4 | - | - | -
STUDYHAR1VRS | BELTBK2 | 3013 | BELTON2 | 1015 | 1BELTON | 2 | 1015 | 1BELTON 44.000 | 3013 | BELTON2 100.00 | 3 | 1015-3013-3 | 67.7 | 67.7 | 39.2 | 61.5 | 90.9 | 26 | 67.7 | 36.4 | 56.9 | 84.1 | 26 | -6.8 | 2025 | 2024 | -1 |  | 63.7 | 69.6 | 67.7 | BELTON TIE 03 | 100/44 kV Transformer | 63.7 | 69.6 | 67.7 | 67.7 | 33.1 | 51.3 | 75.7 | 10.2 | 15.2 | - | - | - | - | 90.9 | - | - | -
STUDYVCS1VRS | AB_MORNBK4_L | 541 | 6MORN ST | 630 | MORN STR | 4 | 600 | HARRISBG 100.00 | 601 | HCKRY GR 100.00 | 1 | 600-601-1 | 125.6 | 125.6 | 110.5 | 121.2 | 96.9 | 392 | 125.6 | 103.9 | 114 | 90.1 | 309 | -6.8 | 2020 | 2020 | 0 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 125.6 | 85.2 | 96.2 | 76.7 | 25 | 20.2 | - | 96.1 | 103.7 | 88.9 | 96.9 | 97.4 | 93.9 | 84.7
STUDYVCS1VRS | BELTBK2 | 3013 | BELTON2 | 1015 | 1BELTON | 2 | 1015 | 1BELTON 44.000 | 3013 | BELTON2 100.00 | 1 | 1015-3013-1 | 66.5 | 66.5 | 38.7 | 60.7 | 91.3 | 26 | 66.5 | 35.9 | 56.2 | 84.5 | 26 | -6.8 | 2024 | 2024 | 0 |  | 63.7 | 66.5 | 66.5 | BELTON TIE 01 | 100/44 kV Transformer | 63.7 | 66.5 | 66.5 | 66.5 | 32.6 | 50.6 | 76.1 | 10.1 | 15.2 | - | - | 57.4 | 56.9 | 91.3 | - | 57 | 56.6
STUDYVCS1VRS | CENTRALBK3 | 4 | 6CENTRAL | 2613 | CENTRL 3 | 3 | 4 | 6CENTRAL 230.00 | 2611 | CENTRL 1 1.0000 | 1 | 4-2611-1 | 265.2 | 265.2 | 196 | 260.1 | 98.1 | 183 | 265.2 | 182.7 | 242.2 | 91.3 | 78 | -6.8 | 2020 | 2019 | -1 |  | 247.7 | 276.9 | 265.2 | CENTRAL TIE 01 | 230/100/44 kV Transformer | 247.7 | 276.9 | 269.9 | 265.2 | 158 | 213.1 | 80.4 | 47 | 17.7 | - | 79.1 | 75.8 | 68.9 | 98.1 | 79.4 | 74.2 | 67.9
STUDYROX4VRS | STAMEY1 | 445 | 6STAMEY | 490 | STAMEY | 1 | 445 | 6STAMEY 230.00 | 490 | STAMEY 100.00 | 2 | 445-490-2 | 620.2 | 620.2 | 368.4 | 610.2 | 98.4 | 13 | 620.2 | 344.6 | 568.6 | 91.7 | 13 | -6.7 | 2020 | 2019 | -1 |  | 575.8 | 661.6 | 620.2 | STAMEY TIE 02 | 230/100 kV Transformer | 575.8 | 661.6 | 620.2 | 620.2 | 338 | 557.9 | 90 | 52.3 | 8.4 | - | - | - | - | 98.4 | - | - | -
STUDYASH1VRS | CLIFSBK1 | 234 | 6CLIFSID | 2615 | CLIFF A1 | A1 | 254 | GAFFNEY 100.00 | 324 | CHEROKEE 100.00 | 1 | 254-324-1 | 125.6 | 125.6 | 112.9 | 122.7 | 96.8 | 111 | 125.6 | 106.2 | 115.5 | 90.3 | 108 | -6.5 | 2021 | 2020 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 125.6 | 96.7 | 104.4 | 82.6 | 18.3 | 14.2 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
STUDYROX4VRS | STAMEY2 | 445 | 6STAMEY | 490 | STAMEY | 2 | 445 | 6STAMEY 230.00 | 490 | STAMEY 100.00 | 1 | 445-490-1 | 668 | 668 | 376.6 | 615.1 | 92.1 | 13 | 668 | 352.3 | 573.2 | 85.8 | 13 | -6.3 | 2024 | 2023 | -1 |  | 613 | 669.2 | 668 | STAMEY TIE 01 | 230/100 kV Transformer | 613.2 | 672 | 668 | 668 | 345.5 | 562.3 | 84.2 | 52.8 | 7.9 | - | - | 57.3 | 55.2 | 92.1 | - | 55.5 | 53.9
STUDYASH1VRS | INMANK3 | 3260 | INMAN 2 | 1479 | 1INMAN | 3 | 1479 | 1INMAN 44.000 | 3260 | INMAN 2 100.00 | 2 | 1479-3260-2 | 28.4 | 28.4 | 20.4 | 25.9 | 91.2 | 52 | 28.4 | 19.1 | 24.2 | 85.1 | 24 | -6.1 | 2024 | 2024 | 0 |  | 26.7 | 29.2 | 28.4 | INMAN TIE 02 | 100/44 kV Transformer | 26.7 | 29.2 | 28.4 | 28.4 | 18.8 | 23.8 | 83.9 | 2.1 | 7.3 | - | - | - | - | 91.2 | - | - | -
STUDYASH1VRS | INMANBK2 | 3260 | INMAN 2 | 1479 | 1INMAN | 2 | 1479 | 1INMAN 44.000 | 3260 | INMAN 2 100.00 | 3 | 1479-3260-3 | 28.4 | 28.4 | 20.4 | 25.9 | 91.1 | 52 | 28.4 | 19.1 | 24.2 | 85 | 15 | -6.1 | 2024 | 2024 | 0 |  | 26.8 | 29.2 | 28.4 | INMAN TIE 03 | 100/44 kV Transformer | 26.8 | 29.2 | 28.4 | 28.4 | 18.7 | 23.8 | 83.9 | 2.1 | 7.2 | - | - | - | - | 91.1 | - | - | -
STUDYNAN1VRS | BECKERD4 | 713 | 6BECKRDT | 726 | BECKRDIT | 4 | 713 | 6BECKRDT 230.00 | 726 | BECKRDIT 100.00 | 2 | 713-726-2 | 275.6 | 275.6 | 216.7 | 273.3 | 99.2 | 376 | 275.6 | 203.6 | 256.8 | 93.2 | 307 | -6 | 2019 | 2018 | -1 |  | 252.8 | 278 | 275.6 | BECKERDITE TIE 02 | 230/100 kV Transformer | 252.8 | 278 | 275.6 | 275.6 | 193.1 | 243.4 | 88.3 | 29.9 | 10.9 | - | - | - | - | 99.2 | - | - | -
STUDYNAN1VRS | BECKERD4 | 713 | 6BECKRDT | 726 | BECKRDIT | 4 | 713 | 6BECKRDT 230.00 | 726 | BECKRDIT 100.00 | 3 | 713-726-3 | 271 | 271 | 216.9 | 273.5 | 100.9 | 377 | 271 | 203.8 | 257.1 | 94.9 | 338 | -6 | 2018 | 2017 | -1 |  | 251.9 | 271 | 271 | BECKERDITE TIE 03 | 230/100 kV Transformer | 251.9 | 271 | 271 | 271 | 193.3 | 243.6 | 89.9 | 29.9 | 11 | - | - | - | - | 100.9 | - | - | -
STUDYRCH1VRS | AB_STEEL_W_S | 331 | 6ALLEN | 545 | 6WOODLWN | 2 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 1 | 331-545-1 | 717 | 717 | 444.1 | 649.5 | 92.2 | 13 | 717 | 420 | 614.1 | 86.3 | 13 | -5.9 | 2024 | 2023 | -1 |  | 717 | 717 | 717 | STEELBERRY WH | 230 kV Line | 792.617 | 996.5466 | 792.617 | - | - | - | - | - | - | 94.9 | - | 65.6 | 63.7 | 92.2 | - | 64.7 | 61.9
STUDYRCH1VRS | AB_STEEL_B_S | 331 | 6ALLEN | 545 | 6WOODLWN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 444.1 | 649.4 | 92.2 | 39 | 717 | 420 | 613.9 | 86.3 | 39 | -5.9 | 2024 | 2023 | -1 |  | 717 | 717 | 717 | STEELBERRY BL | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 425.3 | 630.3 | 89 | 19.1 | 3.2 | 94.9 | - | - | - | 92.2 | - | - | -
STUDYVCS1VRS | ECHOW | 164 | HORSESHO | 10120 | ASHVHWYW | 1 | 164 | HORSESHO 100.00 | 2471 | NIXRDTAP 100.00 | 1 | 164-2471-1 | 138.6 | 138.6 | 104.2 | 129.7 | 95.7 | 93 | 138.6 | 97.3 | 121.7 | 89.8 | 65 | -5.9 | 2021 | 2020 | -1 |  | 126.4 | 138.6 | 126.4 | ECHO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | 88.1 | 88.1 | 71 | 41.6 | 24.7 | - | 89.6 | 95.7 | 82 | 95.7 | 88.5 | 89.4 | 77.4
STUDYASH1VRS | HENDBK3 | 3163 | HNDRSNV2 | 1283 | 1HNDRSNV | 3 | 1246 | 1CAMPOBL 44.000 | 1343 | 1S MER T 44.000 | 1 | 1246-1343-1 | 22.2 | 22.2 | 15.1 | 20.9 | 94.9 | 27 | 22.2 | 14.6 | 19.9 | 89.1 | 38 | -5.8 | 2022 | 2021 | -1 |  | 22.2504 | 27.051 | 22.2504 | TUXEDO B | 44 kV Line | 0 | 0 | 0 | 22.2 | 14.7 | 19.7 | 88.3 | 1.2 | 6.6 | - | - | 64.3 | 52.4 | 94.9 | - | 68.7 | 56.1
STUDYASH1VRS | TIGERBK6 | 111 | 6_TIGER | 2694 | TIGER 6 | 6 | 269 | LAWSONFK 100.00 | 290 | PINEWOOD 100.00 | 1 | 269-290-1 | 126.4 | 126.4 | 114 | 129.1 | 103.4 | 130 | 126.4 | 109.5 | 123.8 | 97.6 | 130 | -5.8 | 2018 | 2015 | -3 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 139.4 | 91.6 | 130.4 | 93.3 | -1.3 | 10.1 | - | 90.3 | 94.5 | 84.3 | 103.4 | 92.2 | 94.3 | 84.9
STUDYASH1VRS | HENDBK3 | 3163 | HNDRSNV2 | 1283 | 1HNDRSNV | 3 | 1343 | 1S MER T 44.000 | 1598 | 1TRYN RT 44.000 | 1 | 1343-1598-1 | 22.2 | 22.2 | 14.6 | 20 | 94.7 | 26 | 22.2 | 14.1 | 19.2 | 88.9 | 25 | -5.8 | 2022 | 2021 | -1 |  | 22.2504 | 27.051 | 22.2504 | TUXEDO B | 44 kV Line | 0 | 0 | 0 | - | - | - | - | - | - | - | - | 64.1 | 52.3 | 94.7 | - | 68.5 | 55.9
STUDYNAN1VRS | BECKERD4 | 713 | 6BECKRDT | 726 | BECKRDIT | 4 | 713 | 6BECKRDT 230.00 | 726 | BECKRDIT 100.00 | 1 | 713-726-1 | 273.1 | 273.1 | 211.6 | 266.9 | 97.7 | 362 | 273.1 | 198.9 | 250.9 | 91.9 | 262 | -5.8 | 2020 | 2019 | -1 |  | 260.3 | 273.1 | 273.1 | BECKERDITE TIE 01 | 230/100 kV Transformer | 260.3 | 273.1 | 273.1 | 273.1 | 188.5 | 237.6 | 87 | 29.3 | 10.7 | - | 80.9 | 79.1 | 76.6 | 97.7 | 81.5 | 78.6 | 75.7
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 154.6 | 580.2 | 99.5 | 14 | 590 | 145.5 | 551.3 | 93.8 | 13 | -5.7 | 2019 | 2018 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.4 | - | - | - | 99.5 | - | - | -
STUDYROX4VRS | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 483.4 | 821.8 | 103.2 | 26 | 796.7 | 456.4 | 776.7 | 97.5 | 19 | -5.7 | 2018 | 2015 | -3 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 437 | 747.5 | 93.8 | 74.3 | 9.4 | 93.8 | - | 54.3 | 50.7 | 103.2 | - | - | -
STUDYVCS1VRS | NGRNVBK3 | 107 | 6N GRNVL | 2647 | N GRNV 3 | 3 | 107 | 6N GRNVL 230.00 | 2646 | N GRNV 2 1.0000 | 2 | 107-2646-2 | 224.1 | 224.1 | 179.3 | 213.1 | 95.1 | 404 | 224.1 | 168.8 | 200.7 | 89.6 | 284 | -5.5 | 2022 | 2020 | -2 |  | 224.1 | 239 | 224.1 | N GREENVILLE TIE 02 | 230/100/44 kV Transformer | 251.1 | 280.9 | 273.7 | 224.1 | 155.1 | 184.6 | 82.4 | 28.5 | 12.7 | - | 81.4 | 82.9 | 73.9 | 95.1 | 81.8 | 81.9 | 73.2
STUDYVCS1VRS | NGRNVBK3 | 107 | 6N GRNVL | 2647 | N GRNV 3 | 3 | 107 | 6N GRNVL 230.00 | 2645 | N GRNV 1 1.0000 | 1 | 107-2645-1 | 224.1 | 224.1 | 174.7 | 206.6 | 92.2 | 337 | 224.1 | 164.5 | 194.5 | 86.8 | 273 | -5.4 | 2024 | 2022 | -2 |  | 224.1 | 239 | 224.1 | N GREENVILLE TIE 01 | 230/100/44 kV Transformer | 258.9 | 239 | 224.1 | 224.1 | 151.3 | 179.2 | 80 | 27.4 | 12.2 | - | 79.3 | 80.7 | 72 | 92.2 | 79.7 | 79.8 | 71.4
STUDYHAR1VRS | SINGLE 424 | 304348 | ROCKHM23 | 304378 | RICH230 | 2 | 304348 | ROCKHM230 TT230.00 | 304378 | RICH230 TT 230.00 | 1 | 304348-304378-1 | 1014 | 1014 | 589.1 | 938.7 | 91.1 | 35 | 1014 | 554.3 | 886 | 85.7 | 14 | -5.4 | 2024 | 2023 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | - | - | 58.2 | 91.1 | - | - | 57.7
STUDYROX4VRS | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 466.9 | 814.2 | 96.9 | 16 | 840 | 440.8 | 769 | 91.6 | 13 | -5.3 | 2020 | 2019 | -1 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 422.1 | 740.8 | 88.2 | 73.4 | 8.7 | 88.2 | - | - | - | 96.9 | - | 55 | 51.7
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304550 | CASTLE HAYNE230.00 | 304577 | MURRAYVL 230.00 | 1 | 304550-304577-1 | 590 | 590 | 121.7 | 549.6 | 94.2 | 13 | 590 | 116.6 | 523.3 | 89 | 13 | -5.2 | 2022 | 2021 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93 | - | - | - | 94.2 | - | - | -
STUDYRCH1VRS | WOODLAWNBK4 | 545 | 6WOODLWN | 2688 | WOODL 4 | 4 | 545 | 6WOODLWN 230.00 | 2689 | WOODL 5 1.0000 | 5 | 545-2689-5 | 415.7 | 415.7 | 295.6 | 377.7 | 90.9 | 457 | 415.7 | 279.3 | 356.8 | 85.8 | 129 | -5.1 | 2025 | 2023 | -2 |  | 346.4 | 415.7 | 415.7 | WOODLAWN TIE 05 | 230/100/44 kV Transformer | 395.5 | 415.7 | 415.7 | 415.7 | 283.1 | 364.4 | 87.6 | 13.3 | 3.3 | - | 88.4 | 75.3 | 73.1 | 90.9 | 89 | 74.2 | 71.1
STUDYVCS1VRS | NGRNVBK3 | 107 | 6N GRNVL | 2647 | N GRNV 3 | 3 | 182 | N GRNVLE 100.00 | 2646 | N GRNV 2 1.0000 | 2 | 182-2646-2 | 224.1 | 224.1 | 167.6 | 202.1 | 90.2 | 287 | 224.1 | 158.3 | 190.9 | 85.2 | 187 | -5 | 2025 | 2024 | -1 |  | 224.1 | 239 | 224.1 | N GREENVILLE TIE 02 | 230/100/44 kV Transformer | 251.1 | 280.9 | 273.7 | 224.1 | 144.3 | 174.7 | 78 | 27.4 | 12.2 | - | 73.9 | 75.3 | 66.9 | 90.2 | 74.3 | 74.4 | 66.3
STUDYRCH1VRS | WOODLAWNBK4 | 545 | 6WOODLWN | 2688 | WOODL 4 | 4 | 545 | 6WOODLWN 230.00 | 2690 | WOODL 6 1.0000 | 6 | 545-2690-6 | 415.7 | 415.7 | 295.9 | 378 | 90.9 | 485 | 415.7 | 279.5 | 357.1 | 85.9 | 155 | -5 | 2025 | 2023 | -2 |  | 346.4 | 415.7 | 415.7 | WOODLAWN TIE 06 | 230/100/44 kV Transformer | 395 | 452.2 | 424.6 | 415.7 | 283.4 | 364.7 | 87.7 | 13.3 | 3.2 | - | 88.5 | 75.4 | 73.2 | 90.9 | 89 | 74.3 | 71.2
STUDYBRN1VRS | SINGLE 454 | 304369 | FAY EAST | 304389 | P2-FAY E | 1 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 2 | 304369-304389-2 | 150 | 150 | 116.3 | 233.3 | 155.6 | 52 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | - | - | - | 155.6 | - | - | -
STUDYROX4VRS | SINGLE 455 | 304369 | FAY EAST | 304389 | P2-FAY E | 2 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 1 | 304369-304389-1 | 150 | 150 | 117 | 233.2 | 155.5 | 52 | - | - | - | - | - | - | 2018 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | 76.7 | 77.9 | 77.9 | 155.5 | 79.6 | 80.7 | 80.8
STUDYVCS1VRS | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 400.2 | 705.6 | 109.2 | 39 | - | - | - | - | - | - | 2018 | - | - |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 121.7 | 74.3 | 82.8 | 69.5 | 109.2 | 74.2 | 74.7 | 62.5
STUDYHAR1VRS | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 37.1 | 76.9 | 100.6 | 13 | - | - | - | - | - | - | 2018 | - | - |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 43.6 | 63 | 83.8 | 13.9 | 16.8 | 100.8 | - | - | - | 100.6 | - | - | -
STUDYRCH1VRS | MONROEBLLAN | 380 | LANCASTR | 392 | RED ROSE | 1 | 10107 | MINIRANT 100.00 | 10381 | LAN R WH 100.00 | 1 | 10107-10381-1 | 71.2 | 71.2 | 45.1 | 72.7 | 100.6 | 145 | - | - | - | - | - | - | 2018 | - | - |  | 58.5 | 71.2 | 58.5 | MONROE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 58.5 | 38.7 | 49 | 83.9 | 23.7 | 16.7 | - | 79.7 | 81.7 | 63.1 | 100.6 | 82 | 79.2 | 61.1
STUDYRCH1VRS | MONROEBLLAN | 380 | LANCASTR | 392 | RED ROSE | 1 | 10381 | LAN R WH 100.00 | 10392 | RED R WH 100.00 | 1 | 10381-10392-1 | 71.2 | 71.2 | 45.3 | 73.1 | 100.6 | 145 | - | - | - | - | - | - | 2018 | - | - |  | 58.5 | 71.2 | 58.5 | MONROE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 37.9 | 78.3 | 110.1 | -5.2 | -9.5 | - | 79.7 | 81.7 | 63.1 | 100.6 | 82 | 79.2 | 61.1
STUDYROX4VRS | EASTRVR | 2181 | 1MTN ISL | 2235 | 1GASTPMP | 1 | 2181 | 1MTN ISL 44.000 | 2406 | 1NGFLTAP 44.000 | 1 | 2181-2406-1 | 49.5 | 49.5 | 32.2 | 52 | 100.5 | 13 | - | - | - | - | - | - | 2018 | - | - |  | 49.5 | 49.5 | 49.5 | WEST RIVER | 44 kV Line | 0 | 0 | 0 | - | - | - | - | - | - | - | - | 63.9 | 62.2 | 100.5 | - | 63.2 | 61.8
STUDYHAR1VRS | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304406 | ST PAULS 115.00 | 304412 | FLOR DUP SW 115.00 | 1 | 304406-304412-1 | 119 | 119 | 86.9 | 111.3 | 95.7 | 228 | - | - | - | - | - | - | 2021 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | 70.8 | - | 74.6 | 95.7 | 77.5 | - | 78.7
STUDYHAR1VRS | SINGLE 635 | 304540 | GEIGER T | 304542 | FOLKSTN | 1 | 304543 | FOLKSTN 115 115.00 | 305061 | E9-DAWSON 115.00 | 1 | 304543-305061-1 | 158 | 158 | 80.7 | 148.9 | 94.3 | 25 | - | - | - | - | - | - | 2022 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | 51.4 | 94.3 | - | - | 52.5
STUDYHAR1VRS | WESTRVR | 2181 | 1MTN ISL | 2406 | 1NGFLTAP | 1 | 2181 | 1MTN ISL 44.000 | 2235 | 1GASTPMP 44.000 | 1 | 2181-2235-1 | 49.5 | 49.5 | 25.1 | 49.2 | 94.2 | 13 | - | - | - | - | - | - | 2022 | - | - |  | 49.5 | 49.5 | 49.5 | EAST RIVER | 44 kV Line | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | 94.2 | - | - | -
STUDYHAR1VRS | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304251 | LEE230 SUB 230.00 | 304958 | WYNCO#3 18.000 | 1 | 304251-304958-1 | 220 | 220 | 198.5 | 206.7 | 94 | 113 | - | - | - | - | - | - | 2022 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.9 | 83.7 | 85 | 84.7 | 94 | 87.6 | 88.4 | 88.5
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 147 | EITAP 100.00 | 230 | BLREC23 100.00 | 1 | 147-230-1 | 86.6 | 86.6 | 11.5 | 80.6 | 92.9 | 1 | - | - | - | - | - | - | 2023 | - | - |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER WH | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | 75.5 | - | - | - | 92.9 | - | - | -
STUDYROX4VRS | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 790 | SADLER 100.00 | 2679 | SADLE 3 1.0000 | 3 | 790-2679-3 | 553.7 | 553.7 | 278.6 | 514 | 92.8 | 13 | - | - | - | - | - | - | 2023 | - | - |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 202.7 | 391.3 | 70.7 | 122.7 | 22.1 | 108.4 | - | 67 | 56.6 | 92.8 | - | 63 | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 147 | EITAP 100.00 | 190 | PISGAH 100.00 | 1 | 147-190-1 | 86.6 | 86.6 | 11.1 | 80.8 | 92.7 | 1 | - | - | - | - | - | - | 2023 | - | - |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER WH | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | 75.2 | - | - | - | 92.7 | - | - | -
STUDYHAR1VRS | SINGLE 613 | 304519 | M-TARAWA | 304524 | JACKSV23 | 1 | 304251 | LEE230 SUB 230.00 | 304959 | WYNCO#4 18.000 | 1 | 304251-304959-1 | 220 | 220 | 194.9 | 203.2 | 92.4 | 114 | - | - | - | - | - | - | 2023 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 88.4 | 82.1 | 83.4 | 83.1 | 92.4 | 85.9 | 86.7 | 86.8
STUDYROX4VRS | WESTRVR | 2181 | 1MTN ISL | 2406 | 1NGFLTAP | 1 | 2191 | 1RIVRBND 44.000 | 2235 | 1GASTPMP 44.000 | 1 | 2191-2235-1 | 49.5 | 49.5 | 23 | 47.4 | 90.7 | 13 | - | - | - | - | - | - | 2025 | - | - |  | 47.6 | 49.5 | 47.6 | EAST RIVER | 44 kV Line | 0 | 0 | 0 | - | - | - | - | - | - | - | - | - | - | 90.7 | - | - | -
STUDYHAR1VRS | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 387.7 | 601.8 | 110.8 | 78 | 539 | 354 | 548.6 | 100.4 | 17 | -10.4 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.6 | - | - | 64 | 110.8 | 72.3 | - | 70.5
STUDYVCS1VRS | SHELBY2 | 336 | 6SHELBY | 2676 | SHELB 2 | 2 | 1790 | 1SHELBY 44.000 | 2678 | SHELB 4 1.0000 | 4 | 1790-2678-4 | 70.7 | 70.7 | 33.5 | 76.7 | 108.5 | 13 | 70.7 | 31.1 | 71 | 100.4 | 13 | -8.1 | 2018 | 2013 | -5 |  | 56.7 | 70.7 | 70.7 | SHELBY TIE 04 TERT | 230/100/44 kV Transformer | 56.7 | 70.7 | 70.7 | 70.7 | 25.3 | 57 | 80.7 | 19.7 | 27.8 | - | - | - | - | 108.5 | - | - | -
STUDYROX4VRS | LANCA1 | 3380 | LANCAST2 | 1726 | 1LANCSTR | 1 | 1726 | 1LANCSTR 44.000 | 3380 | LANCAST2 100.00 | 2 | 1726-3380-2 | 30.5 | 30.5 | 16.8 | 33.6 | 110.3 | 13 | 30.5 | 15.5 | 30.7 | 100.8 | 13 | -9.5 | 2018 | 2013 | -5 |  | 28.1 | 30.5 | 28.5 | LANCASTER MN 02 | 100/44 kV Transformer | 28.1 | 31.5 | 30.4 | 30.5 | 15.5 | 30 | 98.3 | 3.6 | 12 | - | - | - | - | 110.3 | - | - | -
STUDYASH1VRS | ODELL1 | 687 | WINECOFF | 681 | WESTFORK | 1 | 570 | COL P KN 100.00 | 687 | WINECOFF 100.00 | 1 | 570-687-1 | 129.9 | 129.9 | 124.5 | 160.3 | 119.3 | 192 | 129.9 | 106.8 | 137.1 | 100.9 | 169 | -18.4 | 2018 | 2013 | -5 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 129.9 | 81.6 | 105.1 | 81 | 55.2 | 38.3 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 203.9 | 627.2 | 107.6 | 14 | 590 | 190.4 | 595.6 | 101.3 | 14 | -6.3 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 106.5 | - | - | - | 107.6 | - | - | -
STUDYASH1VRS | ODELL1 | 687 | WINECOFF | 681 | WESTFORK | 1 | 570 | COL P KN 100.00 | 681 | WESTFORK 100.00 | 1 | 570-681-1 | 118.6 | 118.6 | 111.4 | 145.4 | 121.7 | 190 | 118.6 | 96 | 125.3 | 102.6 | 169 | -19.1 | 2018 | 2013 | -5 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.6 | 81.6 | 104 | 87.8 | 41.4 | 33.9 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
STUDYROX4VRS | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 82 | 113 | 111.5 | 311 | 102 | 76.5 | 104.6 | 102.8 | 232 | -8.7 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 127.6 | - | - | - | 111.5 | - | - | -
STUDYVCS1VRS | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 70.4 | 70.4 | 140.9 | 26 | 50 | 51.6 | 51.6 | 103.1 | 26 | -37.8 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
STUDYVCS1VRS | MULLW | 465 | HICKORY | 483 | NEWTON T | 1 | 465 | HICKORY 100.00 | 10423 | ZIONCTAP 100.00 | 1 | 465-10423-1 | 141.2 | 141.2 | 87.4 | 173.9 | 123.8 | 65 | 141.2 | 71.7 | 147.6 | 103.1 | 13 | -20.7 | 2018 | 2013 | -5 |  | 103.9 | 141.2 | 128 | MULL BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 104 | 68.1 | 81 | 76.9 | 92.9 | 46.9 | - | 83 | 73.9 | 60.9 | 123.8 | 86.6 | 70.4 | 61.2
STUDYASH1VRS | CLOVER2 | 3354 | CLOVER2 | 1663 | 1CLOVER | 2 | 1663 | 1CLOVER 44.000 | 3354 | CLOVER2 100.00 | 1 | 1663-3354-1 | 75.7 | 75.7 | 44 | 86.9 | 114.8 | 13 | 75.7 | 40.3 | 78.3 | 103.5 | 13 | -11.3 | 2018 | 2013 | -5 |  | 71.3 | 77.8 | 75.7 | CLOVER TIE 01 | 100/44 kV Transformer | 71.3 | 77.8 | 75.7 | 75.7 | 35.5 | 68.2 | 90.1 | 18.7 | 24.7 | - | - | 60.1 | 58.1 | 114.8 | - | 59.7 | 56.7
STUDYASH1VRS | CLOVER1 | 3354 | CLOVER2 | 1663 | 1CLOVER | 1 | 1663 | 1CLOVER 44.000 | 3354 | CLOVER2 100.00 | 2 | 1663-3354-2 | 75.7 | 75.7 | 44.7 | 86.8 | 114.7 | 13 | 75.7 | 41.1 | 78.4 | 103.6 | 13 | -11.1 | 2018 | 2013 | -5 |  | 71.4 | 77.9 | 75.7 | CLOVER TIE 02 | 100/44 kV Transformer | 71.3 | 77.8 | 75.7 | 75.7 | 36.1 | 68.3 | 90.2 | 18.5 | 24.5 | - | - | - | - | 114.7 | - | - | -
STUDYVCS1VRS | CORONBK2 | 28 | CORONACA | 1049 | 1CORONAC | 2 | 28 | CORONACA 100.00 | 1049 | 1CORONAC 44.000 | 4 | 28-1049-4 | 55.4 | 55.4 | 42.3 | 62.2 | 112.2 | 52 | 55.4 | 39.4 | 57.5 | 103.7 | 52 | -8.5 | 2018 | 2013 | -5 |  | 45.7 | 64.1 | 55.4 | CORONACA TIE 04 | 100/44 kV Transformer | 61.4 | 64.1 | 64.1 | 55.4 | 37.8 | 54.9 | 99.1 | 7.3 | 13.1 | - | - | - | - | 112.2 | - | - | -
STUDYVCS1VRS | CORONBK4 | 28 | CORONACA | 1049 | 1CORONAC | 4 | 28 | CORONACA 100.00 | 1049 | 1CORONAC 44.000 | 3 | 28-1049-3 | 45.7 | 45.7 | 29 | 52.1 | 114 | 26 | 45.7 | 27 | 47.8 | 104.7 | 26 | -9.3 | 2018 | 2013 | -5 |  | 43.4 | 45.7 | 45.7 | CORONACA TIE 03 | 100/44 kV Transformer | 43.4 | 47.5 | 46.1 | 45.7 | 25.9 | 45.4 | 99.2 | 6.7 | 14.8 | - | - | - | - | 114 | - | - | -
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 141.9 | 234.4 | 118.3 | 182 | 196.8 | 128.4 | 212.3 | 105.7 | 63 | -12.6 | 2018 | 2013 | -5 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 110 | 73.8 | 73.7 | 64.3 | 118.3 | 79.7 | 79.4 | 69.4
STUDYROX4VRS | WALNUTCO1 | 809 | WALNUT C | 2371 | 1WALNTCV | 1 | 809 | WALNUT C 100.00 | 2371 | 1WALNTCV 44.000 | 2 | 809-2371-2 | 45.7 | 45.7 | 26.5 | 52.4 | 114.6 | 13 | 45.7 | 24.7 | 48.3 | 105.7 | 13 | -8.9 | 2018 | 2013 | -5 |  | 45.7 | 45.7 | 45.7 | WALNUT COVE TIE 02 | 100/44 kV Transformer | 46.1 | 50.3 | 49 | 45.7 | 25.3 | 49.8 | 109 | 2.6 | 5.6 | - | - | - | - | 114.6 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 220 | 1BLREC25 100.00 | 10177 | MARIETBL 100.00 | 1 | 220-10177-1 | 86.6 | 86.6 | 44 | 112.9 | 131.2 | 13 | 86.6 | 37.3 | 92 | 105.8 | 13 | -25.4 | 2018 | 2013 | -5 |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER BL | 100 kV Line | 86.6 | 106 | 86.6 | - | - | - | - | - | - | - | - | - | - | 131.2 | - | 50.7 | -
STUDYROX4VRS | WALNUTCO2 | 809 | WALNUT C | 2371 | 1WALNTCV | 2 | 809 | WALNUT C 100.00 | 2371 | 1WALNTCV 44.000 | 1 | 809-2371-1 | 45.7 | 45.7 | 25.3 | 52.5 | 115 | 13 | 45.7 | 23.6 | 48.3 | 105.8 | 13 | -9.2 | 2018 | 2013 | -5 |  | 43.7 | 45.7 | 45.7 | WALNUT COVE TIE 01 | 100/44 kV Transformer | 43.7 | 47.7 | 46.4 | 45.7 | 23.3 | 50.4 | 110.2 | 2.1 | 4.8 | - | - | 54.8 | 54.2 | 115 | - | 54.6 | 54.2
STUDYHAR1VRS | SWEPSONVILL3 | 3964 | SWEPSVI2 | 2448 | 1SWEPSVL | 3 | 2448 | 1SWEPSVL 44.000 | 3964 | SWEPSVI2 100.00 | 2 | 2448-3964-2 | 44.8 | 44.8 | 25.2 | 53.2 | 118.7 | 13 | 44.8 | 23.2 | 47.9 | 106.9 | 13 | -11.8 | 2018 | 2013 | -5 |  | 42.9 | 44.8 | 44.8 | SWEPSONVILLE TIE 02 | 100/44 kV Transformer | 42.9 | 44.8 | 44.8 | 44.8 | 19.9 | 39.2 | 87.6 | 14 | 31.1 | - | - | 57.3 | 57 | 118.7 | - | 57.7 | 57.4
STUDYHAR1VRS | SWEPSONVILL2 | 3964 | SWEPSVI2 | 2448 | 1SWEPSVL | 2 | 2448 | 1SWEPSVL 44.000 | 3964 | SWEPSVI2 100.00 | 3 | 2448-3964-3 | 44.8 | 44.8 | 25.1 | 53.3 | 118.9 | 13 | 44.8 | 23.1 | 47.9 | 107 | 13 | -11.9 | 2018 | 2013 | -5 |  | 42.9 | 44.8 | 44.8 | SWEPSONVILLE TIE 03 | 100/44 kV Transformer | 42.9 | 44.8 | 44.8 | 44.8 | 19.8 | 39.2 | 87.6 | 14.1 | 31.3 | - | - | - | - | 118.9 | - | - | -
STUDYBRN1VRS | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 107.8 | 237.5 | 116.8 | 20 | 201 | 99 | 218.2 | 107.2 | 13 | -9.6 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | - | - | - | 116.8 | - | - | 52.5
STUDYASH1VRS | HENDBK3 | 3163 | HNDRSNV2 | 1283 | 1HNDRSNV | 3 | 1246 | 1CAMPOBL 44.000 | 1304 | 1LANDRUM 44.000 | 1 | 1246-1304-1 | 22.2 | 22.2 | 19.5 | 25.3 | 115.1 | 56 | 22.2 | 18.7 | 24 | 107.5 | 64 | -7.6 | 2018 | 2013 | -5 |  | 22.2504 | 27.051 | 22.2504 | TUXEDO A | 44 kV Line | 0 | 0 | 0 | 22.2 | 18 | 23.1 | 103.3 | 2.2 | 11.8 | - | 84.4 | 84.6 | 69 | 115.1 | 89.4 | 88.9 | 72.6
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 116 | 143.4 | 124.5 | 143 | 113.1 | 100.8 | 124.6 | 107.6 | 117 | -16.9 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 83.3 | 97.3 | 84.3 | 46.1 | 40.2 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
STUDYHAR1VRS | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 258.1 | 681.5 | 116.6 | 55 | 590 | 241.6 | 648.4 | 109.8 | 17 | -6.8 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.6 | - | - | - | 116.6 | - | - | 55.5
STUDYROX4VRS | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 897 | GLEN RVN 100.00 | 1 | 857-897-1 | 207.8 | 207.8 | 164.5 | 257.6 | 122.7 | 271 | 207.8 | 149.2 | 233.3 | 109.9 | 104 | -12.8 | 2018 | 2013 | -5 |  | 207.8 | 207.8 | 207.8 | ALAMANCE BL | 100 kV Line | 282.4892 | 327.0016 | 282.4892 | 207.8 | 122.6 | 153 | 73.4 | 104.6 | 49.3 | - | 73.8 | 73.8 | 71.5 | 122.7 | 79 | 78.6 | 76.4
STUDYASH1VRS | WALHABK4 | 3069 | WALHALL2 | 1177 | 1WALHALA | 4 | 1177 | 1WALHALA 44.000 | 3069 | WALHALL2 100.00 | 3 | 1177-3069-3 | 25.3 | 25.3 | 19.6 | 30.8 | 121.6 | 65 | 25.3 | 18.1 | 27.9 | 110.2 | 52 | -11.4 | 2018 | 2013 | -5 |  | 23.5 | 26.1 | 25.3 | WALHALLA TIE 03 | 100/44 kV Transformer | 23.5 | 26.1 | 25.3 | 25.3 | 16.9 | 25.7 | 101.5 | 5.1 | 20.1 | - | - | - | - | 121.6 | - | - | -
STUDYASH1VRS | WALHABK4 | 3069 | WALHALL2 | 1177 | 1WALHALA | 4 | 1177 | 1WALHALA 44.000 | 3069 | WALHALL2 100.00 | 2 | 1177-3069-2 | 25.3 | 25.3 | 19.7 | 31 | 122.4 | 65 | 25.3 | 18.2 | 28.1 | 110.9 | 52 | -11.5 | 2018 | 2013 | -5 |  | 23.5 | 26.1 | 25.3 | WALHALLA TIE 02 | 100/44 kV Transformer | 23.5 | 26.1 | 25.3 | 25.3 | 17 | 25.9 | 102.2 | 5.1 | 20.2 | - | 86.9 | 83 | 78 | 122.4 | 87 | 80.5 | 77.2
STUDYROX4VRS | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 121.9 | 149.5 | 129.2 | 145 | 113.1 | 106.1 | 130.1 | 111.8 | 117 | -17.4 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 88.5 | 108.6 | 93.4 | 40.9 | 35.8 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
STUDYASH1VRS | WALHABK2 | 3069 | WALHALL2 | 1177 | 1WALHALA | 2 | 1177 | 1WALHALA 44.000 | 3069 | WALHALL2 100.00 | 4 | 1177-3069-4 | 25.3 | 25.3 | 20.1 | 31.2 | 123.4 | 65 | 25.3 | 18.5 | 28.3 | 111.9 | 65 | -11.5 | 2018 | 2013 | -5 |  | 23.5 | 26.1 | 25.3 | WALHALLA TIE 04 | 100/44 kV Transformer | 23.5 | 26.1 | 25.3 | 25.3 | 17.3 | 26.1 | 103.1 | 5.1 | 20.3 | - | - | - | - | 123.4 | - | - | -
STUDYBRN1VRS | HNDRSN-FRNKL | 304089 | HENDER11 | 304105 | FRANKLIN |  | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 117.4 | 194.7 | 119.3 | 449 | 170 | 108.3 | 190.1 | 114.1 | 296 | -5.2 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118 | 72.3 | - | 72 | 119.3 | 75.2 | - | 74.9
STUDYHAR1VRS | LANCA2 | 3380 | LANCAST2 | 1726 | 1LANCSTR | 2 | 1726 | 1LANCSTR 44.000 | 3380 | LANCAST2 100.00 | 1 | 1726-3380-1 | 27 | 27 | 15.2 | 34.2 | 126.8 | 13 | 27 | 14 | 31.1 | 115.4 | 13 | -11.4 | 2018 | 2013 | -5 |  | 24.1 | 27 | 26.1 | LANCASTER MN 01 | 100/44 kV Transformer | 24.1 | 27 | 26.1 | 27 | 14 | 31 | 114.8 | 3.2 | 12 | - | - | 59.6 | 56.7 | 126.8 | - | 58.6 | 56
STUDYASH1VRS | MARIEBK2 | 3177 | MARIETT2 | 1309 | 1MARIETA | 2 | 1309 | 1MARIETA 44.000 | 3177 | MARIETT2 100.00 | 3 | 1309-3177-3 | 42.2 | 42.2 | 26.6 | 54.8 | 129.8 | 13 | 42.2 | 24.9 | 50.1 | 118.7 | 13 | -11.1 | 2018 | 2013 | -5 |  | 39.3 | 43.7 | 42.2 | MARIETTA TIE 03 | 100/44 kV Transformer | 39.3 | 43.7 | 42.2 | 42.2 | 23.7 | 47.4 | 112.4 | 7.4 | 17.4 | - | - | - | - | 129.8 | - | - | -
STUDYASH1VRS | MARIEBK3 | 3177 | MARIETT2 | 1309 | 1MARIETA | 3 | 1309 | 1MARIETA 44.000 | 3177 | MARIETT2 100.00 | 2 | 1309-3177-2 | 42.2 | 42.2 | 26.6 | 54.8 | 129.8 | 13 | 42.2 | 24.8 | 50.1 | 118.8 | 13 | -11 | 2018 | 2013 | -5 |  | 39.3 | 43.7 | 42.2 | MARIETTA TIE 02 | 100/44 kV Transformer | 39.3 | 43.7 | 42.2 | 42.2 | 23.7 | 47.4 | 112.4 | 7.4 | 17.4 | - | - | 63.8 | 61 | 129.8 | - | 63.2 | 60.6
STUDYROX4VRS | ROUGHEDGE1A | 3654 | ROUGHED2 | 2194 | 1ROUGHED | 1A | 2194 | 1ROUGHED 44.000 | 3654 | ROUGHED2 100.00 | 1B | 2194-3654-1B | 21.6 | 21.6 | 13.6 | 27.9 | 129.2 | 26 | 21.6 | 12.6 | 25.7 | 118.9 | 26 | -10.3 | 2018 | 2013 | -5 |  | 20 | 22.3 | 21.6 | ROUGHEDGE TIE 1B | 100/44 kV Transformer | 20 | 22.3 | 21.6 | 21.6 | 11.8 | 23.9 | 110.8 | 4 | 18.4 | - | - | - | - | 129.2 | - | - | -
STUDYBRN1VRS | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 133.1 | 265.9 | 129 | 77 | 201 | 123.2 | 245 | 118.9 | 40 | -10.1 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 122.1 | - | - | 61.1 | 129 | - | - | 64.5
STUDYMAY1VRS | ROUGHEDGE1B | 3654 | ROUGHED2 | 2194 | 1ROUGHED | 1B | 2194 | 1ROUGHED 44.000 | 3654 | ROUGHED2 100.00 | 1A | 2194-3654-1A | 21.5 | 21.5 | 13.6 | 27.9 | 129.8 | 26 | 21.5 | 12.6 | 25.7 | 119.4 | 26 | -10.4 | 2018 | 2013 | -5 |  | 19.9 | 22.3 | 21.5 | ROUGHEDGE TIE 1A | 100/44 kV Transformer | 19.9 | 22.3 | 21.5 | 21.5 | 11.9 | 23.9 | 111.3 | 4 | 18.5 | - | 72.7 | 70.5 | 64.6 | 129.8 | 72.6 | 67 | 63.8
STUDYVCS1VRS | CORONBK4 | 28 | CORONACA | 1049 | 1CORONAC | 4 | 28 | CORONACA 100.00 | 1049 | 1CORONAC 44.000 | 2 | 28-1049-2 | 42 | 42 | 30.9 | 55.4 | 131.9 | 65 | 42 | 28.7 | 50.9 | 121.1 | 39 | -10.8 | 2018 | 2013 | -5 |  | 39.1 | 43.4 | 42 | CORONACA TIE 02 | 100/44 kV Transformer | 39.1 | 43.4 | 42 | 42 | 27.6 | 48.2 | 114.8 | 7.2 | 17.1 | - | 80.1 | 75 | 72.1 | 131.9 | 80.5 | 74.4 | 71.7
STUDYHAR1VRS | PINNACLE2 | 3775 | PINNACL2 | 2336 | 1PINACLE | 2 | 2336 | 1PINACLE 44.000 | 3775 | PINNACL2 100.00 | 1 | 2336-3775-1 | 27.7 | 27.7 | 18.7 | 37.8 | 136.4 | 26 | 27.7 | 17.3 | 35.1 | 126.6 | 13 | -9.8 | 2018 | 2013 | -5 |  | 24.8 | 27.7 | 26.7 | PINNACLE TIE 01 | 100/44 kV Transformer | 24.8 | 27.7 | 26.7 | 27.7 | 17.1 | 34.4 | 124.2 | 3.4 | 12.2 | - | 72.7 | 68.5 | 64.9 | 136.4 | 72.9 | 67.7 | 64.8
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 135 | DANIEL 100.00 | 220 | 1BLREC25 100.00 | 1 | 135-220-1 | 86.6 | 86.6 | 65.1 | 134.9 | 154.7 | 43 | 86.6 | 58.2 | 113.5 | 128.4 | 16 | -26.3 | 2018 | 2013 | -5 |  | 86.6 | 106 | 86.6 | DAVIDSON RIVER BL | 100 kV Line | 86.6 | 106 | 86.6 | 86.6 | 59.6 | 67.5 | 77.1 | 67.4 | 77.6 | - | 72.6 | 72.6 | 55.5 | 154.7 | 82.4 | 75 | 57.5
STUDYHAR1VRS | PINNACLE1 | 3775 | PINNACL2 | 2336 | 1PINACLE | 1 | 2336 | 1PINACLE 44.000 | 3775 | PINNACL2 100.00 | 2 | 2336-3775-2 | 26 | 26 | 18.8 | 37.8 | 145.4 | 52 | 26 | 17.4 | 35.1 | 134.9 | 26 | -10.5 | 2018 | 2013 | -5 |  | 23.2 | 26 | 25.1 | PINNACLE TIE 02 | 100/44 kV Transformer | 23.2 | 26 | 25.1 | 26 | 17.2 | 34.4 | 132.2 | 3.4 | 13.2 | - | - | - | - | 145.4 | - | - | -
STUDYBRN1VRS | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 57.2 | 184.5 | 153.7 | 39 | 119 | 51.4 | 168.1 | 139.8 | 16 | -13.9 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 142.4 | - | - | - | 153.7 | - | - | -
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 47 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 7 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 54 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
CAT1GMASH1VRS | - | - | - | - | - | - | 183 | OAKVALE | 195 | SHADY GR | 1 | 183-195-1 | 207.8 | 207.8 | - | 206.3 | 99.3 | 650 | 207.8 | - | 161.4 | 77.7 | 684 | -21.6 | 2019 | 2029 | 10 |  | 207.8 | 284.9 | 240.7 | OAKVALE BL | 100 kV Line | 264.3032 | 327.0016 | 264.3032 | - | - | - | - | - | - | - | 99.2 | 83.4 | 65.6 | 84.6 | 99.3 | 70.5 | 56
BEL1GMASH1VRS | - | - | - | - | - | - | 382 | MCADENVL | 647 | RANKIN T | 1 | 382-647-1 | 170.1 | 170.1 | - | 159.6 | 93.8 | 650 | 170.1 | - | 128.6 | 75.6 | 26 | -18.2 | 2023 | 2031 | 8 |  | 170.1 | 196.8 | 177.9 | MOUNTAIN ISLAND | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 170.1 | - | 119.8 | 70.4 | 39.8 | 23.4 | - | 95.5 | 97.4 | 81.1 | 93.9 | 93.8 | 87.6 | 73
CAT1GMASH1VRS | - | - | - | - | - | - | 242 | BUSH RIV | 283 | NEWBERRY | 1 | 242-283-1 | 86.6 | 86.6 | - | 79.4 | 91.6 | 253 | 86.6 | - | 64 | 73.9 | 8 | -17.7 | 2024 | 2033 | 9 |  | 86.6 | 121.24 | 108.3 | MIDWAY WH | 100 kV Line | 132.1516 | 163.5008 | 132.1516 | - | - | - | - | - | - | - | 92.1 | 87.5 | 72.9 | 76.7 | 91.6 | 73.6 | 61.7
CAT1GMASH1VRS | - | - | - | - | - | - | 687 | WINECOFF | 10642 | POPLRT B | 1 | 687-10642-1 | 120 | 120 | - | 117.3 | 97.8 | 325 | 120 | - | 99.4 | 82.8 | 253 | -15 | 2020 | 2025 | 5 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
BEL1GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 116.3 | 113.2 | 325 | 102.7 | - | 101 | 98.3 | 350 | -14.9 | 2018 | 2015 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
CAT1GMASH1VRS | - | - | - | - | - | - | 642 | POPLR TN | 687 | WINECOFF | 1 | 642-687-1 | 120 | 120 | - | 108.6 | 90.5 | 325 | 120 | - | 91 | 75.8 | 27 | -14.7 | 2025 | 2031 | 6 |  | 120 | 129.9 | 125.6 | HOPEWHELL WH | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 91.4 | 97.1 | 85.2 | 94.9 | 90.5 | 87.3 | 81.6
CAT1GMASH1VRS | - | - | - | - | - | - | 2259 | EASTFLDR | 10642 | POPLRT B | 1 | 2259-10642-1 | 126.4 | 126.4 | - | 117.4 | 92.9 | 325 | 126.4 | - | 99.4 | 78.7 | 182 | -14.2 | 2023 | 2029 | 6 |  | 126.4 | 139.4 | 126.7 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | - | - | - | - | - | - | - | 93.7 | 103.4 | 85.7 | 100.3 | 92.9 | 93.5 | 82.3
BEL1GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 113.3 | 110.3 | 325 | 102.7 | - | 98.7 | 96.1 | 336 | -14.2 | 2018 | 2016 | -2 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
CAT1GMASH1VRS | - | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 108.3 | 108.3 | - | 119.3 | 110.2 | 325 | 108.3 | - | 104.9 | 96.8 | 351 | -13.4 | 2018 | 2016 | -2 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.2 | 80.5 | 32.1 | 29.7 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
BEL1GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 108.2 | 105.3 | 325 | 102.7 | - | 94.7 | 92.2 | 262 | -13.1 | 2018 | 2019 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
BUC5GMRCH1VRS | - | - | - | - | - | - | 536 | 6BUCK | 561 | BUCK TIE | A4 | 536-561-A4 | 509 | 509 | - | 471 | 92.5 | 325 | 509 | - | 405.3 | 79.6 | 300 | -12.9 | 2023 | 2028 | 5 |  | 509 | 584.2 | 547.9 | BUCK TIE AT4 | 230/100 kV Transformer | 509 | 584.2 | 547.9 | - | - | - | - | - | - | - | 91.9 | 91.7 | 79.6 | 91.3 | 92.5 | 86.5 | 74.7
BEL1GMHAR1VRS | - | - | - | - | - | - | 673 | THRIFT T | 10555 | BELHAV W | 1 | 673-10555-1 | 177.9 | 177.9 | - | 172 | 96.7 | 325 | 177.9 | - | 149.5 | 84 | 246 | -12.7 | 2021 | 2024 | 3 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
BEL1GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10555 | BELHAV W | 1 | 611-10555-1 | 177.9 | 177.9 | - | 172 | 96.7 | 325 | 177.9 | - | 149.5 | 84.1 | 246 | -12.6 | 2021 | 2024 | 3 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
CAT1GMASH1VRS | - | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 120 | 120 | - | 122.5 | 102.1 | 325 | 120 | - | 107.6 | 89.7 | 351 | -12.4 | 2018 | 2020 | 2 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 120 | - | 87.2 | 72.7 | 35.3 | 29.4 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
BEL1GMROB2VRS | - | - | - | - | - | - | 304057 | DARLINGT | 304954 | DCP#12 | 1 | 304057-304954-1 | 150 | 150 | - | 136.3 | 90.9 | 650 | 150 | - | 117.9 | 78.6 | 702 | -12.3 | 2025 | 2029 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | 83.2 | 85.6 | 85.2 | 96.2 | 90.9 | 92 | 92.1
ALL4GMRCH1VRS | - | - | - | - | - | - | 304615 | BARN CRK | 304616 | BARNARD | 1 | 304615-304616-1 | 150 | 150 | - | 139.1 | 92.7 | 325 | 150 | - | 120.5 | 80.4 | 351 | -12.3 | 2023 | 2027 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
CAT1GMASH1VRS | - | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 108.3 | 108.3 | - | 111.8 | 103.2 | 325 | 108.3 | - | 98.4 | 90.9 | 351 | -12.3 | 2018 | 2020 | 2 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.2 | 80.5 | 24.6 | 22.7 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
BEL1GMHAR1VRS | - | - | - | - | - | - | 555 | BELHAVEN | 611 | LAKEWOOD | 1 | 555-611-1 | 177.9 | 177.9 | - | 167.2 | 94 | 325 | 177.9 | - | 145.7 | 81.9 | 234 | -12.1 | 2022 | 2026 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | - | - | - | - | - | - | - | 91.9 | 94.7 | 82.3 | 93.3 | 94 | 94.3 | 82.1
THRPGMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 114.2 | 111.2 | 650 | 102.7 | - | 102.6 | 99.9 | 702 | -11.3 | 2018 | 2014 | -4 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 25.6 | 24.9 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
MCG1GMHAR1VRS | - | - | - | - | - | - | 648 | REAMES R | 10590 | GERDAU W | 1 | 648-10590-1 | 91.2 | 91.2 | - | 96.6 | 105.9 | 325 | 91.2 | - | 87 | 95.4 | 351 | -10.5 | 2018 | 2016 | -2 |  | 91.2 | 112.3 | 91.2 | REAMES RD. RET. TAP | 100 kV Line | 106 | 130.6 | 106 | 91.2 | - | 97.1 | 106.5 | -0.5 | -0.6 | - | 106.2 | 110.3 | 85.9 | 104.8 | 105.9 | 105.6 | 84.9
MAR3GMASH1VRS | - | - | - | - | - | - | 928 | JESUPTWN | 943 | N GREENS | 1 | 928-943-1 | 177.9 | 177.9 | - | 175.7 | 98.8 | 325 | 177.9 | - | 158.6 | 89.2 | 351 | -9.6 | 2019 | 2021 | 2 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 163.5 | - | 143.8 | 87.9 | 31.9 | 10.9 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
ALL5GMASH1VRS | - | - | - | - | - | - | 385 | NEWPORT | 10119 | ROCK H7 | 2 | 385-10119-2 | 196.8 | 196.8 | - | 183.6 | 93.3 | 325 | 196.8 | - | 165.1 | 83.9 | 338 | -9.4 | 2023 | 2025 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 94.3 | 100 | 80.6 | 97.3 | 93.3 | 93.9 | 74.1
CAT1GMVCS1VRS | - | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 28.9 | 28.9 | - | 29.2 | 101.1 | 650 | 28.9 | - | 26.5 | 91.7 | 702 | -9.4 | 2018 | 2019 | 1 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 28.9 | - | 25.8 | 89.2 | 3.4 | 11.9 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
BUC5GMHAR1VRS | - | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37.6 | 94 | 325 | 40 | - | 33.9 | 84.7 | 351 | -9.3 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | 40 | - | 31 | 77.6 | 6.6 | 16.4 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
MCG1GMHAR1VRS | - | - | - | - | - | - | 2413 | 1AO SMIT | 2456 | 1WLTR KI | 1 | 2413-2456-1 | 40 | 40 | - | 36.5 | 91.2 | 325 | 40 | - | 32.8 | 82.1 | 351 | -9.1 | 2024 | 2026 | 2 |  | - | - | - | - | - | - | - | - | 40 | - | 29.9 | 74.8 | 6.6 | 16.4 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
ALL5GMASH1VRS | - | - | - | - | - | - | 385 | NEWPORT | 417 | WYLIE HY | 1 | 385-417-1 | 196.8 | 196.8 | - | 177.4 | 90.1 | 325 | 196.8 | - | 159.3 | 81 | 328 | -9.1 | 2025 | 2027 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | - | - | - | - | - | - | - | 91.1 | 96.7 | 77.8 | 94.1 | 90.1 | 90.7 | 71.4
CAT1GMASH1VRS | - | - | - | - | - | - | 1291 | 1JPS SLA | 1352 | 1TIGERVT | 1 | 1291-1352-1 | 25.8 | 25.8 | - | 24.1 | 93.5 | 325 | 25.8 | - | 21.9 | 84.7 | 351 | -8.8 | 2023 | 2024 | 1 |  | 25.8 | 31.3 | 25.8 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 20.5 | 79.3 | 3.6 | 14.2 | - | 93.4 | 94.8 | 76.6 | 92.5 | 93.5 | 93 | 76
MCG1GMHAR1VRS | - | - | - | - | - | - | 894 | GILBRTHT | 10968 | TROLNGWB | 1 | 894-10968-1 | 118.8 | 118.8 | - | 112.3 | 94.6 | 325 | 118.8 | - | 101.9 | 85.8 | 351 | -8.8 | 2022 | 2023 | 1 |  | 118.8 | 130.8 | 118.8 | SWEPSONVILLE BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 118.8 | - | 92.3 | 77.7 | 20 | 16.9 | - | 93.8 | 93.9 | 84.9 | 94.5 | 94.6 | 94.5 | 85.4
MCG1GMHAR1VRS | - | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 128 | 128 | - | 123.5 | 96.5 | 325 | 128 | - | 112.2 | 87.7 | 351 | -8.8 | 2021 | 2022 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 101.1 | 79 | 22.4 | 17.5 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
MCG1GMRCH1VRS | - | - | - | - | - | - | 333 | 6NEWPORT | 541 | 6MORN ST | 1 | 333-541-1 | 436.9 | 436.9 | - | 400.6 | 91.7 | 650 | 436.9 | - | 363.1 | 83.1 | 682 | -8.6 | 2024 | 2025 | 1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 436.9 | - | 370.5 | 84.8 | 30.1 | 6.9 | 100.8 | 90.8 | 88.7 | 80.8 | 95 | 91.7 | 85.5 | 76.6
CAT1GMASH1VRS | - | - | - | - | - | - | 1271 | 1GEN ELE | 1280 | 1HEND MN | 1 | 1271-1280-1 | 25.8 | 25.8 | - | 24.5 | 94.9 | 325 | 25.8 | - | 22.3 | 86.6 | 351 | -8.3 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | HENDERSONVILLE #1 | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.5 | 83.5 | 3 | 11.4 | - | 94.5 | 95.6 | 77.6 | 94.4 | 94.9 | 94.7 | 77.7
CAT1GMASH1VRS | - | - | - | - | - | - | 1280 | 1HEND MN | 1295 | 1KANUGA | 1 | 1280-1295-1 | 25.8 | 25.8 | - | 24.5 | 94.9 | 325 | 25.8 | - | 22.3 | 86.6 | 351 | -8.3 | 2022 | 2023 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.5 | 83.5 | 3 | 11.4 | - | 94.5 | 95.7 | 77.6 | 94.5 | 94.9 | 94.7 | 77.7
CAT1GMASH1VRS | - | - | - | - | - | - | 1331 | 1PENROS | 1335 | 1PISGAH | 1 | 1331-1335-1 | 25.8 | 25.8 | - | 23.7 | 92 | 325 | 25.8 | - | 21.6 | 83.8 | 351 | -8.2 | 2024 | 2025 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 19.9 | 77.1 | 3.8 | 14.9 | - | 91.7 | 92.1 | 75.4 | 91.5 | 92 | 91.7 | 75.2
CAT1GMASH1VRS | - | - | - | - | - | - | 1309 | 1MARIETA | 1322 | 1MRRTTA | 1 | 1309-1322-1 | 44.7 | 44.7 | - | 41.4 | 92.7 | 325 | 44.7 | - | 37.8 | 84.6 | 351 | -8.1 | 2023 | 2024 | 1 |  | 44.6532 | 49.149 | 44.6532 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 35.3 | 79.1 | 6.1 | 13.6 | - | 92.6 | 93.9 | 83.7 | 91.7 | 92.7 | 92.3 | 83.1
CAT1GMASH1VRS | - | - | - | - | - | - | 103 | 3M TAP | 10180 | MICHMV W | 1 | 103-10180-1 | 126.1 | 126.1 | - | 118.4 | 93.9 | 325 | 126.1 | - | 108.2 | 85.8 | 351 | -8.1 | 2022 | 2023 | 1 |  | 126.1 | 139.4 | 126.1 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.1 | - | 94.4 | 74.9 | 24 | 19 | - | 93.8 | 94.9 | 84.7 | 92.6 | 93.9 | 93.1 | 83.7
ALL4GMROX4VRS | - | - | - | - | - | - | 2422 | 1ENO | 2621 | ENO 3 | 3 | 2422-2621-3 | 40 | 40 | - | 38.4 | 96 | 650 | 40 | - | 35.1 | 87.9 | 702 | -8.1 | 2021 | 2022 | 1 |  | 40 | 50 | 50 | ENO TIE 03 TERT | 230/100/44 kV Transformer | 40 | 50 | 50 | 40 | - | 28.5 | 71.2 | 9.9 | 24.8 | - | 95 | 76 | 75.5 | 94 | 96 | 76.8 | 76.3
CAT1GMASH1VRS | - | - | - | - | - | - | 195 | SHADY GR | 10181 | MOONVI W | 1 | 195-10181-1 | 126.4 | 126.4 | - | 118.3 | 93.6 | 325 | 126.4 | - | 108.1 | 85.6 | 351 | -8 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 94.4 | 74.7 | 23.9 | 18.9 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
CAT1GMASH1VRS | - | - | - | - | - | - | 10180 | MICHMV W | 10181 | MOONVI W | 1 | 10180-10181-1 | 126.4 | 126.4 | - | 118.3 | 93.6 | 325 | 126.4 | - | 108.2 | 85.6 | 351 | -8 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 94.4 | 74.7 | 23.9 | 18.9 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
MCG1GMHAR1VRS | - | - | - | - | - | - | 925 | IMPERALW | 10944 | NORTEL W | 1 | 925-10944-1 | 130.6 | 130.6 | - | 120.6 | 92.4 | 325 | 130.6 | - | 110.7 | 84.7 | 351 | -7.7 | 2023 | 2024 | 1 |  | 130.6 | 161.4 | 130.6 | PANTHER WH | 100 kV Line | 130.5928 | 161.4224 | 130.5928 | 130.6 | - | 107.5 | 82.3 | 13.1 | 10.1 | - | 91.6 | 91.9 | 73.9 | 92.2 | 92.4 | 92.3 | 74.3
CAT1GMVCS1VRS | - | - | - | - | - | - | 600 | HARRISBG | 601 | HCKRY GR | 1 | 600-601-1 | 120 | 120 | - | 116.9 | 97.4 | 325 | 120 | - | 107.7 | 89.8 | 351 | -7.6 | 2020 | 2020 | 0 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 120 | - | 92.4 | 77 | 24.5 | 20.4 | - | 96.1 | 103.7 | 88.9 | 96.9 | 97.4 | 93.9 | 84.7
CLI5GMASH1VRS | - | - | - | - | - | - | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 254-324-1 | 120 | 120 | - | 121.7 | 101.4 | 650 | 120 | - | 112.6 | 93.9 | 702 | -7.5 | 2018 | 2017 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 120 | - | 99.7 | 83.1 | 22 | 18.3 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
ALL5GMHAR1VRS | - | - | - | - | - | - | 663 | STELCK R | 684 | WESTNHSW | 1 | 663-684-1 | 102.7 | 102.7 | - | 92.9 | 90.5 | 325 | 102.7 | - | 85.3 | 83.1 | 351 | -7.4 | 2025 | 2025 | 0 |  | 102.7 | 113.1 | 102.7 | WESTINGHOUSE TAP LINE WH | 100 kV Line | 102.7 | 113.1 | 102.7 | 102.7 | - | 76.1 | 74.1 | 16.8 | 16.4 | - | 90.6 | 94.6 | 82.1 | 89.7 | 90.5 | 90.5 | 81.3
OCO1GMASH1VRS | - | - | - | - | - | - | 1030 | 1BLREC 7 | 1206 | 1BEACON | 1 | 1030-1206-1 | 31 | 31 | - | 28.3 | 91.2 | 325 | 31 | - | 26 | 83.8 | 351 | -7.4 | 2024 | 2025 | 1 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | - | 24.5 | 79 | 3.8 | 12.2 | - | 91.1 | 92.9 | 85.4 | 90.4 | 91.2 | 91 | 84.8
CAT1GMAMW1VRS | - | - | - | - | - | - | 1382 | 1NEWBERY | 1390 | 1NWBYC3 | 1 | 1382-1390-1 | 22 | 22 | - | 19.8 | 90.2 | 325 | 22 | - | 18.3 | 83.4 | 351 | -6.8 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | 22 | - | 17.9 | 81.3 | 1.9 | 8.9 | - | 90.2 | 90.7 | 90.2 | 89.5 | 90.2 | 89.9 | 89.6
MAR3GMASH1VRS | - | - | - | - | - | - | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737-779-1 | 126.4 | 126.4 | - | 117.2 | 92.7 | 325 | 126.4 | - | 109.3 | 86.5 | 325 | -6.2 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | MAYO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | - | - | - | - | - | - | - | 93 | 95 | 85.1 | 95.6 | 92.7 | 93.5 | 84
BEL1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 21.5 | 96.6 | 325 | 22.2 | - | 20.2 | 90.8 | 351 | -5.8 | 2021 | 2020 | -1 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 3.6 | 16.1 | - | 95.4 | 95.5 | 78.8 | 98 | 96.6 | 96 | 79.3
BEL1GMHAR1VRS | - | - | - | - | - | - | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 836-850-1 | 1904.3 | 1904.3 | - | 1717 | 90.2 | 648 | 1904.3 | - | 1619.3 | 85 | 446 | -5.2 | 2025 | 2024 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | - | 1493.3 | 78.4 | 223.7 | 11.8 | 95 | 85.5 | 93.3 | 80.5 | 88.7 | 90.2 | 87.2 | 75.1
CAT1GMASH1VRS | - | - | - | - | - | - | 41 | LEE | 151 | ESTES TB | 1 | 41-151-1 | 103.4 | 103.4 | - | 143.2 | 138.5 | 594 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 137.3 | 145.8 | 143.1 | 93.2 | 138.5 | 84.8 | 83.5
CAT1GMASH1VRS | - | - | - | - | - | - | 41 | LEE | 195 | SHADY GR | 1 | 41-195-1 | 103.4 | 103.4 | - | 135.2 | 130.7 | 1804 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 129.5 | 137.9 | 135.4 | 85 | 130.7 | 76.9 | 75.6
CAT1GMASH1VRS | - | - | - | - | - | - | 151 | ESTES TB | 195 | SHADY GR | 1 | 151-195-1 | 103.4 | 103.4 | - | 110.4 | 106.8 | 107 | - | - | - | - | - | - | 2018 | - | - |  | 103.4 | 103.4 | 103.4 | PIEDMONT | 100 kV Line | 126.436 | 126.436 | 126.436 | - | - | - | - | - | - | - | 105.6 | 113.4 | 111.7 | - | 106.8 | 52.4 | 51.6
BEL1GMHAR1VRS | - | - | - | - | - | - | 304047 | WSPN115 | 304406 | ST PAULS | 1 | 304047-304406-1 | 119 | 119 | - | 108.4 | 91.1 | 325 | - | - | - | - | - | - | 2024 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.3 | 84.3 | - | 88.1 | 109.3 | 91.1 | - | 92.2
CAT1GMVCS1VRS | - | - | - | - | - | - | 465 | HICKORY | 483 | NEWTON T | 1 | 465-483-1 | 103.9 | 103.9 | - | 125.8 | 121.1 | 325 | 103.9 | - | 107.7 | 103.6 | 351 | -17.5 | 2018 | 2013 | -5 |  | 103.9 | 141.2 | 128 | MULL WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 104 | - | 102.8 | 98.8 | 23 | 22.3 | - | 117.8 | 103.4 | 86.4 | 117.5 | 121.1 | 98.4 | 86.4
BAD1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 119.3 | 116.2 | 325 | 102.7 | - | 107.3 | 104.5 | 351 | -11.7 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 25.9 | 25.3 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 73.2 | 146.5 | 650 | 50 | - | 52.7 | 105.4 | 702 | -41.1 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 42 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 43 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | CAT1 | - | - | - | - | - | 687 | WINECOFF | 10642 | POPLRT B | 1 | 687-10642-1 | 125.6 | 125.6 | - | 118.4 | 94.3 | 311 | 125.6 | - | 98.8 | 78.7 | 337 | -15.6 | 2022 | 2029 | 7 |  | 120 | 129.9 | 125.6 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | 125.6 | - | 78 | 62.1 | 40.4 | 32.2 | - | 98.7 | 104.3 | 91.9 | 101.1 | 97.8 | 94.3 | 88.3
STUDY | CAT1 | - | - | - | - | - | 2259 | EASTFLDR | 10642 | POPLRT B | 1 | 2259-10642-1 | 126.7 | 126.7 | - | 118.5 | 93.5 | 311 | 126.7 | - | 98.9 | 78 | 337 | -15.5 | 2023 | 2029 | 6 |  | 126.4 | 139.4 | 126.7 | HOPEWELL BL | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.7 | - | 78.1 | 61.6 | 40.4 | 31.9 | - | 93.7 | 103.4 | 85.7 | 100.3 | 92.9 | 93.5 | 82.3
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 114 | 111 | 622 | 102.7 | - | 98.4 | 95.8 | 674 | -15.2 | 2018 | 2016 | -2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 32.2 | 31.4 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
STUDY | BUGS | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 116.8 | 113.7 | 311 | 102.7 | - | 101.3 | 98.7 | 337 | -15 | 2018 | 2014 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
STUDY | BUGS | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 113.8 | 110.8 | 311 | 102.7 | - | 99 | 96.4 | 337 | -14.4 | 2018 | 2016 | -2 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
STUDY | CAT1 | - | - | - | - | - | 465 | HICKORY | 483 | NEWTON T | 1 | 465-483-1 | 128 | 128 | - | 125.9 | 98.4 | 311 | 128 | - | 107.7 | 84.1 | 337 | -14.3 | 2020 | 2024 | 4 |  | 103.9 | 141.2 | 128 | MULL WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 102.2 | 79.9 | 23.7 | 18.5 | - | 117.8 | 103.4 | 86.4 | 117.5 | 121.1 | 98.4 | 86.4
STUDY | CAT1 | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 108.3 | 108.3 | - | 120 | 110.8 | 311 | 108.3 | - | 104.7 | 96.7 | 337 | -14.1 | 2018 | 2016 | -2 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.5 | 80.8 | 32.5 | 30 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
STUDY | BUGS | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 108.6 | 105.7 | 311 | 102.7 | - | 95 | 92.5 | 337 | -13.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
STUDY | CAT1 | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 108.3 | 108.3 | - | 112.5 | 103.8 | 311 | 108.3 | - | 98.2 | 90.7 | 337 | -13.1 | 2018 | 2020 | 2 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 108.3 | - | 87.5 | 80.8 | 25 | 23 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
STUDY | BUGS | - | - | - | - | - | 611 | LAKEWOOD | 10555 | BELHAV W | 1 | 611-10555-1 | 177.9 | 177.9 | - | 172.7 | 97.1 | 311 | 177.9 | - | 150 | 84.3 | 337 | -12.8 | 2020 | 2024 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
STUDY | BUGS | - | - | - | - | - | 673 | THRIFT T | 10555 | BELHAV W | 1 | 673-10555-1 | 177.9 | 177.9 | - | 172.7 | 97.1 | 311 | 177.9 | - | 149.9 | 84.3 | 337 | -12.8 | 2020 | 2024 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND WH | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | - | 94.6 | 97.5 | 84.8 | 97.2 | 96.7 | 97.1 | 84.5
STUDY | CAT1 | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 125.6 | 125.6 | - | 123.1 | 98 | 311 | 125.6 | - | 107.4 | 85.5 | 337 | -12.5 | 2020 | 2023 | 3 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 125.6 | - | 87.5 | 69.7 | 35.6 | 28.3 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
STUDY | BUGS | - | - | - | - | - | 555 | BELHAVEN | 611 | LAKEWOOD | 1 | 555-611-1 | 177.9 | 177.9 | - | 167.7 | 94.3 | 311 | 177.9 | - | 146.1 | 82.2 | 337 | -12.1 | 2022 | 2026 | 4 |  | 177.9 | 196.8 | 177.9 | RIVERBEND | 100 kV Line | 177.8764 | 177.8764 | 177.8764 | 177.9 | - | 115.4 | 64.9 | 52.3 | 29.4 | - | 91.9 | 94.7 | 82.3 | 93.3 | 94 | 94.3 | 82.1
STUDY | MCG1 | - | - | - | - | - | 304057 | DARLINGT | 304954 | DCP#12 | 1 | 304057-304954-1 | 150 | 150 | - | 137.9 | 92 | 622 | 150 | - | 121.1 | 80.7 | 674 | -11.3 | 2024 | 2027 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | 83.2 | 85.6 | 85.2 | 96.2 | 90.9 | 92 | 92.1
STUDY | MCG1 | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 87.1 | 100.6 | 311 | 86.6 | - | 77.3 | 89.3 | 324 | -11.3 | 2018 | 2021 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 100 | 101.4 | 92.2 | 110 | 99.9 | 100.6 | 91.5
STUDY | MCG1 | - | - | - | - | - | 737 | DAN RIV | 779 | RIDGVEWT | 1 | 737-779-1 | 126.4 | 126.4 | - | 118.2 | 93.5 | 311 | 126.4 | - | 104.3 | 82.5 | 337 | -11 | 2023 | 2026 | 3 |  | 126.4 | 139.4 | 126.4 | MAYO WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 71.5 | 56.6 | 46.7 | 36.9 | - | 93 | 95 | 85.1 | 95.6 | 92.7 | 93.5 | 84
STUDY | MCG1 | - | - | - | - | - | 2089 | WAYNICKR | 10810 | WENTW WH | 1 | 2089-10810-1 | 86.6 | 86.6 | - | 79.3 | 91.6 | 596 | 86.6 | - | 70 | 80.8 | 648 | -10.8 | 2024 | 2027 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 90.9 | 92.3 | 83.9 | 101.1 | 90.8 | 91.6 | 83.2
STUDY | MCG1 | - | - | - | - | - | 737 | DAN RIV | 10810 | WENTW WH | 1 | 737-10810-1 | 86.6 | 86.6 | - | 79.4 | 91.6 | 298 | 86.6 | - | 70 | 80.9 | 324 | -10.7 | 2024 | 2027 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER BL | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 91 | 92.4 | 84 | 101.2 | 90.9 | 91.6 | 83.3
STUDY | MCG1 | - | - | - | - | - | 648 | REAMES R | 10590 | GERDAU W | 1 | 648-10590-1 | 91.2 | 91.2 | - | 96.3 | 105.6 | 311 | 91.2 | - | 87.1 | 95.6 | 337 | -10 | 2018 | 2016 | -2 |  | 91.2 | 112.3 | 91.2 | REAMES RD. RET. TAP | 100 kV Line | 106 | 130.6 | 106 | 91.2 | - | 97.1 | 106.5 | -0.8 | -0.9 | - | 106.2 | 110.3 | 85.9 | 104.8 | 105.9 | 105.6 | 84.9
STUDY | MCG1 | - | - | - | - | - | 928 | JESUPTWN | 943 | N GREENS | 1 | 928-943-1 | 177.9 | 177.9 | - | 176.8 | 99.4 | 311 | 177.9 | - | 159.2 | 89.5 | 337 | -9.9 | 2019 | 2020 | 1 |  | 177.9 | 196.8 | 177.9 | KERNERSVILLE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | 163.5 | - | 145 | 88.7 | 31.8 | 10.7 | - | 99.2 | 101.2 | 90 | 101.8 | 98.8 | 99.4 | 88.7
STUDY | ALL5 | - | - | - | - | - | 385 | NEWPORT | 10119 | ROCK H7 | 2 | 385-10119-2 | 196.8 | 196.8 | - | 184.7 | 93.9 | 311 | 196.8 | - | 165.6 | 84.1 | 337 | -9.8 | 2022 | 2024 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | 196.8 | - | 122.2 | 62.1 | 62.5 | 31.8 | - | 94.3 | 100 | 80.6 | 97.3 | 93.3 | 93.9 | 74.1
STUDY | ALL5 | - | - | - | - | - | 385 | NEWPORT | 417 | WYLIE HY | 1 | 385-417-1 | 196.8 | 196.8 | - | 178.5 | 90.7 | 311 | 196.8 | - | 159.9 | 81.2 | 337 | -9.5 | 2025 | 2027 | 2 |  | 196.8 | 228.1 | 196.8 | HOOK | 100 kV Line | 196.7552 | 228.1044 | 196.7552 | 196.8 | - | 118.6 | 60.2 | 59.9 | 30.5 | - | 91.1 | 96.7 | 77.8 | 94.1 | 90.1 | 90.7 | 71.4
STUDY | BUGS | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37.6 | 94 | 311 | 40 | - | 33.8 | 84.5 | 337 | -9.5 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | 40 | - | 30.9 | 77.3 | 6.7 | 16.7 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
STUDY | BUGS | - | - | - | - | - | 2413 | 1AO SMIT | 2456 | 1WLTR KI | 1 | 2413-2456-1 | 40 | 40 | - | 36.4 | 91.1 | 311 | 40 | - | 32.8 | 81.9 | 337 | -9.2 | 2024 | 2026 | 2 |  | - | - | - | - | - | - | - | - | 40 | - | 29.8 | 74.5 | 6.6 | 16.6 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
STUDY | BUGS | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 128 | 128 | - | 123.5 | 96.4 | 311 | 128 | - | 112.1 | 87.6 | 337 | -8.8 | 2021 | 2022 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 128 | - | 101 | 78.9 | 22.5 | 17.5 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
STUDY | THRP | - | - | - | - | - | 894 | GILBRTHT | 10968 | TROLNGWB | 1 | 894-10968-1 | 118.8 | 118.8 | - | 112.2 | 94.5 | 311 | 118.8 | - | 101.8 | 85.7 | 337 | -8.8 | 2022 | 2023 | 1 |  | 118.8 | 130.8 | 118.8 | SWEPSONVILLE BL | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 118.8 | - | 92 | 77.4 | 20.2 | 17.1 | - | 93.8 | 93.9 | 84.9 | 94.5 | 94.6 | 94.5 | 85.4
STUDY | OCO1 | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 30 | 30 | - | 29.1 | 97 | 622 | 30 | - | 26.5 | 88.4 | 674 | -8.6 | 2020 | 2021 | 1 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 30 | - | 25.8 | 86 | 3.3 | 11 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
STUDY | CLI5 | - | - | - | - | - | 1291 | 1JPS SLA | 1352 | 1TIGERVT | 1 | 1291-1352-1 | 25.8 | 25.8 | - | 24 | 93 | 311 | 25.8 | - | 21.9 | 84.8 | 337 | -8.2 | 2023 | 2024 | 1 |  | 25.8 | 31.3 | 25.8 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 20.4 | 79.3 | 3.6 | 13.7 | - | 93.4 | 94.8 | 76.6 | 92.5 | 93.5 | 93 | 76
STUDY | CLI5 | - | - | - | - | - | 1271 | 1GEN ELE | 1280 | 1HEND MN | 1 | 1271-1280-1 | 25.8 | 25.8 | - | 24.4 | 94.7 | 311 | 25.8 | - | 22.4 | 86.7 | 337 | -8 | 2022 | 2022 | 0 |  | 25.8 | 31.3 | 25.8 | HENDERSONVILLE #1 | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.5 | 83.5 | 2.9 | 11.2 | - | 94.5 | 95.6 | 77.6 | 94.4 | 94.9 | 94.7 | 77.7
STUDY | CLI5 | - | - | - | - | - | 1280 | 1HEND MN | 1295 | 1KANUGA | 1 | 1280-1295-1 | 25.8 | 25.8 | - | 24.4 | 94.7 | 311 | 25.8 | - | 22.4 | 86.7 | 337 | -8 | 2022 | 2022 | 0 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 21.5 | 83.5 | 2.9 | 11.2 | - | 94.5 | 95.7 | 77.6 | 94.5 | 94.9 | 94.7 | 77.7
STUDY | CLI5 | - | - | - | - | - | 1331 | 1PENROS | 1335 | 1PISGAH | 1 | 1331-1335-1 | 25.8 | 25.8 | - | 23.7 | 91.7 | 311 | 25.8 | - | 21.6 | 83.8 | 337 | -7.9 | 2024 | 2025 | 1 |  | 25.8 | 31.3 | 25.8 | KANUGA | 44 kV Line | 0 | 0 | 0 | 25.8 | - | 19.9 | 77.1 | 3.8 | 14.6 | - | 91.7 | 92.1 | 75.4 | 91.5 | 92 | 91.7 | 75.2
STUDY | CLI5 | - | - | - | - | - | 1309 | 1MARIETA | 1322 | 1MRRTTA | 1 | 1309-1322-1 | 44.7 | 44.7 | - | 41.2 | 92.3 | 311 | 44.7 | - | 37.8 | 84.6 | 337 | -7.7 | 2024 | 2024 | 0 |  | 44.6532 | 49.149 | 44.6532 | MARIETTA | 44 kV Line | 0 | 0 | 0 | 44.7 | - | 35.3 | 79.1 | 5.9 | 13.2 | - | 92.6 | 93.9 | 83.7 | 91.7 | 92.7 | 92.3 | 83.1
STUDY | BUGS | - | - | - | - | - | 925 | IMPERALW | 10944 | NORTEL W | 1 | 925-10944-1 | 130.6 | 130.6 | - | 120.5 | 92.3 | 311 | 130.6 | - | 110.6 | 84.7 | 337 | -7.6 | 2024 | 2024 | 0 |  | 130.6 | 161.4 | 130.6 | PANTHER WH | 100 kV Line | 130.5928 | 161.4224 | 130.5928 | 130.6 | - | 107.2 | 82.1 | 13.3 | 10.2 | - | 91.6 | 91.9 | 73.9 | 92.2 | 92.4 | 92.3 | 74.3
STUDY | ALL5 | - | - | - | - | - | 663 | STELCK R | 684 | WESTNHSW | 1 | 663-684-1 | 102.7 | 102.7 | - | 92.9 | 90.5 | 311 | 102.7 | - | 85.3 | 83.1 | 337 | -7.4 | 2025 | 2025 | 0 |  | 102.7 | 113.1 | 102.7 | WESTINGHOUSE TAP LINE WH | 100 kV Line | 102.7 | 113.1 | 102.7 | 102.7 | - | 76.2 | 74.2 | 16.7 | 16.3 | - | 90.6 | 94.6 | 82.1 | 89.7 | 90.5 | 90.5 | 81.3
STUDY | CLI5 | - | - | - | - | - | 195 | SHADY GR | 10181 | MOONVI W | 1 | 195-10181-1 | 126.4 | 126.4 | - | 117.4 | 92.9 | 311 | 126.4 | - | 108.2 | 85.6 | 337 | -7.3 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 94.4 | 74.7 | 23 | 18.2 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
STUDY | CLI5 | - | - | - | - | - | 10180 | MICHMV W | 10181 | MOONVI W | 1 | 10180-10181-1 | 126.4 | 126.4 | - | 117.4 | 92.9 | 311 | 126.4 | - | 108.2 | 85.6 | 337 | -7.3 | 2023 | 2023 | 0 |  | 126.4 | 139.4 | 126.4 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.4 | 126.436 | 126.4 | - | 94.5 | 74.7 | 22.9 | 18.2 | - | 93.6 | 94.7 | 84.7 | 92.4 | 93.6 | 92.9 | 83.7
STUDY | CLI5 | - | - | - | - | - | 103 | 3M TAP | 10180 | MICHMV W | 1 | 103-10180-1 | 126.1 | 126.1 | - | 117.4 | 93.1 | 311 | 126.1 | - | 108.1 | 85.8 | 337 | -7.3 | 2023 | 2023 | 0 |  | 126.1 | 139.4 | 126.1 | GREENBRIAR WH | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.1 | - | 94.5 | 74.9 | 22.9 | 18.2 | - | 93.8 | 94.9 | 84.7 | 92.6 | 93.9 | 93.1 | 83.7
STUDY | OCO1 | - | - | - | - | - | 1030 | 1BLREC 7 | 1206 | 1BEACON | 1 | 1030-1206-1 | 31 | 31 | - | 28.2 | 91 | 311 | 31 | - | 26 | 83.9 | 337 | -7.1 | 2024 | 2025 | 1 |  | 31 | 33 | 31 | WALHALLA | 44 kV Line | 0 | 0 | 0 | 31 | - | 24.5 | 79 | 3.7 | 12 | - | 91.1 | 92.9 | 85.4 | 90.4 | 91.2 | 91 | 84.8
STUDY | CLI5 | - | - | - | - | - | 254 | GAFFNEY | 324 | CHEROKEE | 1 | 254-324-1 | 125.6 | 125.6 | - | 121.1 | 96.4 | 622 | 125.6 | - | 112.4 | 89.5 | 674 | -6.9 | 2021 | 2020 | -1 |  | 120 | 129.9 | 125.6 | BEAVER WH | 100 kV Line | 153.8016 | 178.0496 | 153.8016 | 125.6 | - | 103.5 | 82.4 | 17.6 | 14 | - | 102.5 | 103.4 | 93.7 | 96.8 | 101.4 | 96.4 | 85.2
STUDY | MCG1 | - | - | - | - | - | 304251 | LEE230 S | 304957 | WYNCO#2 | 1 | 304251-304957-1 | 220 | 220 | - | 199.7 | 90.8 | 622 | 220 | - | 185.1 | 84.2 | 674 | -6.6 | 2025 | 2024 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.3 | 86.1 | 87.4 | 87.2 | 96.3 | 89.9 | 90.8 | 90.9
STUDY | CAT1 | - | - | - | - | - | 600 | HARRISBG | 601 | HCKRY GR | 1 | 600-601-1 | 125.6 | 125.6 | - | 118 | 93.9 | 311 | 125.6 | - | 109.9 | 87.5 | 337 | -6.4 | 2022 | 2022 | 0 |  | 120.0276 | 129.9 | 125.57 | CRAB ORCHARD WH | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 125.6 | - | 91 | 72.5 | 27 | 21.4 | - | 96.1 | 103.7 | 88.9 | 96.9 | 97.4 | 93.9 | 84.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 21.4 | 96 | 311 | 22.2 | - | 20.2 | 90.7 | 337 | -5.3 | 2021 | 2020 | -1 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 3.5 | 15.5 | - | 95.4 | 95.5 | 78.8 | 98 | 96.6 | 96 | 79.3
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 119.2 | 116 | 311 | 102.7 | - | 103.1 | 100.4 | 337 | -15.6 | 2018 | 2013 | -5 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 32.7 | 31.7 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
1.6 | % Yearly Load Growth |  | 2018 Summer Screening (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\Base18s_no hydro\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | Base2018_no hydro.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 17 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 18 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304047 | WSPN115 | 304406 | ST PAULS | 1 | 304047-304406-1 | 119 | 119 | - | 109.7 | 92.2 | 13 | 119 | - | 79.7 | 67 | 13 | -25.2 | 2024 | 2039 | 15 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.3 | 84.3 | - | 88.1 | 109.3 | 91.1 | - | 92.2
STUDY | BADX | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 110.8 | 110.8 | - | 111.5 | 100.6 | 13 | 110.8 | - | 87.2 | 78.7 | 13 | -21.9 | 2018 | 2029 | 11 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110 | 114 | 100.9 | 120.5 | 113.2 | 113.7 | 100.6
STUDY | BADX | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 110.8 | 110.8 | - | 108.6 | 98 | 13 | 110.8 | - | 84.9 | 76.6 | 13 | -21.4 | 2020 | 2030 | 10 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.1 | 111 | 98.3 | 117.9 | 110.3 | 110.8 | 98
STUDY | BADX | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 110.8 | 110.8 | - | 103.6 | 93.5 | 13 | 110.8 | - | 81 | 73.1 | 13 | -20.4 | 2023 | 2033 | 10 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.9 | 93.8 | 113.2 | 105.3 | 105.7 | 93.5
STUDY | BADX | - | - | - | - | - | 681 | WESTFORK | 687 | WINECOFF | 1 | 681-687-1 | 118.6 | 118.6 | - | 117.8 | 99.3 | 13 | 118.6 | - | 100 | 84.4 | 13 | -14.9 | 2019 | 2024 | 5 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.6 | - | 82 | 69.1 | 35.8 | 30.2 | - | 110.8 | 117.6 | 101.5 | 114.9 | 110.2 | 110.8 | 99.3
STUDY | BADX | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 113.1 | 113.1 | - | 117.5 | 103.9 | 13 | 113.1 | - | 101.5 | 89.7 | 13 | -14.2 | 2018 | 2020 | 2 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 84.7 | 74.9 | 32.8 | 29 | 125.1 | 112.4 | 112.3 | 100.6 | 129.2 | 116.2 | 116 | 103.9
STUDY | BADX | - | - | - | - | - | 570 | COL P KN | 681 | WESTFORK | 1 | 570-681-1 | 118.6 | 118.6 | - | 110.4 | 93.1 | 13 | 118.6 | - | 93.5 | 78.9 | 13 | -14.2 | 2023 | 2028 | 5 |  | 108.3 | 118.6 | 108.3 | ODELL | 100 kV Line | 126.436 | 139.426 | 126.436 | 118.6 | - | 82 | 69.1 | 28.4 | 24 | - | 103.8 | 110.1 | 95.1 | 121.7 | 103.2 | 103.8 | 93.1
STUDY | BADX | - | - | - | - | - | 570 | COL P KN | 687 | WINECOFF | 1 | 570-687-1 | 129.9 | 129.9 | - | 121 | 93.1 | 13 | 129.9 | - | 102.8 | 79.1 | 13 | -14 | 2023 | 2028 | 5 |  | 120 | 129.9 | 125.6 | ODELL | 100 kV Line | 126.4 | 139.4 | 126.4 | 129.9 | - | 82 | 63.1 | 39 | 30 | - | 102.6 | 104.1 | 95.1 | 119.3 | 102.1 | 98 | 93.1
STUDY | BADX | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 113.1 | 113.1 | - | 112.3 | 99.3 | 26 | 113.1 | - | 96.8 | 85.6 | 26 | -13.7 | 2019 | 2023 | 4 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | - | 80 | 70.7 | 32.3 | 28.6 | 120.5 | 107.3 | 107.3 | 96 | 124.5 | 111.2 | 111 | 99.3
STUDY | BADX | - | - | - | - | - | 304615 | BARN CRK | 304616 | BARNARD | 1 | 304615-304616-1 | 150 | 150 | - | 139.1 | 92.8 | 13 | 150 | - | 120.6 | 80.4 | 13 | -12.4 | 2023 | 2027 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.7 | - | 91.8 | 93 | 92.7 | - | 92.8
STUDY | BADX | - | - | - | - | - | 304057 | DARLINGT | 304954 | DCP#12 | 1 | 304057-304954-1 | 150 | 150 | - | 138.2 | 92.1 | 26 | 150 | - | 120.3 | 80.2 | 26 | -11.9 | 2024 | 2027 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | 83.2 | 85.6 | 85.2 | 96.2 | 90.9 | 92 | 92.1
STUDY | BADX | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 94.7 | 94.7 | - | 86.6 | 91.5 | 13 | 94.7 | - | 76.9 | 81.2 | 13 | -10.3 | 2024 | 2027 | 3 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 100 | 101.4 | 92.2 | 110 | 99.9 | 100.6 | 91.5
STUDY | BADX | - | - | - | - | - | 2433 | 1MEBANE | 2456 | 1WLTR KI | 1 | 2433-2456-1 | 40 | 40 | - | 37.3 | 93.3 | 13 | 40 | - | 33.6 | 84.1 | 13 | -9.2 | 2023 | 2024 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 30.7 | 76.8 | 6.6 | 16.5 | - | 93 | 93.1 | 92.5 | 93.9 | 94 | 94 | 93.3
STUDY | BADX | - | - | - | - | - | 2413 | 1AO SMIT | 2456 | 1WLTR KI | 1 | 2413-2456-1 | 40 | 40 | - | 36.2 | 90.5 | 13 | 40 | - | 32.6 | 81.5 | 13 | -9 | 2025 | 2026 | 1 |  | - | - | - | - | - | - | - | - | 40 | - | 29.6 | 74 | 6.6 | 16.5 | - | 90.2 | 90.3 | 89.7 | 91 | 91.2 | 91.1 | 90.5
STUDY | BADX | - | - | - | - | - | 1041 | 1CLARK H | 3022 | CLARK H2 | 1 | 1041-3022-1 | 30 | 30 | - | 29 | 96.8 | 26 | 30 | - | 26.4 | 88.1 | 26 | -8.7 | 2021 | 2021 | 0 |  | 28.9 | 30 | 30 | CLARK HILL TIE 01 | 100/44 kV Transformer | 28.9 | 30 | 30 | 30 | - | 25.7 | 85.5 | 3.3 | 11.3 | - | 100.8 | 97.6 | 97.1 | 99.3 | 101.1 | 97 | 96.8
STUDY | BADX | - | - | - | - | - | 956 | RNDLPH R | 957 | RNDLPH T | 1 | 956-957-1 | 129.9 | 129.9 | - | 122.8 | 94.5 | 13 | 129.9 | - | 111.7 | 86 | 13 | -8.5 | 2022 | 2023 | 1 |  | 128 | 129.9 | 128 | RANDOLPH AVE | 100 kV Line | 127.9948 | 141.158 | 127.9948 | 129.9 | - | 100.5 | 77.4 | 22.3 | 17.1 | - | 95.9 | 96.1 | 94.1 | 96.3 | 96.5 | 96.4 | 94.5
STUDY | BADX | - | - | - | - | - | 304251 | LEE230 S | 304957 | WYNCO#2 | 1 | 304251-304957-1 | 220 | 220 | - | 199.9 | 90.9 | 26 | 220 | - | 185.7 | 84.4 | 26 | -6.5 | 2025 | 2024 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.3 | 86.1 | 87.4 | 87.2 | 96.3 | 89.9 | 90.8 | 90.9
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 73.2 | 146.3 | 26 | 50 | - | 52.6 | 105.2 | 26 | -41.1 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.5 | - | 146.3
Populate Summary Worksheet

## 2018 Wind
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2018 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
THRPGM | SINGLE 455 | 304369 | FAY EAST | 304389 | P2-FAY E | 2 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 1 | 304369-304389-1 | 150 | 150 | 113.9 | 227.1 | 151.4 | 100 | 150 | 113.9 | 227.1 | 151.4 | 100 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | 76.5 | 77.8 | 77.8 | 155.6 | 79.4 | 80.5 | 80.6
THRPGM | SINGLE 454 | 304369 | FAY EAST | 304389 | P2-FAY E | 1 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 2 | 304369-304389-2 | 150 | 150 | 113.2 | 227.1 | 151.4 | 100 | 150 | 113.2 | 227.1 | 151.4 | 100 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 151.4 | - | - | - | 155.6 | - | - | -
THRPGM | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 70.4 | 70.4 | 140.9 | 50 | 50 | 70.4 | 70.4 | 140.9 | 50 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 145.5 | - | 145.4 | 140.9 | 146.4 | - | 146.2
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 45.8 | 160.8 | 133.7 | 25 | 119 | 50.9 | 171.1 | 142.4 | 75 | 8.7 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 133.7 | - | - | - | 144.7 | - | - | -
RWGSGM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 118 | 144.8 | 124.8 | 275 | 113.1 | 118.3 | 145.1 | 125.1 | 275 | 0.3 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 33.2 | 29.1 | 124.8 | 112.1 | 112 | 100.4 | 128.9 | 115.9 | 115.7 | 103.6
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 93.6 | 126.1 | 124.6 | 541 | 102 | 96.3 | 129.1 | 127.6 | 661 | 3 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 124.6 | - | - | - | 108.4 | - | - | -
BEL1GM | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 702.8 | 1014.6 | 123.4 | 5836 | 822 | 681.6 | 992.4 | 120.7 | 6129 | -2.7 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 123.4 | 82.8 | 86.6 | 85.2 | 139.2 | 99.5 | 101.3 | 100.8
BEL1GM | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 449 | 791.6 | 122 | 88 | 621.4 | 448 | 789.8 | 121.7 | 85 | -0.3 | 2018 | 2018 | 0 |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 122 | 74.4 | 82.9 | 69.6 | 109.4 | 74.3 | 74.9 | 62.6
RWGSGM | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 112.2 | 138.7 | 120.1 | 275 | 113.1 | 112.5 | 139.1 | 120.5 | 275 | 0.4 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 38.4 | 33.3 | 120.1 | 107 | 107 | 95.8 | 124.2 | 110.8 | 110.7 | 99.1
THRPGM | HNDRSN-FRNKL | 304089 | HENDER11 | 304105 | FRANKLIN |  | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 118.7 | 192.4 | 117.4 | 818 | 170 | 119.6 | 193.3 | 118 | 845 | 0.6 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 117.4 | 71.8 | - | 71.3 | 118.6 | 74.7 | - | 74.3
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 120.9 | 241.3 | 117 | 75 | 201 | 126.2 | 251.8 | 122.1 | 125 | 5.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 117 | - | - | 58.5 | 123.6 | - | - | 61.8
DRGSGM | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 718 | 6SADLER 230.00 | 2679 | SADLE 3 1.0000 | 3 | 718-2679-3 | 553.7 | 553.7 | 375.2 | 645 | 116.5 | 41 | 553.7 | 376.3 | 646.8 | 116.8 | 41 | 0.3 | 2018 | 2018 | 0 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 261.1 | 460.7 | 83.2 | 184.3 | 33.3 | 116.5 | - | 74.9 | 64.2 | 101.3 | - | 70.7 | 55.9
MCG2GM | SINGLE 190 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 37.5 | 170.2 | 115.3 | 25 | 158 | 36.6 | 170.2 | 115.4 | 25 | 0.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.3 | - | - | - | 116.1 | - | - | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 257.8 | 674.7 | 114.5 | 100 | 590 | 259.4 | 678.5 | 115.6 | 100 | 1.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 114.5 | - | - | - | 115.5 | - | - | 55.2
DRGSGM | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 718 | 6SADLER 230.00 | 2673 | SADLE 4 1.0000 | 4 | 718-2673-4 | 553.7 | 553.7 | 384.8 | 631.5 | 114 | 41 | 553.7 | 385.9 | 633.3 | 114.4 | 41 | 0.4 | 2018 | 2018 | 0 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 182.6 | 32.9 | 114 | 70.5 | 76.7 | 61.3 | 98.7 | 72.1 | 72.5 | 53.6
DRGSGM | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 790 | SADLER 100.00 | 2673 | SADLE 4 1.0000 | 4 | 790-2673-4 | 553.7 | 553.7 | 384.8 | 631.5 | 114 | 41 | 553.7 | 385.9 | 633.3 | 114.4 | 41 | 0.4 | 2018 | 2018 | 0 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 182.6 | 32.9 | 114 | 70.9 | 77.1 | 61.7 | 98.7 | 72.5 | 73 | 54
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 95.3 | 129.4 | 109.6 | 364 | 116 | 98.1 | 132.5 | 112.3 | 429 | 2.7 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 109.6 | - | - | - | 95.3 | - | - | -
NANTGM | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 131.2 | 217 | 108.9 | 166 | 196.8 | 132.4 | 219 | 110 | 199 | 1.1 | 2018 | 2018 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 108.9 | 73 | 73 | 63.7 | 117.5 | 79 | 78.8 | 68.9
DRGSGM | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 790 | SADLER 100.00 | 2679 | SADLE 3 1.0000 | 3 | 790-2679-3 | 553.7 | 553.7 | 328.3 | 598.2 | 108 | 25 | 553.7 | 329.4 | 600.1 | 108.4 | 25 | 0.4 | 2018 | 2018 | 0 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 217.1 | 415.9 | 75.1 | 182.3 | 32.9 | 108 | - | 66.8 | 56.4 | 92.6 | - | 62.8 | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 203.8 | 619.4 | 105.5 | 25 | 590 | 205.2 | 623.5 | 106.5 | 25 | 1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105.5 | - | - | - | 106.5 | - | - | -
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 95.8 | 213.6 | 104.9 | 25 | 201 | 101.1 | 223.9 | 110 | 25 | 5.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.9 | - | - | - | 111.5 | - | - | -
CAT1GM | NORMANB | 540 | 6MCGUIRE | 543 | 6RIVRBEN | 1 | 540 | 6MCGUIRE 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 540-543-2 | 617.5 | 617.5 | 412.9 | 655.5 | 104.8 | 61 | 617.5 | 407.2 | 646.5 | 103.4 | 57 | -1.4 | 2018 | 2018 | 0 |  | 529.8 | 617.5 | 553.7 | NORMAN BL | 230 kV Line | 556.9073 | 617.458 | 556.9073 | - | - | - | - | - | - | 104.8 | - | - | - | 77.6 | - | - | -
THRPGM | SINGLE 146 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304099 | E18-POCO 115.00 | 304105 | FRANKLIN 115.00 | 1 | 304099-304105-1 | 170 | 170 | 43.7 | 166.5 | 104.8 | 25 | 170 | 43.5 | 166.5 | 104.9 | 25 | 0.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.8 | - | - | - | 105.4 | - | - | -
BEL1GM | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 74.4 | 101.2 | 104 | 493 | 97 | 67.5 | 94.1 | 96.8 | 423 | -7.2 | 2018 | 2021 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104 | 76.4 | - | 81.6 | 113.8 | 87.1 | - | 87.5
MCG1GM | MOSERB | 332 | 6CATAWBA | 331 | 6ALLEN | 1 | 331 | 6ALLEN 230.00 | 332 | 6CATAWBA 230.00 | 2 | 331-332-2 | 796.6 | 796.6 | 550.9 | 824.8 | 104 | 142 | 796.6 | 558.2 | 836 | 105.5 | 192 | 1.5 | 2018 | 2018 | 0 |  | 766.3292 | 796.6 | 796.6 | MOSER BL | 230 kV Line | 1151.8836 | 1436.2698 | 1151.8836 | 796.6 | 464.9 | 705.9 | 87.9 | 118.9 | 16.1 | 104 | - | - | - | 82.6 | - | - | -
CAT1GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 385.6 | 483.9 | 103.9 | 1139 | 478 | 372.7 | 468.8 | 100.5 | 1138 | -3.4 | 2018 | 2018 | 0 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 88.6 | 21 | 103.9 | 85.6 | 91.7 | 78.3 | 100.4 | 86.9 | 86.6 | 74.5
ALL5GM | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 482 | 829.4 | 103.7 | 75 | 796.7 | 481.5 | 828.6 | 103.6 | 75 | -0.1 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 209.7 | 26.9 | 103.7 | - | - | - | 104.7 | - | - | -
MCG1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 540 | 6MCGUIRE 230.00 | 546 | 8MCGUIRE 500.00 | A1 | 540-546-A1 | 1680 | 1680 | 1225.3 | 1724.4 | 102.6 | 330 | 1680 | 1215.6 | 1719 | 102.3 | 333 | -0.3 | 2018 | 2018 | 0 |  | 1573.1 | 1680 | 1680 | MCGUIRE SWITCHING STA 01 | 500/230 kV Transformer | 1680 | 1680 | 1680 | - | - | - | - | - | - | 102.6 | 75.9 | 81.5 | 68.3 | 72.3 | 72.4 | 67.3 | -
MCG1GM | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 37.2 | 76.8 | 100.8 | 25 | 71.2 | 37.2 | 76.8 | 100.8 | 25 | 0 | 2018 | 2018 | 0 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 2.4 | 1.8 | 100.8 | - | - | - | 100.5 | - | - | -
MCG1GM | ANSON-OAKBOR | 542 | 6OAKBORO | 304985 | LILES SS |  | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 381.8 | 417.5 | 100.5 | 1436 | 436.9 | 382.4 | 419 | 100.8 | 1415 | 0.3 | 2018 | 2018 | 0 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 23 | 15.8 | 100.5 | 90.6 | 88.6 | 80.6 | 94.4 | 91.5 | 85 | 76.1
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 405.3 | 488.1 | 99.8 | 858 | 478 | 405.4 | 488.2 | 99.8 | 849 | 0 | 2019 | 2019 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 58.1 | 12.2 | 99.8 | 82.6 | 82.9 | 81.7 | 102.1 | 85 | 85.1 | 83.6
RWGSGM | BELEWSCREEKB | 714 | 6BELEWS | 846 | 6N GRNSB | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 405.3 | 488.1 | 99.8 | 883 | 478 | 405.4 | 488.2 | 99.8 | 874 | 0 | 2019 | 2019 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 58.1 | 12.2 | 99.8 | 82.6 | 82.9 | 81.7 | 102.1 | 85 | 85.1 | 83.6
BEL1GM | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 349.2 | 535.8 | 98.1 | 27 | 539 | 353.5 | 543.2 | 99.6 | 53 | 1.5 | 2020 | 2019 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.1 | - | - | 63.2 | 109.3 | 71.5 | - | 69.6
THRPGM | SINGLE 179 | 304137 | METHOD | 304150 | I-NCSU S | 1 | 304163 | MILB115 TT 115.00 | 304168 | YONKERS 115.00 | 1 | 304163-304168-1 | 190 | 190 | 59.2 | 178.1 | 97.8 | 100 | 190 | 57 | 178.1 | 97.9 | 100 | 0.1 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.8 | - | - | - | 98.5 | - | - | -
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 154.5 | 571.4 | 97.4 | 25 | 590 | 155.8 | 575.8 | 98.4 | 25 | 1 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.4 | - | - | - | 98.4 | - | - | -
BEL1GM | SINGLE 208 | 304162 | MILB230 | 304163 | MILB115 | 2 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 1 | 304162-304163-1 | 300 | 300 | 215.2 | 290.3 | 96.8 | 1151 | 300 | 214.6 | 289.4 | 96.5 | 1150 | -0.3 | 2021 | 2021 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.8 | 71.7 | - | 72 | 98 | 73.3 | - | 73
STUDY | SINGLE 855 | 304730 | CAMDEN | 312715 | 6LUGOFF | 1 | 304723 | CAMDEN JCT 115.00 | 304726 | CAMDEN DUSTY115.00 | 1 | 304723-304726-1 | 108 | 108 | 40.2 | 93 | 96.2 | 75 | 108 | 40.4 | 93 | 96.2 | 75 | 0 | 2021 | 2021 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.2 | - | - | - | 96.1 | - | - | -
MCG2GM | SINGLE 213 | 304163 | MILB115 | 304168 | YONKERS | 1 | 304137 | METHOD 115.00 | 304150 | I-NCSU S 115.00 | 1 | 304137-304150-1 | 190 | 190 | 119.2 | 177.4 | 95.1 | 223 | 190 | 121 | 177.4 | 95.2 | 272 | 0.1 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.1 | - | - | 63.4 | 95.8 | - | - | 65.8
ALL5GM | AB_STEEL_W_S | 331 | 6ALLEN | 545 | 6WOODLWN | 2 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 1 | 331-545-1 | 717 | 717 | 453.9 | 663.9 | 94.9 | 26 | 717 | 453.5 | 663.4 | 94.9 | 26 | 0 | 2022 | 2022 | 0 |  | 717 | 717 | 717 | STEELBERRY WH | 230 kV Line | 792.617 | 996.5466 | 792.617 | - | - | - | - | - | - | 94.9 | - | 65.6 | 63.7 | 91.7 | - | 64.4 | 61.7
ALL5GM | AB_STEEL_B_S | 331 | 6ALLEN | 545 | 6WOODLWN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 453.9 | 663.8 | 94.9 | 76 | 717 | 453.5 | 663.4 | 94.9 | 76 | 0 | 2022 | 2022 | 0 |  | 717 | 717 | 717 | STEELBERRY BL | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 444.2 | 658.7 | 93.6 | 5.1 | 1.3 | 94.9 | - | - | - | 91.7 | - | - | -
CAT1GM | DACUSB | 7 | 6OCONEE | 107 | 6N GRNVL | 1 | 4 | 6CENTRAL 230.00 | 104 | 6SHADYTB 230.00 | 1 | 4-104-1 | 478 | 478 | 385.6 | 439.9 | 94.1 | 1114 | 478 | 375.1 | 428.4 | 91.6 | 1113 | -2.5 | 2022 | 2024 | 2 |  | 458.045 | 478 | 458.045 | FISHER BL | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 356.5 | 74.6 | 83.4 | 19.5 | 94.1 | 85.6 | 91.7 | 78.3 | 89.6 | 86.9 | 86.6 | 74.5
THRPGM | SINGLE 659 | 304563 | LELAND I | 304568 | DELCO | 1 | 304035 | SUT 1-2F 115.00 | 304560 | I-ASMPCS 115.00 | 1 | 304035-304560-1 | 159 | 159 | 71.6 | 151.2 | 94.1 | 50 | 159 | 77.3 | 151.2 | 94.1 | 50 | 0 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.1 | - | - | - | 94.1 | - | - | -
BEL1GM | ROCK_SPRINGS | 546 | 8MCGUIRE | 719 | 8ANTIOCH | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1693.2 | 1862.9 | 94 | 5880 | 1904.3 | 1704.8 | 1879.6 | 95 | 5974 | 1 | 2022 | 2022 | 0 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1478.9 | 1641.2 | 81.8 | 221.7 | 12.2 | 94 | 84.8 | 92.6 | 79.9 | 87.5 | 89.5 | 86.3 | 74.3
MCG1GM | SINGLE 424 | 304348 | ROCKHM23 | 304378 | RICH230 | 2 | 304348 | ROCKHM230 TT230.00 | 304378 | RICH230 TT 230.00 | 1 | 304348-304378-1 | 1014 | 1014 | 606.2 | 968.7 | 93.9 | 75 | 1014 | 595.3 | 950.7 | 92.2 | 75 | -1.7 | 2022 | 2024 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.9 | - | - | 59.2 | 92.4 | - | - | 58.5
MCG1GM | SINGLE 215 | 304163 | MILB115 | 304174 | I-PERSTO | 1 | 304137 | METHOD 115.00 | 304153 | TRYON HILLS 115.00 | 1 | 304137-304153-1 | 108 | 108 | 59.5 | 97.6 | 93.9 | 154 | 108 | 61.3 | 97.6 | 93.9 | 175 | 0 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.9 | - | - | 56.4 | 94.6 | - | - | 59.1
CAT1GM | MCGUIRE_XFMR | 546 | 8MCGUIRE | 540 | 6MCGUIRE | A1 | 333 | 6NEWPORT 230.00 | 337 | 8NEWPORT 500.00 | A5 | 333-337-A5 | 1120 | 1120 | 729.3 | 1044.1 | 93.2 | 12 | 1120 | 721.1 | 1032.9 | 92.2 | 11 | -1 | 2023 | 2024 | 1 |  | 1120 | 1120 | 1120 | NEWPORT TIE AT5 | 500/230 kV Transformer | 1120 | 1120 | 1120 | - | - | - | - | - | - | 93.2 | - | 100 | 61.9 | - | - | 63 | -
THRPGM | BASE CASE | 0 |  | 0 |  |  | 304615 | BARN CRK E 230.00 | 304616 | BARNARD 115.00 | 1 | 304615-304616-1 | 150 | 150 | 139.4 | 139.4 | 92.9 | 50 | 150 | 139.4 | 139.4 | 92.9 | 50 | 0 | 2023 | 2023 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.5 | - | 91.6 | 93 | 92.8 | - | 92.8
THRPGM | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 71 | 187.8 | 92.5 | 25 | 201 | 76.2 | 198.1 | 97.6 | 25 | 5.1 | 2023 | 2020 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.5 | - | - | - | 99 | - | - | -
NANTGM | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 432.4 | 736.1 | 92.4 | 46 | 796.7 | 439.2 | 747.5 | 93.8 | 49 | 1.4 | 2023 | 2023 | 0 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 35.2 | 4.4 | 92.4 | - | 53.4 | - | 101.9 | - | - | -
BEL1GM | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304047 | WSPN115 TT 115.00 | 304406 | ST PAULS 115.00 | 1 | 304047-304406-1 | 119 | 119 | 88 | 110.9 | 92.4 | 552 | 119 | 100.4 | 125 | 104.3 | 895 | 11.9 | 2023 | 2018 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.4 | 73.7 | - | 77.3 | 97.1 | 80.2 | - | 81.1
BEL1GM | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304550 | CASTLE HAYNE230.00 | 304577 | MURRAYVL 230.00 | 1 | 304550-304577-1 | 590 | 590 | 121.8 | 540.1 | 92 | 25 | 590 | 122.9 | 544.8 | 93 | 25 | 1 | 2024 | 2023 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | - | 93 | - | - | -
BEL1GM | SINGLE 937 | 304747 | WALTERS | 361167 | 5COSBY T | 1 | 304740 | WALTERS 138.00 | 22854 | 05SULVN 138.00 | 1 | 22854-304740-1 | 100 | 100 | 69.2 | 89.8 | 91.7 | 164 | 100 | 66.4 | 87 | 89.1 | 127 | -2.6 | 2024 | 2026 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.7 | 70.8 | - | 52.3 | 88.3 | 80.4 | - | -
THRPGM | SINGLE 232 | 304182 | FALLS230 | 304185 | FALLS115 | 2 | 304182 | FALLS230 TT 230.00 | 304185 | FALLS115 TT 115.00 | 1 | 304182-304185-1 | 300 | 300 | 197 | 275.1 | 91.7 | 450 | 300 | 197.7 | 276.1 | 92 | 481 | 0.3 | 2024 | 2024 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.7 | - | - | 65.8 | 92.3 | - | - | 66.3
LEE3GM | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 105 | 6SHADYTW 230.00 | 109 | 6SHADY G 230.00 | 2 | 105-109-2 | 478 | 478 | 262.2 | 421.4 | 91.5 | 24 | 478 | 244 | 392.2 | 84.7 | 18 | -6.8 | 2024 | 2029 | 5 |  | 477.96 | 477.96 | 477.96 | SHADY GROVE WH | 230 kV Line | 859.9297 | 1008.8939 | 859.9297 | 478 | 207.1 | 333.8 | 70.7 | 87.6 | 20.8 | 91.5 | - | 57.7 | 53.6 | 87.9 | - | 57.1 | 51.4
BEL1GM | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 304378 | RICH230 TT 230.00 | 304978 | RICH CC2 18.000 | 1 | 304378-304978-1 | 795 | 795 | 692.8 | 725.7 | 91.3 | 586 | 795 | 696.8 | 728.8 | 91.7 | 690 | 0.4 | 2024 | 2024 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | 84.1 | 86.5 | 85.4 | 93.8 | 88.6 | 89.4 | 88.5
BEL1GM | ANTIOCH_XFM1 | 719 | 8ANTIOCH | 712 | 6ANTIOCH | 1 | 712 | 6ANTIOCH 230.00 | 719 | 8ANTIOCH 500.00 | 2 | 712-719-2 | 840 | 840 | 479.3 | 766.3 | 91.2 | 15 | 840 | 476.2 | 761.3 | 90.6 | 14 | -0.6 | 2024 | 2025 | 1 |  | 840 | 840 | 840 | ANTIOCH TIE 02 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 460.2 | 736.3 | 87.7 | 30 | 3.5 | 91.2 | - | - | 56.3 | - | - | 55.7 | -
BEL1GM | SINGLE 207 | 304162 | MILB230 | 304163 | MILB115 | 1 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 2 | 304162-304163-2 | 300 | 300 | 203 | 272.3 | 90.8 | 436 | 300 | 202.4 | 271.4 | 90.5 | 405 | -0.3 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | - | - | - | 91.8 | - | - | -
BEL1GM | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304550 | CASTLE HAYNE230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304550-304564-1 | 478 | 478 | 332 | 432.8 | 90.8 | 882 | 478 | 369.2 | 477.3 | 100.5 | 2440 | 9.7 | 2025 | 2018 | -7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | - | - | 70.1 | 92.7 | 71.4 | - | 71.5
BEL1GM | SINGLE 463 | 304378 | RICH230 | 304423 | LAUREL H | 1 | 304057 | DARLINGTON 230.00 | 304954 | DCP#12 13.800 | 1 | 304057-304954-1 | 150 | 150 | 128.1 | 135.8 | 90.5 | 157 | 150 | 128.9 | 138.3 | 92.2 | 186 | 1.7 | 2025 | 2024 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.5 | 82.8 | 85.1 | 84.8 | 96.2 | 90.9 | 91.9 | 92.1
DRGSGM | SADLERB | 826 | 6ERNEST2 | 718 | 6SADLER | 1 | 718 | 6SADLER 230.00 | 826 | 6ERNEST2 230.00 | 2 | 718-826-2 | 717 | 717 | 377.9 | 664.2 | 90.3 | 24 | 717 | 379 | 666.2 | 90.6 | 24 | 0.3 | 2025 | 2025 | 0 |  | 576 | 717 | 576 | SADLER WH | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 90.3 | - | - | - | 78.9 | - | - | -
BEL1GM | SINGLE 240 | 304190 | WAKE 230 | 304191 | WENDELL | 1 | 304156 | ROL/SQD TAP 230.00 | 304190 | WAKE 230 230.00 | 1 | 304156-304190-1 | 797 | 797 | 554 | 728.4 | 90.2 | 1084 | 797 | 552.7 | 734.5 | 91.1 | 1084 | 0.9 | 2025 | 2024 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.2 | - | - | 69.4 | 91.5 | 72.5 | - | 70.2
BEL1GM | SINGLE 462 | 304378 | RICH230 | 304415 | RAEFORD | 1 | 304047 | WSPN115 TT 115.00 | 304432 | PA-LUMB#2 115.00 | 1 | 304047-304432-1 | 133 | 133 | 88.5 | 117.4 | 90.1 | 380 | 133 | 99.5 | 128.3 | 98.8 | 556 | 8.7 | 2025 | 2019 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.1 | - | - | 70.7 | 92.7 | - | - | 72.1
CAT1GM | DACUSB | 7 | 6OCONEE | 107 | 6N GRNVL | 1 | 7 | 6OCONEE 230.00 | 107 | 6N GRNVL 230.00 | 2 | 7-107-2 | 478 | 478 | 361 | 420.2 | 90 | 568 | 478 | 353.5 | 411.4 | 88.2 | 498 | -1.8 | 2025 | 2026 | 1 |  | 459.7 | 477.96 | 477.96 | DACUS WH | 230 kV Line | 556.9073 | 617.458 | 556.9073 | 478 | 293.6 | 342.5 | 71.8 | 77.7 | 18.2 | 90 | - | - | - | 85.4 | - | - | -
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 3 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 4 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDYASH1VRS | FIBERLN1 | 9 | ANDERSON | 66 | TOXAWAY | 1 | 9 | ANDERSON 100.00 | 66 | TOXAWAY 100.00 | 2 | 9-66-2 | 346.4 | 346.4 | 222.7 | 369.9 | 103.5 | 13 | 346.4 | 205.8 | 341.7 | 95.5 | 13 | -8 | 2018 | 2021 | 3 |  | 346.4 | 346.4 | 346.4 | FIBER BL | 100 kV Line | 440.6208 | 511.4596 | 440.6208 | - | - | - | - | - | - | - | - | - | - | 103.5 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 163 | HNDRSNVL 100.00 | 1 | 132-163-1 | 64.8 | 64.8 | 20.7 | 62.3 | 98 | 7 | 64.8 | 18.6 | 58.1 | 91.2 | 1 | -6.8 | 2020 | 2024 | 4 |  | 64.8 | 70.7 | 64.8 | HOGBACK | 100 kV Line | 69.6264 | 75.6884 | 69.6264 | - | - | - | - | - | - | 70.2 | - | - | - | 98 | - | - | -
STUDYASH1VRS | PISGAH230-SH | 110 | 6SHILOH | 108 | 6PISGAH |  | 132 | CAMPOBEL 100.00 | 163 | HNDRSNVL 100.00 | 2 | 132-163-2 | 64.8 | 64.8 | 20.7 | 62.3 | 98 | 7 | 64.8 | 18.6 | 58.1 | 91.2 | 1 | -6.8 | 2020 | 2024 | 4 |  | 64.8 | 70.7 | 64.8 | HOGBACK | 100 kV Line | 69.6264 | 75.6884 | 69.6264 | - | - | - | - | - | - | 70.2 | - | - | - | 98 | - | - | -
STUDYBRN1VRS | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 79.7 | 110.1 | 113.8 | 222 | 97 | 72.5 | 102.6 | 106.1 | 174 | -7.7 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104 | 76.4 | - | 81.6 | 113.8 | 87.1 | - | 87.5
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 1 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BUGS | - | - | - | - | - | 537 | 6COWANS1 | 540 | 6MCGUIRE | 1 | 537-540-1 | 318.6 | 318.6 | - | 335.6 | 105.3 | 192 | 318.6 | - | 272.7 | 85.6 | 39 | -19.7 | 2018 | 2028 | 10 |  | 306.691 | 318.64 | 318.64 | COWANS FORD BL | 230 kV Line | 422.9946 | 524.5611 | 422.9946 | 318.6 | - | 183.4 | 57.6 | 152.2 | 47.7 | 79.5 | - | 70 | - | 78.8 | - | 105.3 | -
1.6 | % Yearly Load Growth |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\2018 Wind\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018_wind.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case) |  |  |  | 2018 Summer Screening Wind Case (2008 NCPWG Study Base Case)
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
Populate Summary Worksheet

## 2013 Base - PEC Br1DnTRM
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 49.4 | 164.3 | 136.7 | 3 | 119 | 45.5 | 155 | 128.7 | 48 | -8 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 136.7 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 121.3 | 241.3 | 117.1 | 3 | 201 | 116.5 | 231.1 | 112.2 | 144 | -4.9 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 117.1 | - | - | - | - | - | - | 59.7
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 637.7 | 928.1 | 112.9 | 221 | 822 | 671 | 986 | 120 | 10818 | 7.1 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.9 | 75.4 | 77.7 | - | - | 94 | 95.9 | 95.6
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 106.4 | 130.5 | 112.3 | 9 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -0.1 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 18.9 | 16.6 | 112.3 | 100.8 | 100.8 | - | - | 104.5 | 100.4 | 89.7
STUDY | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 102.6 | 186.2 | 111.8 | 16 | 170 | 109.6 | 187.4 | 112.1 | 1070 | 0.3 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 111.8 | - | - | - | - | - | - | 67.3
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 101.1 | 125 | 108 | 9 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -0.1 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 24.7 | 21.2 | 108 | 96.2 | 96.2 | - | - | 99.9 | 95.8 | 85.6
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 97.1 | 214.5 | 105.4 | 1 | 201 | 92.4 | 204.8 | 100.5 | 48 | -4.9 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105.4 | - | - | - | - | - | - | -
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 127.4 | 210.6 | 105 | 8 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -4.1 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 105 | 70.4 | 70.4 | - | - | 73.5 | 70.9 | 61.7
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 62 | 112.1 | 103.5 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 2.6 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 16.1 | 14.9 | 103.5 | - | 61.9 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 62 | 112.1 | 103.5 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 2.6 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 16.1 | 14.9 | 103.5 | - | - | - | - | - | - | -
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 2 | 50 | 51.6 | 51.6 | 103.1 | 96 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.3 | - | - | - | 105.4 | - | 105.2
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 310.4 | 608.7 | 102.5 | 3 | 590 | 243 | 644.5 | 108.7 | 48 | 6.2 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.5 | - | - | - | - | - | - | 52.6
STUDY | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 17 | 149.1 | 99.7 | 1 | 158 | 23.1 | 149.1 | 99.3 | 48 | -0.4 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.7 | - | - | - | - | - | - | -
STUDY | SINGLE 751 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 70.5 | 95 | 97.3 | 26 | 97 | 55.6 | 76 | 77.2 | 87 | -20.1 | 2015 | 2030 | 15 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.3 | 72.2 | - | - | - | - | - | 69.3
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 452.6 | 770 | 96.7 | 2 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -8.2 | 2016 | 2021 | 5 | CT Upgrade (1039.2 MVA) pushes out to 2032 | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 69.1 | 8.7 | 96.7 | - | - | - | - | - | - | 52.4
STUDY | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 98.4 | 212.7 | 96.5 | 3 | 220 | 92.6 | 201.2 | 91.3 | 96 | -5.2 | 2016 | 2019 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.5 | - | - | - | - | - | - | -
STUDY | SINGLE 627 | 304530 | JACKSV11 | 305068 | E9-JAX N | 1 | 304530 | JACKSV115 TT115.00 | 304535 | NORTHWOODS 115.00 | 1 | 304530-304535-1 | 221 | 221 | 116.2 | 208.9 | 95.7 | 5 | 221 | 109 | 196.6 | 90 | 240 | -5.7 | 2016 | 2020 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.7 | - | - | - | - | - | - | 51.7
STUDY | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 118.9 | 178.3 | 95.6 | 5 | 201 | 110 | 174.9 | 93.4 | 96 | -2.2 | 2016 | 2018 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.6 | - | - | - | - | - | - | 58.5
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 259.2 | 555.7 | 94 | 2 | 590 | 191.8 | 591.2 | 100.1 | 48 | 6.1 | 2017 | 2013 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94 | - | - | - | - | - | - | -
STUDY | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 355.8 | 400.6 | 93.9 | 47 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -4.1 | 2017 | 2020 | 3 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 6.1 | 9.2 | 93.9 | 83 | 82.3 | - | - | 83.1 | 80.6 | 72.1
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 442.6 | 762.9 | 93.7 | 3 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | -0.2 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 143.2 | 16.9 | 93.7 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 73 | 189.5 | 93.3 | 1 | 201 | 68.4 | 180 | 88.5 | 48 | -4.8 | 2018 | 2021 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.3 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 67.5 | 95 | 93.2 | 16 | 102 | 90.2 | 120.4 | 118.4 | 910 | 25.2 | 2018 | 2013 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.2 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 375.3 | 450.2 | 92.4 | 33 | 478 | 365.4 | 440 | 89.7 | 1473 | -2.7 | 2018 | 2020 | 2 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 20.2 | 4.8 | 92.4 | 76.5 | 76.8 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 375.3 | 450.2 | 92.4 | 34 | 478 | 365.4 | 440 | 89.7 | 1520 | -2.7 | 2018 | 2020 | 2 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 20.2 | 4.8 | 92.4 | 76.5 | 76.8 | - | - | 76.7 | 76.3 | 74.8
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 437.2 | 762.5 | 90.8 | 1 | 840 | 400 | 698.1 | 83.1 | 48 | -7.7 | 2020 | 2025 | 5 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 67.9 | 8.1 | 90.8 | - | 51 | - | - | - | 51.3 | -
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 52.7 | 105.4 | 702 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.3 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 102.6 | 99.9 | 702 | 0 | 2014 | 2014 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 108 | 96.2 | 96.2 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 107.3 | 104.5 | 351 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 112.3 | 100.8 | 100.8 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 114.1 | 90.3 | 351 | 0 | 2020 | 2020 | 0 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 84.6 | 87.9 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 20.2 | 90.8 | 351 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | 89.4 | 89.4 | 89.4 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 115.7 | 96.4 | 351 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 95.8 | 95.9 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 101 | 98.3 | 350 | 0 | 2015 | 2015 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 85.9 | 98.6 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 84.4 | 97.5 | 325 | 0 | 2015 | 2015 | 0 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 88.6 | 89.9 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 98.7 | 96.1 | 336 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 83.7 | 96.4 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | 556.9 | - | 521.2 | 93.6 | 351 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 94.7 | 92.2 | 262 | 0 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 88.7 | 79.9 | 92.5 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.5 | 674 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.3 | 79.4 | 80.9 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 98.4 | 95.8 | 674 | 0 | 2016 | 2016 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 108 | 96.2 | 96.2 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 103.1 | 100.4 | 337 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 112.3 | 100.8 | 100.8 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 20.2 | 90.7 | 337 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | 89.4 | 89.4 | 89.4 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115.9 | 96.3 | 337 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 95.8 | 95.9 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 101.3 | 98.7 | 337 | 0 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 85.9 | 98.6 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 99 | 96.4 | 337 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 83.7 | 96.4 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | 556.9 | - | 521.2 | 93.6 | 337 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 95 | 92.5 | 337 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 88.7 | 79.9 | 92.5 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC Br1DnTRM |  |  |  | Base 2013 w PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 52.6 | 105.2 | 26 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.3 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.3 | 79.4 | 80.9 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2013 Base-PEC HrDnTRM
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 4 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 2 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 6 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 42.7 | 149.5 | 124.2 | 1 | 119 | 45.5 | 155 | 128.7 | 48 | 4.5 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 124.2 | - | - | - | - | - | - | -
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 107.4 | 131.8 | 113.5 | 9 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -1.3 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 20.2 | 17.8 | 113.5 | 101.9 | 101.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 634.1 | 926.3 | 112.7 | 226 | 822 | 671 | 986 | 120 | 10818 | 7.3 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.7 | 74.7 | 77.3 | - | - | 94 | 95.9 | 95.6
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 113.7 | 225.7 | 109.6 | 3 | 201 | 116.5 | 231.1 | 112.2 | 144 | 2.6 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 109.6 | - | - | - | - | - | - | 59.7
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 102.1 | 126.3 | 109.2 | 9 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -1.3 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 26 | 22.4 | 109.2 | 97.3 | 97.2 | - | - | 99.9 | 95.8 | 85.6
STUDY | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 96.8 | 180.7 | 108.9 | 12 | 170 | 109.6 | 187.4 | 112.1 | 1070 | 3.2 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 108.9 | - | - | - | - | - | - | 67.3
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 129.4 | 213.9 | 107 | 8 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -6.1 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 107 | 71.8 | 71.7 | - | - | 73.5 | 70.9 | 61.7
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 242.2 | 634.5 | 106.8 | 1 | 590 | 243 | 644.5 | 108.7 | 48 | 1.9 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 106.8 | - | - | - | - | - | - | 52.6
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 62 | 111.9 | 103.4 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 2.7 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 15.9 | 14.8 | 103.4 | - | 61.8 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 62 | 111.9 | 103.4 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 2.7 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 15.9 | 14.8 | 103.4 | - | - | - | - | - | - | -
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 2 | 50 | 51.6 | 51.6 | 103.1 | 96 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
STUDY | SINGLE 421 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 353.1 | 547.2 | 100.2 | 3 | 539 | 318.7 | 488.1 | 89 | 48 | -11.2 | 2013 | 2021 | 8 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.2 | - | - | - | - | - | - | 64.1
STUDY | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 18.9 | 149.1 | 100 | 1 | 158 | 23.1 | 149.1 | 99.3 | 48 | -0.7 | 2013 | 2014 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 464 | 789.3 | 99.1 | 2 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -10.6 | 2014 | 2021 | 7 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 88.4 | 11.1 | 99.1 | - | - | - | - | - | - | 52.4
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 191.1 | 581.2 | 98.3 | 1 | 590 | 191.8 | 591.2 | 100.1 | 48 | 1.8 | 2015 | 2013 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.3 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 89.6 | 199.5 | 97.9 | 1 | 201 | 92.4 | 204.8 | 100.5 | 48 | 2.6 | 2015 | 2013 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.9 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 69.1 | 97.1 | 95.4 | 18 | 102 | 90.2 | 120.4 | 118.4 | 910 | 23 | 2016 | 2013 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.4 | - | - | - | - | - | - | -
STUDY | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 119.6 | 175.5 | 94 | 7 | 201 | 110 | 174.9 | 93.4 | 96 | -0.6 | 2017 | 2018 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94 | - | - | - | - | - | - | 58.5
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 379.2 | 456.2 | 93.9 | 34 | 478 | 365.4 | 440 | 89.7 | 1473 | -4.2 | 2017 | 2020 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 26.2 | 6.3 | 93.9 | 77.5 | 77.8 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 379.2 | 456.2 | 93.9 | 35 | 478 | 365.4 | 440 | 89.7 | 1520 | -4.2 | 2017 | 2020 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 26.2 | 6.3 | 93.9 | 77.5 | 77.8 | - | - | 76.7 | 76.3 | 74.8
STUDY | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 357 | 400.5 | 93.9 | 47 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -4.1 | 2017 | 2020 | 3 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 6 | 9.2 | 93.9 | 83.4 | 82.6 | - | - | 83.1 | 80.6 | 72.1
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 443.1 | 763.7 | 93.8 | 3 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | -0.3 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 144 | 17 | 93.8 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 448.2 | 781.5 | 93 | 1 | 840 | 400 | 698.1 | 83.1 | 48 | -9.9 | 2018 | 2025 | 7 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 86.9 | 10.3 | 93 | - | 52.6 | - | - | - | 51.3 | -
STUDY | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 93.7 | 203.4 | 92.3 | 3 | 220 | 92.6 | 201.2 | 91.3 | 96 | -1 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.3 | - | - | - | - | - | - | -
STUDY | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 735 | 735 | 443.1 | 690.8 | 92 | 2 | 735 | 443.5 | 688.5 | 91.7 | 96 | -0.3 | 2019 | 2019 | 0 |  | 735 | 796.7 | 735 | PINOCA BL | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 354.3 | 619.7 | 76.8 | 71.1 | 15.2 | 92 | - | 61.4 | - | - | - | 60.9 | 53.1
STUDY | SINGLE 627 | 304530 | JACKSV11 | 305068 | E9-JAX N | 1 | 304530 | JACKSV115 TT115.00 | 304535 | NORTHWOODS 115.00 | 1 | 304530-304535-1 | 221 | 221 | 110.4 | 198.9 | 91 | 5 | 221 | 109 | 196.6 | 90 | 240 | -1 | 2019 | 2020 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91 | - | - | - | - | - | - | 51.7
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 145.5 | 535.6 | 90.7 | 1 | 590 | 146.7 | 546.3 | 92.6 | 48 | 1.9 | 2020 | 2018 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.7 | - | - | - | - | - | - | -
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 52.7 | 105.4 | 702 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 102.6 | 99.9 | 702 | 0 | 2014 | 2014 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 109.2 | 97.3 | 97.2 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 107.3 | 104.5 | 351 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 113.5 | 101.9 | 101.9 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 114.1 | 90.3 | 351 | 0 | 2020 | 2020 | 0 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 84.4 | 87.7 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 20.2 | 90.8 | 351 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | 89.5 | 89.5 | 89.5 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 115.7 | 96.4 | 351 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 95.5 | 95.6 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 101 | 98.3 | 350 | 0 | 2015 | 2015 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 86.3 | 99 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 84.4 | 97.5 | 325 | 0 | 2015 | 2015 | 0 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 88.7 | 90 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 98.7 | 96.1 | 336 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 84.1 | 96.8 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | 556.9 | - | 521.2 | 93.6 | 351 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 94.7 | 92.2 | 262 | 0 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.1 | 80.3 | 92.9 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.5 | 674 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.1 | 79.4 | 80.8 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 98.4 | 95.8 | 674 | 0 | 2016 | 2016 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 109.2 | 97.3 | 97.2 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 103.1 | 100.4 | 337 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 113.5 | 101.9 | 101.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 20.2 | 90.7 | 337 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | 89.5 | 89.5 | 89.5 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115.9 | 96.3 | 337 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 95.5 | 95.6 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 101.3 | 98.7 | 337 | 0 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 86.3 | 99 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 99 | 96.4 | 337 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 84.1 | 96.8 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | 556.9 | - | 521.2 | 93.6 | 337 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 95 | 92.5 | 337 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 89.1 | 80.3 | 92.9 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w PEC HrDnTRM |  |  |  | Base 2013 w PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 52.6 | 105.2 | 26 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.1 | 79.4 | 80.8 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2013 FPWC-PEC Br1DnTRM
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 13 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 7 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 20 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 47.8 | 161.5 | 134.4 | 2 | 119 | 45.5 | 155 | 128.7 | 48 | -5.7 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 134.4 | - | - | - | - | - | - | -
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 111.6 | 136.9 | 117.9 | 9 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -5.7 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 25.3 | 22.2 | 117.9 | 105.9 | 105.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 119.7 | 238.5 | 115.8 | 3 | 201 | 116.5 | 231.1 | 112.2 | 144 | -3.6 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 115.8 | - | - | - | - | - | - | 59.7
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 106.3 | 131.3 | 113.6 | 9 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -5.7 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 31 | 26.8 | 113.6 | 101.3 | 101.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 638.9 | 928.6 | 113 | 228 | 822 | 671 | 986 | 120 | 10818 | 7 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 113 | 75.3 | 77.5 | - | - | 94 | 95.9 | 95.6
STUDY | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 101.7 | 187.2 | 112.8 | 15 | 170 | 109.6 | 187.4 | 112.1 | 1070 | -0.7 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.8 | - | - | - | - | - | - | 67.3
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 134.2 | 221.7 | 110.9 | 14 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -10 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 110.9 | 74.4 | 74.4 | - | - | 73.5 | 70.9 | 61.7
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 95.5 | 211.8 | 104.1 | 1 | 201 | 92.4 | 204.8 | 100.5 | 48 | -3.6 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.1 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 311.3 | 611.2 | 103.2 | 3 | 590 | 243 | 644.5 | 108.7 | 48 | 5.5 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.2 | - | - | - | - | - | - | 52.6
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.1 | 2 | 50 | 51.6 | 51.6 | 103.1 | 96 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.4 | 110.9 | 102.4 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 3.7 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 14.9 | 13.8 | 102.4 | - | 61.3 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.4 | 110.9 | 102.4 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 3.7 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 14.9 | 13.8 | 102.4 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 471.6 | 802.2 | 100.7 | 2 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -12.2 | 2013 | 2021 | 8 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 101.3 | 12.7 | 100.7 | - | - | - | - | - | - | 52.4
STUDY | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 14.4 | 149.1 | 100 | 1 | 158 | 23.1 | 149.1 | 99.3 | 48 | -0.7 | 2013 | 2014 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100 | - | - | - | - | - | - | -
STUDY | SINGLE 751 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 71.8 | 97.5 | 99.9 | 27 | 97 | 55.6 | 76 | 77.2 | 87 | -22.7 | 2014 | 2030 | 16 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.9 | 73.6 | - | - | - | - | - | 69.3
STUDY | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 121.7 | 180.3 | 96.9 | 8 | 201 | 110 | 174.9 | 93.4 | 96 | -3.5 | 2015 | 2018 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.9 | - | - | - | - | - | - | 58.5
STUDY | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 361.2 | 410.1 | 96.3 | 47 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -6.5 | 2016 | 2020 | 4 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 15.6 | 11.6 | 96.3 | 84.3 | 83.5 | - | - | 83.1 | 80.6 | 72.1
STUDY | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 98.2 | 212.1 | 96.3 | 3 | 220 | 92.6 | 201.2 | 91.3 | 96 | -5 | 2016 | 2019 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.3 | - | - | - | - | - | - | -
STUDY | SINGLE 627 | 304530 | JACKSV11 | 305068 | E9-JAX N | 1 | 304530 | JACKSV115 TT115.00 | 304535 | NORTHWOODS 115.00 | 1 | 304530-304535-1 | 221 | 221 | 115.8 | 208.3 | 95.4 | 5 | 221 | 109 | 196.6 | 90 | 240 | -5.4 | 2016 | 2020 | 4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.4 | - | - | - | - | - | - | 51.7
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 260 | 558.6 | 94.7 | 2 | 590 | 191.8 | 591.2 | 100.1 | 48 | 5.4 | 2017 | 2013 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.7 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 455.5 | 794.3 | 94.6 | 1 | 840 | 400 | 698.1 | 83.1 | 48 | -11.5 | 2017 | 2025 | 8 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 99.7 | 11.9 | 94.6 | - | 53.3 | - | - | - | 51.3 | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 381.6 | 458.5 | 94.4 | 33 | 478 | 365.4 | 440 | 89.7 | 1473 | -4.7 | 2017 | 2020 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 28.5 | 6.8 | 94.4 | 77.9 | 78.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 381.6 | 458.5 | 94.4 | 34 | 478 | 365.4 | 440 | 89.7 | 1520 | -4.7 | 2017 | 2020 | 3 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 28.5 | 6.8 | 94.4 | 77.9 | 78.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 71.4 | 186.7 | 92 | 1 | 201 | 68.4 | 180 | 88.5 | 48 | -3.5 | 2019 | 2021 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 64.9 | 93.7 | 92 | 12 | 102 | 90.2 | 120.4 | 118.4 | 910 | 26.4 | 2019 | 2013 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | - | - | - | - | -
STUDY | SINGLE 246 | 304196 | ERWIN | 304197 | DUNN | 1 | 304265 | E15-STED 115.00 | 304401 | VANDER 115.00 | 1 | 304265-304401-1 | 163 | 163 | 122.4 | 146.5 | 90.6 | 38 | 163 | 107.9 | 129.7 | 80.7 | 591 | -9.9 | 2020 | 2027 | 7 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.6 | 75.5 | - | - | - | 72.3 | - | 70.3
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 427.2 | 736.5 | 90.3 | 3 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | 3.2 | 2020 | 2018 | -2 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 116.8 | 13.5 | 90.3 | - | - | - | - | - | - | -
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 104 | 101.3 | 2 | 102.7 | - | 98.8 | 96.2 | 96 | -5.1 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 19.8 | 19.3 | 113.6 | 101.3 | 101.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 108.8 | 105.9 | 1 | 102.7 | - | 103.5 | 100.8 | 48 | -5.1 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 19.9 | 19.3 | 117.9 | 105.9 | 105.9 | - | - | 104.5 | 100.4 | 89.7
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 104 | 101.3 | 52 | 102.7 | - | 98.8 | 96.2 | 1384 | -5.1 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 19.8 | 19.3 | 113.6 | 101.3 | 101.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 108.8 | 105.9 | 26 | 102.7 | - | 103.4 | 100.7 | 692 | -5.2 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.5 | 19.9 | 19.4 | 117.9 | 105.9 | 105.9 | - | - | 104.5 | 100.4 | 89.7
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 52.7 | 105.4 | 702 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 102.6 | 99.9 | 702 | 0 | 2014 | 2014 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 113.6 | 101.3 | 101.3 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 107.3 | 104.5 | 351 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 117.9 | 105.9 | 105.9 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 114.1 | 90.3 | 351 | 0 | 2020 | 2020 | 0 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 84 | 87.3 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 20.2 | 90.8 | 351 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | 89.5 | 89.5 | 89.5 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 115.7 | 96.4 | 351 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 95.6 | 95.7 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 101 | 98.3 | 350 | 0 | 2015 | 2015 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.8 | 76.2 | 88.9 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 84.4 | 97.5 | 325 | 0 | 2015 | 2015 | 0 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 97.3 | 98.6 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 98.7 | 96.1 | 336 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | 81.8 | 74.2 | 86.8 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | 556.9 | - | 521.2 | 93.6 | 351 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 94.7 | 92.2 | 262 | 0 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.4 | 70.7 | 83.1 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.5 | 674 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.1 | 79.2 | 80.7 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 98.4 | 95.8 | 674 | 0 | 2016 | 2016 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 113.6 | 101.3 | 101.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 103.1 | 100.4 | 337 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 117.9 | 105.9 | 105.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 20.2 | 90.7 | 337 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | 89.5 | 89.5 | 89.5 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115.9 | 96.3 | 337 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 95.6 | 95.7 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 101.3 | 98.7 | 337 | 0 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 83.8 | 76.2 | 88.9 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 99 | 96.4 | 337 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | 81.8 | 74.2 | 86.8 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | 556.9 | - | 521.2 | 93.6 | 337 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 95 | 92.5 | 337 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.4 | 70.7 | 83.1 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-Br1DnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_Br1DnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC Br1DnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC Br1DnTRM |  |  |  | Base 2013 w Fayettevile and PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 52.6 | 105.2 | 26 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.1 | 105.6 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.1 | 79.2 | 80.7 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2013 FPWC-PEC HrDnTRM
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2013 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 12 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 6 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 18 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 41.4 | 147.2 | 122.3 | 1 | 119 | 45.5 | 155 | 128.7 | 48 | 6.4 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 122.3 | - | - | - | - | - | - | -
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 112.5 | 138 | 119.1 | 9 | 113.1 | 106.5 | 130.6 | 112.2 | 434 | -6.9 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 26.4 | 23.4 | 119.1 | 107 | 106.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 897 | GLEN RVN 100.00 | 1 | 857-897-1 | 207.8 | 207.8 | 156.9 | 245.9 | 116.6 | 18 | 207.8 | 143.6 | 224 | 105.3 | 191 | -11.3 | 2013 | 2013 | 0 |  | 207.8 | 207.8 | 207.8 | ALAMANCE BL | 100 kV Line | 282.4892 | 327.0016 | 282.4892 | - | - | - | - | - | - | 116.6 | 74.7 | 74.6 | - | - | 72.8 | 70.5 | 68.2
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 107.2 | 132.5 | 114.8 | 9 | 113.1 | 101.2 | 125.2 | 107.9 | 432 | -6.9 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 32.2 | 28 | 114.8 | 102.3 | 102.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 136 | 224.7 | 112.7 | 15 | 196.8 | 122.8 | 203.1 | 100.9 | 142 | -11.8 | 2013 | 2013 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 112.7 | 75.7 | 75.6 | - | - | 73.5 | 70.9 | 61.7
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 634.7 | 922.2 | 112.2 | 231 | 822 | 671 | 986 | 120 | 10818 | 7.8 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 112.2 | 74.6 | 77.1 | - | - | 94 | 95.9 | 95.6
STUDY | SINGLE 123 | 304089 | HENDER11 | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 95.9 | 181.6 | 109.7 | 11 | 170 | 109.6 | 187.4 | 112.1 | 1070 | 2.4 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 109.7 | - | - | - | - | - | - | 67.3
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 112.4 | 223.5 | 108.5 | 3 | 201 | 116.5 | 231.1 | 112.2 | 144 | 3.7 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 108.5 | - | - | - | - | - | - | 59.7
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 243 | 636.3 | 107.3 | 1 | 590 | 243 | 644.5 | 108.7 | 48 | 1.4 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 107.3 | - | - | - | - | - | - | 52.6
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 51.6 | 51.6 | 103.2 | 2 | 50 | 51.6 | 51.6 | 103.1 | 96 | -0.1 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.2 | 105.8 | - | - | - | 105.4 | - | 105.2
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 481.8 | 819.5 | 102.9 | 2 | 796.7 | 414.2 | 704.7 | 88.5 | 49 | -14.4 | 2013 | 2021 | 8 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 118.6 | 14.9 | 102.9 | - | - | - | - | - | - | 52.4
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.3 | 110.8 | 102.3 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 3.8 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 14.8 | 13.7 | 102.3 | - | 61.2 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.3 | 110.8 | 102.3 | 1 | 108.3 | 63.6 | 114.9 | 106.1 | 48 | 3.8 | 2013 | 2013 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 14.8 | 13.7 | 102.3 | - | - | - | - | - | - | -
STUDY | SINGLE 421 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 355.6 | 551.5 | 101.1 | 3 | 539 | 318.7 | 488.1 | 89 | 48 | -12.1 | 2013 | 2021 | 8 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 101.1 | - | - | - | - | - | - | 64.1
STUDY | SINGLE 189 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 16.6 | 149.1 | 100.3 | 1 | 158 | 23.1 | 149.1 | 99.3 | 48 | -1 | 2013 | 2014 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.3 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 191.9 | 583.1 | 98.7 | 1 | 590 | 191.8 | 591.2 | 100.1 | 48 | 1.4 | 2014 | 2013 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.7 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 88.3 | 197.3 | 96.8 | 1 | 201 | 92.4 | 204.8 | 100.5 | 48 | 3.7 | 2016 | 2013 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.8 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 465.3 | 811.4 | 96.6 | 2 | 840 | 400 | 698.1 | 83.1 | 48 | -13.5 | 2016 | 2025 | 9 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 116.8 | 13.9 | 96.6 | - | 54.7 | - | - | - | 51.3 | -
STUDY | SINGLE 841 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 362.3 | 410 | 96.3 | 50 | 436.9 | 351.4 | 383.8 | 89.8 | 2223 | -6.5 | 2016 | 2020 | 4 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 15.5 | 11.6 | 96.3 | 84.6 | 83.8 | - | - | 83.1 | 80.6 | 72.1
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 385.3 | 464.2 | 95.8 | 34 | 478 | 365.4 | 440 | 89.7 | 1473 | -6.1 | 2016 | 2020 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 34.2 | 8.2 | 95.8 | 78.8 | 79.1 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 385.3 | 464.2 | 95.8 | 35 | 478 | 365.4 | 440 | 89.7 | 1520 | -6.1 | 2016 | 2020 | 4 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 34.2 | 8.2 | 95.8 | 78.8 | 79.1 | - | - | 76.7 | 76.3 | 74.8
STUDY | SINGLE 145 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304089 | HENDER115 TT115.00 | 304105 | FRANKLIN 115.00 | 1 | 304089-304105-1 | 201 | 201 | 122.1 | 177.2 | 95.2 | 8 | 201 | 110 | 174.9 | 93.4 | 96 | -1.8 | 2017 | 2018 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | - | - | - | - | - | - | 58.5
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 66.5 | 95.7 | 94 | 18 | 102 | 90.2 | 120.4 | 118.4 | 910 | 24.4 | 2017 | 2013 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94 | - | - | - | - | - | - | -
STUDY | JAX-TARAWA23 | 304530 | JACKSV11 | 304535 | NORTHWOO |  | 304530 | JACKSV115 TT115.00 | 305068 | E9-JAX NORTH115.00 | 1 | 304530-305068-1 | 220 | 220 | 93.5 | 203 | 92.1 | 3 | 220 | 92.6 | 201.2 | 91.3 | 96 | -0.8 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.1 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 146.2 | 537.6 | 91.1 | 1 | 590 | 146.7 | 546.3 | 92.6 | 48 | 1.5 | 2019 | 2018 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.1 | - | - | - | - | - | - | -
STUDY | SINGLE 627 | 304530 | JACKSV11 | 305068 | E9-JAX N | 1 | 304530 | JACKSV115 TT115.00 | 304535 | NORTHWOODS 115.00 | 1 | 304530-304535-1 | 221 | 221 | 110.1 | 198.5 | 90.8 | 5 | 221 | 109 | 196.6 | 90 | 240 | -0.8 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | - | - | - | - | - | - | 51.7
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 427.6 | 737.3 | 90.5 | 3 | 796.7 | 443.5 | 767.4 | 93.5 | 144 | 3 | 2020 | 2018 | -2 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 117.6 | 13.7 | 90.5 | - | - | - | - | - | - | -
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 105.1 | 102.3 | 2 | 102.7 | - | 98.8 | 96.2 | 96 | -6.1 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 20.9 | 20.3 | 114.8 | 102.3 | 102.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 109.9 | 107 | 1 | 102.7 | - | 103.5 | 100.8 | 48 | -6.2 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 21 | 20.4 | 119.1 | 107 | 106.9 | - | - | 104.5 | 100.4 | 89.7
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 1 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 1 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 105 | 102.3 | 52 | 102.7 | - | 98.8 | 96.2 | 1384 | -6.1 | 2013 | 2016 | 3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 20.8 | 20.3 | 114.8 | 102.3 | 102.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 109.8 | 106.9 | 26 | 102.7 | - | 103.4 | 100.7 | 692 | -6.2 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.5 | 20.9 | 20.4 | 119.1 | 107 | 106.9 | - | - | 104.5 | 100.4 | 89.7
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 52.7 | 105.4 | 702 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.2 | 105.8 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 102.6 | 99.9 | 702 | 0 | 2014 | 2014 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 114.8 | 102.3 | 102.3 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 107.3 | 104.5 | 351 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 119.1 | 107 | 106.9 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 114.1 | 90.3 | 351 | 0 | 2020 | 2020 | 0 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 83.9 | 87.1 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 20.2 | 90.8 | 351 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | 89.6 | 89.6 | 89.6 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 115.7 | 96.4 | 351 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 95.3 | 95.4 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 101 | 98.3 | 350 | 0 | 2015 | 2015 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 84.1 | 76.6 | 89.3 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 84.4 | 97.5 | 325 | 0 | 2015 | 2015 | 0 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 97.5 | 98.8 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 98.7 | 96.1 | 336 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | 82.1 | 74.5 | 87.1 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | 556.9 | - | 521.2 | 93.6 | 351 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 94.7 | 92.2 | 262 | 0 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.8 | 71 | 83.5 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.5 | 674 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 76.8 | 79.1 | 80.6 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 98.4 | 95.8 | 674 | 0 | 2016 | 2016 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 114.8 | 102.3 | 102.3 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 103.1 | 100.4 | 337 | 0 | 2013 | 2013 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 119.1 | 107 | 106.9 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 20.2 | 90.7 | 337 | 0 | 2020 | 2020 | 0 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | 89.6 | 89.6 | 89.6 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115.9 | 96.3 | 337 | 0 | 2016 | 2016 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 95.3 | 95.4 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 101.3 | 98.7 | 337 | 0 | 2014 | 2014 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 84.1 | 76.6 | 89.3 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 99 | 96.4 | 337 | 0 | 2016 | 2016 | 0 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | 82.1 | 74.5 | 87.1 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | 556.9 | - | 521.2 | 93.6 | 337 | 0 | 2018 | 2018 | 0 |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 95 | 92.5 | 337 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78.8 | 71 | 83.5 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2013 w Fayettevile and PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk13s_PEC_FPWC_Final-HrDnTRM\
2013 | Study Year |  | Thermal Screening | [6 empty] | File: | 2013FPWC_HrDnTRM.xls
2013 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2013 w Fayettevile and PEC HrDnTRM | [5 empty] | 2013 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2013 w Fayettevile and PEC HrDnTRM |  |  |  | Base 2013 w Fayettevile and PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 52.6 | 105.2 | 26 | 0 | 2013 | 2013 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 103.2 | 105.8 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2020 | 2020 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 76.8 | 79.1 | 80.6 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2018 Base-PEC Br1DnTRM
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2018 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 11 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 15 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 55 | 180.2 | 150.1 | 3 | 119 | 50.9 | 171.1 | 142.3 | 75 | -7.8 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 150.1 | - | - | - | - | - | - | -
STUDY | SINGLE 455 | 304369 | FAY EAST | 304389 | P2-FAY E | 2 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 1 | 304369-304389-1 | 150 | 150 | 106.3 | 212 | 141.3 | 4 | 150 | 113.9 | 227.1 | 151.4 | 100 | 10.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 141.3 | 71.8 | 73 | - | - | - | - | -
STUDY | SINGLE 454 | 304369 | FAY EAST | 304389 | P2-FAY E | 1 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 2 | 304369-304389-2 | 150 | 150 | 105.6 | 212 | 141.3 | 4 | 150 | 113.2 | 227.1 | 151.4 | 100 | 10.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 141.3 | - | - | - | - | - | - | -
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 70.5 | 70.5 | 140.9 | 2 | 50 | 70.4 | 70.4 | 140.9 | 50 | 0 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 146.4 | - | - | - | 105.4 | - | 105.2
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 122.3 | 150.1 | 130.4 | 13 | 113.1 | 118.2 | 145 | 125.6 | 275 | -4.8 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 38.5 | 34.7 | 130.4 | 117 | 117 | - | - | 104.5 | 100.4 | 89.7
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 130.9 | 261.6 | 126.9 | 9 | 201 | 126.2 | 251.8 | 122.1 | 125 | -4.8 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 126.9 | - | - | - | - | - | - | 59.7
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 116.4 | 143.9 | 125.6 | 12 | 113.1 | 112.3 | 139 | 120.9 | 275 | -4.7 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 43.6 | 38.8 | 125.6 | 111.9 | 111.9 | - | - | 99.9 | 95.8 | 85.6
STUDY | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 85.7 | 119.3 | 124.1 | 46 | 97 | 67.6 | 94.2 | 96.9 | 423 | -27.2 | 2018 | 2020 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 124.1 | 89 | - | - | - | - | - | 69.3
STUDY | HNDRSN-FRNKL | 304089 | HENDER11 | 304105 | FRANKLIN |  | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 112.1 | 192.6 | 118.4 | 29 | 170 | 119.4 | 193.2 | 118.1 | 845 | -0.3 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 118.4 | - | - | - | - | - | - | 67.3
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 140.4 | 232 | 118.1 | 16 | 196.8 | 131.9 | 218 | 110.2 | 213 | -7.9 | 2018 | 2018 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 118.1 | 79.3 | 79.2 | - | - | 73.5 | 70.9 | 61.7
STUDY | SINGLE 190 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 29.9 | 170.1 | 116 | 1 | 158 | 37 | 170.2 | 115.5 | 25 | -0.5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 105.7 | 233.2 | 114.7 | 3 | 201 | 101.1 | 223.9 | 110 | 25 | -4.7 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 114.7 | - | - | - | - | - | - | -
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 654.5 | 938.8 | 114.2 | 223 | 822 | 684.5 | 993.1 | 120.8 | 6093 | 6.6 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 114.2 | 76.7 | 79.7 | - | - | 94 | 95.9 | 95.6
STUDY | SINGLE 718 | 304631 | MARION23 | 305001 | E1-CHAD | 1 | 304630 | MULLINS 115.00 | 304632 | MARION115 TT115.00 | 1 | 304630-304632-1 | 179 | 179 | 131.7 | 190.7 | 110.1 | 22 | 179 | 109.2 | 160 | 89.1 | 50 | -21 | 2018 | 2026 | 8 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.1 | 74.1 | - | - | - | - | - | 57.9
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 327.4 | 643.4 | 109.7 | 4 | 590 | 259.4 | 678.6 | 115.6 | 100 | 5.9 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 109.7 | - | - | - | - | - | - | 52.6
STUDY | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 392.7 | 692.9 | 107.6 | 3 | 621.4 | 446.3 | 787 | 121.6 | 84 | 14 | 2018 | 2018 | 0 |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 107.6 | - | 73.8 | - | - | - | - | -
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 494.6 | 850.6 | 106.4 | 3 | 796.7 | 479.8 | 825.2 | 104.4 | 75 | -2 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 230.9 | 29.6 | 106.4 | - | - | - | - | - | - | -
STUDY | SINGLE 146 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304099 | E18-POCO 115.00 | 304105 | FRANKLIN 115.00 | 1 | 304099-304105-1 | 170 | 170 | 50.6 | 166.6 | 105.4 | 1 | 170 | 43.1 | 166.5 | 104.9 | 25 | -0.5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105.4 | - | - | - | - | - | - | -
STUDY | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 735 | 735 | 494.6 | 770.8 | 104.6 | 2 | 735 | 479.8 | 747.8 | 102.7 | 50 | -1.9 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA BL | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 354.3 | 619.7 | 76.8 | 151.1 | 27.8 | 104.6 | - | 68 | - | - | - | 60.9 | 53.1
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 73.5 | 103.1 | 104.6 | 21 | 102 | 97.6 | 130.8 | 129.5 | 857 | 24.9 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.6 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 416.8 | 497.2 | 103.8 | 35 | 478 | 404.2 | 486.4 | 100.2 | 849 | -3.6 | 2018 | 2018 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 67.2 | 16.2 | 103.8 | 85.9 | 86.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 416.8 | 497.2 | 103.8 | 36 | 478 | 404.2 | 486.4 | 100.2 | 874 | -3.6 | 2018 | 2018 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 67.2 | 16.2 | 103.8 | 85.9 | 86.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 481.1 | 817.7 | 102.6 | 2 | 796.7 | 438.9 | 746.7 | 93.7 | 49 | -8.9 | 2018 | 2023 | 5 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 116.8 | 14.6 | 102.6 | - | - | - | - | - | - | 52.4
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 80.6 | 207.3 | 102.3 | 1 | 201 | 76.2 | 198.1 | 97.6 | 25 | -4.7 | 2018 | 2020 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.3 | - | - | - | - | - | - | -
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.4 | 109.9 | 101.4 | 1 | 108.3 | 63.3 | 114.8 | 106 | 25 | 4.6 | 2018 | 2018 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 13.9 | 12.8 | 101.4 | - | 61.9 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.4 | 109.9 | 101.4 | 1 | 108.3 | 63.3 | 114.8 | 106 | 25 | 4.6 | 2018 | 2018 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 13.9 | 12.8 | 101.4 | - | - | - | - | - | - | -
STUDY | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 718 | 6SADLER 230.00 | 2679 | SADLE 3 1.0000 | 3 | 718-2679-3 | 553.7 | 553.7 | 326.2 | 561.2 | 101.4 | 1 | 553.7 | 377.1 | 648.2 | 117.1 | 49 | 15.7 | 2018 | 2018 | 0 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 261.1 | 460.7 | 83.2 | 100.5 | 18.2 | 101.4 | - | 66.9 | - | - | - | 57.2 | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 273.3 | 588.8 | 100.7 | 2 | 590 | 205.2 | 623.6 | 106.6 | 25 | 5.9 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.7 | - | - | - | - | - | - | -
STUDY | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 352.5 | 541.7 | 99.4 | 3 | 539 | 353.7 | 543.5 | 99.7 | 63 | 0.3 | 2019 | 2019 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.4 | - | - | - | - | - | - | 64.1
STUDY | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 718 | 6SADLER 230.00 | 2673 | SADLE 4 1.0000 | 4 | 718-2673-4 | 553.7 | 553.7 | 336.1 | 546.9 | 98.8 | 1 | 553.7 | 386.7 | 634.6 | 114.6 | 41 | 15.8 | 2019 | 2018 | -1 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 98 | 17.7 | 98.8 | - | 68.7 | - | - | - | 58.8 | -
STUDY | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 790 | SADLER 100.00 | 2673 | SADLE 4 1.0000 | 4 | 790-2673-4 | 553.7 | 553.7 | 336.1 | 546.9 | 98.8 | 1 | 553.7 | 386.7 | 634.6 | 114.6 | 41 | 15.8 | 2019 | 2018 | -1 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 98 | 17.7 | 98.8 | - | 69.1 | - | - | - | 59.2 | -
STUDY | SINGLE 843 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 371.8 | 413.1 | 98.7 | 53 | 436.9 | 379.4 | 416.1 | 101.7 | 1440 | 3 | 2019 | 2018 | -1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 18.6 | 14 | 98.7 | 88.4 | 87.6 | - | - | 83.1 | 80.6 | 72.1
STUDY | SINGLE 179 | 304137 | METHOD | 304150 | I-NCSU S | 1 | 304163 | MILB115 TT 115.00 | 304168 | YONKERS 115.00 | 1 | 304163-304168-1 | 190 | 190 | 53.6 | 178.2 | 98.5 | 4 | 190 | 57.2 | 178.2 | 98 | 100 | -0.5 | 2019 | 2020 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.5 | - | - | - | - | - | - | -
STUDY | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 37.1 | 74.8 | 97.9 | 1 | 71.2 | 37.3 | 76.8 | 101.1 | 25 | 3.2 | 2020 | 2018 | -2 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 0.4 | -1.1 | 97.9 | - | - | - | - | - | - | -
STUDY | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 355.5 | 452.3 | 96.8 | 47 | 478 | 381.2 | 479.3 | 103.2 | 1139 | 6.4 | 2021 | 2018 | -3 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 57 | 13.9 | 96.8 | 78.7 | 83.8 | - | - | 75 | 75.6 | 64.1
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 464.6 | 809.6 | 96.4 | 2 | 840 | 423.8 | 739.7 | 88.1 | 25 | -8.3 | 2021 | 2026 | 5 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 115 | 13.7 | 96.4 | - | 55.1 | - | - | - | 51.3 | -
STUDY | SINGLE 855 | 304730 | CAMDEN | 312715 | 6LUGOFF | 1 | 304723 | CAMDEN JCT 115.00 | 304726 | CAMDEN DUSTY115.00 | 1 | 304723-304726-1 | 108 | 108 | 36.4 | 93 | 96.2 | 3 | 108 | 40.4 | 93 | 96.2 | 75 | 0 | 2021 | 2021 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.2 | - | - | - | - | - | - | -
STUDY | SINGLE 213 | 304163 | MILB115 | 304168 | YONKERS | 1 | 304137 | METHOD 115.00 | 304150 | I-NCSU S 115.00 | 1 | 304137-304150-1 | 190 | 190 | 124.7 | 177.4 | 95.7 | 30 | 190 | 120.7 | 177.4 | 95.3 | 271 | -0.4 | 2021 | 2022 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.7 | - | - | - | - | - | - | 60.7
STUDY | SINGLE 48 | 304035 | SUT 1-2F | 304545 | CASTLE H | 1 | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 2 | 304035-304545-2 | 131 | 131 | 72.5 | 126.8 | 95.2 | 5 | 131 | 71.2 | 133.4 | 100.1 | 125 | 4.9 | 2022 | 2018 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.2 | - | - | - | - | - | - | -
STUDY | SINGLE 208 | 304162 | MILB230 | 304163 | MILB115 | 2 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 1 | 304162-304163-1 | 300 | 300 | 211.9 | 285 | 95 | 50 | 300 | 214.8 | 289.6 | 96.5 | 1150 | 1.5 | 2022 | 2021 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95 | 71 | - | - | - | - | - | 64.7
STUDY | MARION-MARIO | 304631 | MARION23 | 312729 | 6MARION |  | 304662 | FLORENCE 230.00 | 304663 | LATTA 230.00 | 1 | 304662-304663-1 | 507 | 507 | 209.3 | 473.9 | 94.8 | 1 | 507 | 165.8 | 384.9 | 76.3 | 25 | -18.5 | 2022 | 2036 | 14 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.8 | - | - | - | - | - | - | -
STUDY | SINGLE 846 | 304631 | MARION23 | 312729 | 6MARION | 2 | 304631 | MARION230 TT230.00 | 312729 | 6MARION 230.00 | 1 | 304631-312729-1 | 797 | 797 | 378.2 | 743.2 | 94.5 | 1 | 797 | 314.1 | 617.4 | 77.6 | 25 | -16.9 | 2022 | 2034 | 12 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.5 | - | - | - | - | - | - | -
STUDY | SINGLE 845 | 304631 | MARION23 | 312729 | 6MARION | 1 | 304631 | MARION230 TT230.00 | 312729 | 6MARION 230.00 | 2 | 304631-312729-2 | 797 | 797 | 378.2 | 743.2 | 94.5 | 1 | 797 | 314.1 | 617.4 | 77.6 | 25 | -16.9 | 2022 | 2034 | 12 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.5 | - | - | - | - | - | - | -
STUDY | SINGLE 215 | 304163 | MILB115 | 304174 | I-PERSTO | 1 | 304137 | METHOD 115.00 | 304153 | TRYON HILLS 115.00 | 1 | 304137-304153-1 | 108 | 108 | 63.1 | 97.6 | 94.5 | 10 | 108 | 61.2 | 97.6 | 94 | 174 | -0.5 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.5 | - | - | - | - | - | - | 56.5
STUDY | SINGLE 659 | 304563 | LELAND I | 304568 | DELCO | 1 | 304035 | SUT 1-2F 115.00 | 304560 | I-ASMPCS 115.00 | 1 | 304035-304560-1 | 159 | 159 | 72.8 | 151.3 | 94.2 | 2 | 159 | 77.3 | 151.2 | 94.1 | 50 | -0.1 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.2 | - | - | - | - | - | - | -
STUDY | SINGLE 718 | 304631 | MARION23 | 305001 | E1-CHAD | 1 | 304629 | NICHOLS 115.00 | 304630 | MULLINS 115.00 | 1 | 304629-304630-1 | 179 | 179 | 101.9 | 162.6 | 93.9 | 3 | 179 | 80.2 | 129.3 | 73.3 | 9 | -20.6 | 2022 | 2038 | 16 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.9 | - | - | - | - | - | - | -
STUDY | AB_STEEL_W_S | 331 | 6ALLEN | 545 | 6WOODLWN | 2 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 1 | 331-545-1 | 717 | 717 | 447.3 | 654.2 | 93.5 | 1 | 717 | 454.9 | 665.7 | 95.8 | 26 | 2.3 | 2023 | 2021 | -2 |  | 717 | 717 | 717 | STEELBERRY WH | 230 kV Line | 792.617 | 996.5466 | 792.617 | - | - | - | - | - | - | 93.5 | - | 65.6 | - | - | - | 60.6 | 58.1
STUDY | AB_STEEL_B_S | 331 | 6ALLEN | 545 | 6WOODLWN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 447.3 | 654.1 | 93.5 | 3 | 717 | 454.9 | 665.6 | 95.8 | 76 | 2.3 | 2023 | 2021 | -2 |  | 717 | 717 | 717 | STEELBERRY BL | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 444.2 | 658.7 | 93.6 | -4.6 | -0.1 | 93.5 | - | - | - | - | - | - | -
STUDY | SINGLE 240 | 304190 | WAKE 230 | 304191 | WENDELL | 1 | 304156 | ROL/SQD TAP 230.00 | 304190 | WAKE 230 230.00 | 1 | 304156-304190-1 | 797 | 797 | 566.8 | 748.8 | 93.3 | 166 | 797 | 554 | 735.6 | 91.2 | 1143 | -2.1 | 2023 | 2024 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93.3 | 70.8 | - | - | - | - | - | 57.7
STUDY | BASE CASE | 0 |  | 0 |  |  | 304615 | BARN CRK E 230.00 | 304616 | BARNARD 115.00 | 1 | 304615-304616-1 | 150 | 150 | 139.4 | 139.4 | 93 | 2 | 150 | 139.4 | 139.4 | 92.9 | 50 | -0.1 | 2023 | 2023 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 93 | 92.5 | - | - | - | 80.4 | - | 80.4
STUDY | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 790 | SADLER 100.00 | 2679 | SADLE 3 1.0000 | 3 | 790-2679-3 | 553.7 | 553.7 | 277.7 | 512.7 | 92.6 | 1 | 553.7 | 329.8 | 601.1 | 108.6 | 25 | 16 | 2023 | 2018 | -5 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 217.1 | 415.9 | 75.1 | 96.8 | 17.5 | 92.6 | - | 59 | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 223.7 | 540.7 | 92.4 | 2 | 590 | 155.8 | 575.9 | 98.4 | 25 | 6 | 2023 | 2020 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.4 | - | - | - | - | - | - | -
STUDY | SINGLE 26 | 304020 | BRUN 2 N | 304615 | BARN CRK | 1 | 304020 | BRUN 2 N 230.00 | 305005 | E1-SOUTHPORT230.00 | 1 | 304020-305005-1 | 478 | 478 | 209 | 435.4 | 92 | 2 | 478 | 170.6 | 364.8 | 76.2 | 50 | -15.8 | 2024 | 2036 | 12 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 74.9 | 105.8 | 91.9 | 15 | 116 | 99.5 | 134.5 | 113.9 | 434 | 22 | 2024 | 2018 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.9 | - | - | - | - | - | - | -
STUDY | WHITEVL-E1_C | 304600 | WHITEVIL | 305001 | E1-CHAD |  | 304663 | LATTA 230.00 | 304682 | DILLONMP TAP230.00 | 1 | 304663-304682-1 | 507 | 507 | 357 | 457.3 | 91.4 | 79 | - | - | - | - | - | - | 2024 | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.4 | 71.3 | - | - | - | - | - | 51.4
STUDY | SINGLE 878 | 304761 | I-SOUTHE | 304762 | ENKA SW | 1 | 304790 | VANDERBILT 115.00 | 304791 | W ASHEVILE 115.00 | 1 | 304790-304791-1 | 123 | 123 | 73.9 | 112 | 91.3 | 10 | 123 | 81.3 | 122.5 | 100 | 314 | 8.7 | 2024 | 2018 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | - | - | - | - | - | - | -
STUDY | RICHMOND | 337 | 8NEWPORT | 304377 | RICH500 | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1607.6 | 1782.9 | 91.2 | 243 | 1904.3 | 1702.6 | 1876.4 | 95.3 | 5939 | 4.1 | 2024 | 2022 | -2 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1478.9 | 1641.2 | 81.8 | 141.7 | 9.4 | 91.2 | 81.3 | 88.5 | - | - | 85 | 81.3 | 69.2
STUDY | SINGLE 232 | 304182 | FALLS230 | 304185 | FALLS115 | 2 | 304182 | FALLS230 TT 230.00 | 304185 | FALLS115 TT 115.00 | 1 | 304182-304185-1 | 300 | 300 | 195 | 272.3 | 90.8 | 21 | 300 | 197.6 | 275.9 | 92 | 471 | 1.2 | 2025 | 2024 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.8 | - | - | - | - | - | - | 55.8
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 73.3 | 146.6 | 650 | 41.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 146.4 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 114.5 | 111.5 | 650 | 11.6 | 2019 | 2018 | -1 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 125.6 | 111.9 | 111.9 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 119.7 | 116.6 | 325 | 12.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 130.4 | 117 | 117 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 117.2 | 92.7 | 325 | 2.4 | 2025 | 2023 | -2 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 89.8 | 93.1 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 21.8 | 97.8 | 325 | 7 | 2025 | 2020 | -5 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | - | 95.8 | 95.9 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 114.7 | 95.6 | 325 | -0.8 | 2021 | 2021 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 94.9 | 95 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 116.7 | 113.6 | 325 | 15.3 | 2020 | 2018 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.1 | 113.4 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 87 | 100.5 | 299 | 3 | 2020 | 2018 | -2 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 100.5 | 101.9 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 113.7 | 110.7 | 325 | 14.6 | 2021 | 2018 | -3 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.2 | 110.5 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | - | - | - | - | - | - | 2023 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 108.5 | 105.6 | 325 | 13.4 | 2024 | 2018 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.4 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.6 | 622 | 0.1 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | 80.4 | 81.7 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 114.3 | 111.3 | 622 | 15.5 | 2021 | 2018 | -3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 125.6 | 111.9 | 111.9 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 119.6 | 116.5 | 311 | 16.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 130.4 | 117 | 117 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 21.6 | 97.2 | 311 | 6.5 | 2025 | 2020 | -5 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | - | 95.8 | 95.9 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115 | 95.5 | 311 | -0.8 | 2021 | 2021 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 94.9 | 95 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 117.1 | 114 | 311 | 15.3 | 2019 | 2018 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.1 | 113.4 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 114.1 | 111.1 | 311 | 14.7 | 2021 | 2018 | -3 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.2 | 110.5 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | - | - | - | - | - | - | 2023 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 108.8 | 105.9 | 311 | 13.4 | 2023 | 2018 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.2 | 105.4 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2018 with PEC Br1DnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-Br1DnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018Br1DnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC Br1DnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC Br1DnTRM |  |  |  | Base 2018 with PEC Br1DnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 73.2 | 146.4 | 26 | 41.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 146.4 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 78 | 80.4 | 81.7 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet

## 2018 Base-PEC HrDnTRM
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls | [8 empty] | % Line Loading: |  | MVA (actual) | [5 empty] | CURRENT NEAR-TERM PLANNING HORIZON: 2007 ---> 2012
2018 | Implementation Year | [20 empty] | MVA (rating) * V (pu)
2008 | Annual Screening Year |  | GenMaint+LineCont
|  |  | Screening limit set at 70% or greater. | [16 empty] | % Xfmr Loading: |  | MVA (actual) |  |  | 11 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [18 empty] | MVA (rating) |  |  | 6 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 17 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BASE CASE | 0 |  | 0 |  |  | 304106 | WAKE FOREST 115.00 | 304107 | E18-WAKE EMC69.000 | 1 | 304106-304107-1 | 50 | 50 | 70.5 | 70.5 | 141 | 2 | 50 | 70.4 | 70.4 | 140.9 | 50 | -0.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 141 | 147 | - | - | - | 105.4 | - | 105.2
STUDY | SINGLE 455 | 304369 | FAY EAST | 304389 | P2-FAY E | 2 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 1 | 304369-304389-1 | 150 | 150 | 106 | 211.4 | 140.9 | 4 | 150 | 113.9 | 227.1 | 151.4 | 100 | 10.5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | 72 | 73.2 | - | - | - | - | -
STUDY | SINGLE 454 | 304369 | FAY EAST | 304389 | P2-FAY E | 1 | 304369 | FAY EAST 69.000 | 304389 | P2-FAY EAST 230.00 | 2 | 304369-304389-2 | 150 | 150 | 105.3 | 211.4 | 140.9 | 4 | 150 | 113.2 | 227.1 | 151.4 | 100 | 10.5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 140.9 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304285 | SEYMOUR JOHN115.00 | 304287 | GOLDS SW 115.00 | 1 | 304285-304287-1 | 119 | 119 | 47.9 | 165 | 137.3 | 3 | 119 | 50.9 | 171.1 | 142.3 | 75 | 5 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 137.3 | - | - | - | - | - | - | -
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 897 | GLEN RVN 100.00 | 10777 | REIDST W 100.00 | 1 | 897-10777-1 | 113.1 | 113.1 | 123.3 | 151.4 | 131.7 | 13 | 113.1 | 118.2 | 145 | 125.6 | 275 | -6.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 91.1 | 111.6 | 95.7 | 39.8 | 36 | 131.7 | 118.3 | 118.2 | - | - | 104.5 | 100.4 | 89.7
STUDY | HAWRIVERW | 790 | SADLER | 897 | GLEN RVN | 2 | 777 | REIDST B 100.00 | 897 | GLEN RVN 100.00 | 1 | 777-897-1 | 113.1 | 113.1 | 117.4 | 145.2 | 127 | 13 | 113.1 | 112.3 | 139 | 120.9 | 275 | -6.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 113.1 | 85.9 | 100.3 | 86.8 | 44.9 | 40.2 | 127 | 113.1 | 113.1 | - | - | 99.9 | 95.8 | 85.6
STUDY | ALAMANCEW | 897 | GLEN RVN | 858 | BURL T W | 1 | 857 | BURL T B 100.00 | 938 | MEBANE 100.00 | 1 | 857-938-1 | 196.8 | 196.8 | 142.4 | 235.2 | 120.2 | 19 | 196.8 | 131.9 | 218 | 110.2 | 213 | -10 | 2018 | 2018 | 0 |  | 177.9 | 196.8 | 177.9 | ALAMANCE BL | 100 kV Line | 177.8764 | 196.7552 | 177.8764 | - | - | - | - | - | - | 120.2 | 80.7 | 80.7 | - | - | 73.5 | 70.9 | 61.7
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304261 | LEE 115 SUB 115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304261-304284-1 | 201 | 201 | 123 | 245.6 | 119.1 | 3 | 201 | 126.2 | 251.8 | 122.1 | 125 | 3 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 119.1 | - | - | - | - | - | - | 59.7
STUDY | SINGLE 190 | 304145 | NEUSE | 304185 | FALLS115 | 1 | 304155 | CHEST HILLS 115.00 | 304163 | MILB115 TT 115.00 | 1 | 304155-304163-1 | 158 | 158 | 32 | 170.1 | 116.6 | 1 | 158 | 37 | 170.2 | 115.5 | 25 | -1.1 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 116.6 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304039 | SUT 3 F 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304039-304554-1 | 590 | 590 | 259.3 | 670.5 | 114 | 4 | 590 | 259.4 | 678.6 | 115.6 | 100 | 1.6 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 114 | - | - | - | - | - | - | 52.6
STUDY | SINGLE 57 | 304041 | CF 5-6 F | 304053 | CAPE 5&6 | 1 | 304024 | ROX 1-4F 230.00 | 304870 | ROX #2 24.000 | 1 | 304024-304870-1 | 822 | 822 | 646.5 | 930.8 | 113.2 | 218 | 822 | 684.5 | 993.1 | 120.8 | 6093 | 7.6 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 113.2 | 75.8 | 79.1 | - | - | 94 | 95.9 | 95.6
STUDY | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304348 | ROCKHM230 TT230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304348-304638-1 | 539 | 539 | 389.6 | 605.2 | 111.6 | 48 | 539 | 353.7 | 543.5 | 99.7 | 63 | -11.9 | 2018 | 2019 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 111.6 | 71.3 | - | - | - | - | - | 64.1
STUDY | SINGLE 753 | 304663 | LATTA | 304682 | DILLONMP | 1 | 304632 | MARION115 TT115.00 | 304654 | DILLON TAP 115.00 | 1 | 304632-304654-1 | 97 | 97 | 76.9 | 106.6 | 110.1 | 35 | 97 | 67.6 | 94.2 | 96.9 | 423 | -13.2 | 2018 | 2020 | 2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.1 | 79.4 | - | - | - | - | - | 69.3
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2512 | HIGH RCK 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2512-2513-1 | 102 | 102 | 75.3 | 105.5 | 107.3 | 21 | 102 | 97.6 | 130.8 | 129.5 | 857 | 22.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 107.3 | - | - | - | - | - | - | -
STUDY | JACOBSB | 714 | 6BELEWS | 827 | 6ERNEST1 | 1 | 714 | 6BELEWS 230.00 | 826 | 6ERNEST2 230.00 | 1 | 714-826-1 | 621.4 | 621.4 | 390.9 | 689.8 | 107.2 | 3 | 621.4 | 446.3 | 787 | 121.6 | 84 | 14.4 | 2018 | 2018 | 0 |  | 576 | 621.4 | 576 | JACOBS BL | 230 kV Line | 576.0286 | 718.2431 | 576.0286 | - | - | - | - | - | - | 107.2 | - | 73.6 | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304284 | GBORO WEIL 115.00 | 1 | 304239-304284-1 | 201 | 201 | 97.9 | 217.8 | 107 | 1 | 201 | 101.1 | 223.9 | 110 | 25 | 3 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 107 | - | - | - | - | - | - | -
STUDY | PINOCAB | 543 | 6RIVRBEN | 539 | 6LAKEWOD | 1 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 2 | 539-543-2 | 796.7 | 796.7 | 495.1 | 851.4 | 106.6 | 3 | 796.7 | 479.8 | 825.2 | 104.4 | 75 | -2.2 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA WH | 230 kV Line | 946.9017 | 1176.3571 | 946.9017 | 796.7 | 354.3 | 619.7 | 76.8 | 231.7 | 29.8 | 106.6 | - | - | - | - | - | - | -
STUDY | SINGLE 146 | 304111 | E18-WAKE | 304185 | FALLS115 | 1 | 304099 | E18-POCO 115.00 | 304105 | FRANKLIN 115.00 | 1 | 304099-304105-1 | 170 | 170 | 55.4 | 166.7 | 105.7 | 1 | 170 | 43.1 | 166.5 | 104.9 | 25 | -0.8 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105.7 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 841 | 6BOBWH B 230.00 | 1 | 714-841-1 | 478 | 478 | 420.7 | 503.1 | 105.3 | 36 | 478 | 404.2 | 486.4 | 100.2 | 849 | -5.1 | 2018 | 2018 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN BL | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 73.1 | 17.7 | 105.3 | 86.9 | 87.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 714 | 6BELEWS 230.00 | 842 | 6BOBWH W 230.00 | 2 | 714-842-2 | 478 | 478 | 420.7 | 503.1 | 105.3 | 37 | 478 | 404.2 | 486.4 | 100.2 | 874 | -5.1 | 2018 | 2018 | 0 |  | 477.96 | 477.96 | 477.96 | PLEASANT GARDEN WH | 230 kV Line | 514.2053 | 514.2053 | 514.2053 | 478 | 355 | 430 | 87.6 | 73.1 | 17.7 | 105.3 | 86.9 | 87.2 | - | - | 76.7 | 76.3 | 74.8
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304554 | 9TH ORG TAP 230.00 | 1 | 304552-304554-1 | 590 | 590 | 205.2 | 615.3 | 105 | 1 | 590 | 205.2 | 623.6 | 106.6 | 25 | 1.6 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 105 | - | - | - | - | - | - | -
STUDY | PARKWOD_TX5 | 849 | 8PARKWOD | 847 | 6PARKWOD | 5 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 6 | 847-849-6 | 796.7 | 796.7 | 491.9 | 836 | 104.9 | 2 | 796.7 | 438.9 | 746.7 | 93.7 | 49 | -11.2 | 2018 | 2023 | 5 |  | 796.7 | 796.7 | 796.7 | PARKWOOD TIE 06 | 500/230 kV Transformer | 1017.3 | 1152.7 | 1108.5 | 796.7 | 409.6 | 700.9 | 88 | 135.1 | 16.9 | 104.9 | - | - | - | - | - | - | 52.4
STUDY | AB_LAKEBK3_L | 539 | 6LAKEWOD | 543 | 6RIVRBEN | 2 | 539 | 6LAKEWOD 230.00 | 543 | 6RIVRBEN 230.00 | 1 | 539-543-1 | 735 | 735 | 495.1 | 771.4 | 104.8 | 2 | 735 | 479.8 | 747.8 | 102.7 | 50 | -2.1 | 2018 | 2018 | 0 |  | 735 | 796.7 | 735 | PINOCA BL | 230 kV Line | 916.228 | 916.228 | 916.228 | 796.7 | 354.3 | 619.7 | 76.8 | 151.7 | 28 | 104.8 | - | 68.1 | - | - | - | 60.9 | 53.1
STUDY | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304047 | WSPN115 TT 115.00 | 304406 | ST PAULS 115.00 | 1 | 304047-304406-1 | 119 | 119 | 99 | 124.1 | 104.1 | 40 | 119 | 100.5 | 125.1 | 104.5 | 892 | 0.4 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 104.1 | 83.6 | - | - | - | - | - | 67
STUDY | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 718 | 6SADLER 230.00 | 2679 | SADLE 3 1.0000 | 3 | 718-2679-3 | 553.7 | 553.7 | 327.9 | 564 | 101.9 | 1 | 553.7 | 377.1 | 648.2 | 117.1 | 49 | 15.2 | 2018 | 2018 | 0 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 261.1 | 460.7 | 83.2 | 103.3 | 18.7 | 101.9 | - | 67.4 | - | - | - | 57.2 | -
STUDY | HORSE1151002 | 101 | 3HORSESH | 3164 | HORSESH2 | 2 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 1 | 101-3164-1 | 108.3 | 108.3 | 61.4 | 109.8 | 101.4 | 1 | 108.3 | 63.3 | 114.8 | 106 | 25 | 4.6 | 2018 | 2018 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 01 | 115/100 kV Transformer | 127.8 | 137.8 | 134.5 | 108.3 | 53.4 | 96 | 88.6 | 13.8 | 12.8 | 101.4 | - | 61.9 | - | - | - | 61.1 | 54.7
STUDY | HORSE1151001 | 101 | 3HORSESH | 3164 | HORSESH2 | 1 | 101 | 3HORSESH 115.00 | 3164 | HORSESH2 100.00 | 2 | 101-3164-2 | 108.3 | 108.3 | 61.4 | 109.8 | 101.4 | 1 | 108.3 | 63.3 | 114.8 | 106 | 25 | 4.6 | 2018 | 2018 | 0 |  | 108.3 | 118.6 | 108.3 | HORSESHOE TIE 02 | 115/100 kV Transformer | 127.7 | 137.7 | 134.4 | 108.3 | 53.4 | 96 | 88.6 | 13.8 | 12.8 | 101.4 | - | - | - | - | - | - | -
STUDY | SINGLE 132 | 304099 | E18-POCO | 304105 | FRANKLIN | 1 | 304111 | E18-WAKE FOR115.00 | 304185 | FALLS115 TT 115.00 | 1 | 304111-304185-1 | 170 | 170 | 107.3 | 163.2 | 100.3 | 23 | 170 | 119.4 | 193.2 | 118.1 | 845 | 17.8 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 100.3 | - | - | - | - | - | - | 67.3
STUDY | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304360 | ELLERBE 230.00 | 304638 | WADSBOR TAP1230.00 | 1 | 304360-304638-1 | 507 | 507 | 289.4 | 499.6 | 99.3 | 1 | 507 | 255.6 | 440.9 | 86.8 | 25 | -12.5 | 2019 | 2027 | 8 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 99.3 | - | - | - | - | - | - | 50.4
STUDY | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 718 | 6SADLER 230.00 | 2673 | SADLE 4 1.0000 | 4 | 718-2673-4 | 553.7 | 553.7 | 338 | 549.7 | 99.3 | 1 | 553.7 | 386.7 | 634.6 | 114.6 | 41 | 15.3 | 2019 | 2018 | -1 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 100.8 | 18.2 | 99.3 | - | 69.2 | - | - | - | 58.8 | -
STUDY | SADLER3 | 718 | 6SADLER | 2679 | SADLE 3 | 3 | 790 | SADLER 100.00 | 2673 | SADLE 4 1.0000 | 4 | 790-2673-4 | 553.7 | 553.7 | 337.9 | 549.7 | 99.3 | 1 | 553.7 | 386.7 | 634.6 | 114.6 | 41 | 15.3 | 2019 | 2018 | -1 |  | 525.9 | 597.5 | 553.7 | SADLER TIE 04 | 230/100/44 kV Transformer | 525.9 | 602.8 | 565.6 | 553.7 | 270.2 | 448.9 | 81.1 | 100.8 | 18.2 | 99.3 | - | 69.6 | - | - | - | 59.2 | -
STUDY | SINGLE 179 | 304137 | METHOD | 304150 | I-NCSU S | 1 | 304163 | MILB115 TT 115.00 | 304168 | YONKERS 115.00 | 1 | 304163-304168-1 | 190 | 190 | 64.8 | 178.2 | 98.9 | 4 | 190 | 57.2 | 178.2 | 98 | 100 | -0.9 | 2019 | 2020 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98.9 | - | - | - | - | - | - | -
STUDY | SINGLE 843 | 304377 | RICH500 | 337 | 8NEWPORT | 1 | 333 | 6NEWPORT 230.00 | 541 | 6MORN ST 230.00 | 1 | 333-541-1 | 436.9 | 436.9 | 372.9 | 412.8 | 98.8 | 53 | 436.9 | 379.4 | 416.1 | 101.7 | 1440 | 2.9 | 2019 | 2018 | -1 |  | 436.9351 | 477.96 | 458.045 | SANDY RIDGE BL | 230 kV Line | 458.045 | 506.6376 | 458.045 | 478 | 357.4 | 394.5 | 84.7 | 18.3 | 14.1 | 98.8 | 88.7 | 88 | - | - | 83.1 | 80.6 | 72.1
STUDY | PARKWOD_TX6 | 849 | 8PARKWOD | 847 | 6PARKWOD | 6 | 847 | 6PARKWOD 230.00 | 849 | 8PARKWOD 500.00 | 5 | 847-849-5 | 840 | 840 | 475.1 | 827.6 | 98.5 | 2 | 840 | 423.8 | 739.7 | 88.1 | 25 | -10.4 | 2019 | 2026 | 7 |  | 840 | 840 | 840 | PARKWOOD TIE 05 | 500/230 kV Transformer | 840 | 840 | 840 | 840 | 395.6 | 694.6 | 82.7 | 133 | 15.8 | 98.5 | - | 56.6 | - | - | - | 51.3 | -
STUDY | SINGLE 208 | 304162 | MILB230 | 304163 | MILB115 | 2 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 1 | 304162-304163-1 | 300 | 300 | 217.3 | 294 | 98 | 47 | 300 | 214.8 | 289.6 | 96.5 | 1150 | -1.5 | 2020 | 2021 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 98 | 73.2 | - | - | - | - | - | 64.7
STUDY | WATEREEB | 416 | WATEREE | 375 | GT FALL1 | 1 | 375 | GT FALL1 100.00 | 416 | WATEREE 100.00 | 2 | 375-416-2 | 71.2 | 71.2 | 37.1 | 74.8 | 98 | 1 | 71.2 | 37.3 | 76.8 | 101.1 | 25 | 3.1 | 2020 | 2018 | -2 |  | 58.5 | 71.2 | 58.5 | WATEREE WH | 100 kV Line | 58.5416 | 71.1852 | 58.5416 | 71.2 | 51.6 | 74.4 | 99 | 0.4 | -1 | 98 | - | - | - | - | - | - | -
STUDY | SINGLE 718 | 304631 | MARION23 | 305001 | E1-CHAD | 1 | 304630 | MULLINS 115.00 | 304632 | MARION115 TT115.00 | 1 | 304630-304632-1 | 179 | 179 | 117.7 | 174.1 | 97.3 | 8 | 179 | 109.2 | 160 | 89.1 | 50 | -8.2 | 2020 | 2026 | 6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97.3 | - | - | - | - | - | - | 57.9
STUDY | FISHERB | 4 | 6CENTRAL | 104 | 6SHADYTB | 1 | 4 | 6CENTRAL 230.00 | 105 | 6SHADYTW 230.00 | 2 | 4-105-2 | 478 | 478 | 356.7 | 453.7 | 97.1 | 47 | 478 | 381.2 | 479.3 | 103.2 | 1139 | 6.1 | 2020 | 2018 | -2 |  | 458.045 | 478 | 458.045 | FISHER WH | 230 kV Line | 458.114 | 506.7139 | 458.114 | 478 | 311.4 | 395.3 | 82.9 | 58.4 | 14.2 | 97.1 | 78.9 | 84.1 | - | - | 75 | 75.6 | 64.1
STUDY | SINGLE 462 | 304378 | RICH230 | 304415 | RAEFORD | 1 | 304047 | WSPN115 TT 115.00 | 304432 | PA-LUMB#2 115.00 | 1 | 304047-304432-1 | 133 | 133 | 94.2 | 125.1 | 97 | 24 | 133 | 99.5 | 128.4 | 98.9 | 560 | 1.9 | 2020 | 2019 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 97 | 72 | - | - | - | - | - | 58.1
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304552 | WILM EAST 230.00 | 304577 | MURRAYVL 230.00 | 1 | 304552-304577-1 | 590 | 590 | 155.2 | 566.8 | 96.7 | 1 | 590 | 155.8 | 575.9 | 98.4 | 25 | 1.7 | 2021 | 2020 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.7 | - | - | - | - | - | - | -
STUDY | SINGLE 240 | 304190 | WAKE 230 | 304191 | WENDELL | 1 | 304156 | ROL/SQD TAP 230.00 | 304190 | WAKE 230 230.00 | 1 | 304156-304190-1 | 797 | 797 | 605 | 771 | 96.4 | 205 | 797 | 554 | 735.6 | 91.2 | 1143 | -5.2 | 2021 | 2024 | 3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.4 | 75.9 | - | - | - | - | - | 57.7
STUDY | SINGLE 213 | 304163 | MILB115 | 304168 | YONKERS | 1 | 304137 | METHOD 115.00 | 304150 | I-NCSU S 115.00 | 1 | 304137-304150-1 | 190 | 190 | 113.8 | 177.4 | 96.3 | 5 | 190 | 120.7 | 177.4 | 95.3 | 271 | -1 | 2021 | 2022 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.3 | - | - | - | - | - | - | 60.7
STUDY | SINGLE 855 | 304730 | CAMDEN | 312715 | 6LUGOFF | 1 | 304723 | CAMDEN JCT 115.00 | 304726 | CAMDEN DUSTY115.00 | 1 | 304723-304726-1 | 108 | 108 | 36.7 | 93 | 96.2 | 3 | 108 | 40.4 | 93 | 96.2 | 75 | 0 | 2021 | 2021 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.2 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304035 | SUT 1-2F 115.00 | 304545 | CASTLE HAYNE115.00 | 2 | 304035-304545-2 | 131 | 131 | 67.3 | 128 | 96.1 | 2 | 131 | 71.2 | 133.4 | 100.1 | 125 | 4 | 2021 | 2018 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 96.1 | - | - | - | - | - | - | -
STUDY | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304550 | CASTLE HAYNE230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304550-304564-1 | 478 | 478 | 352 | 455.9 | 95.9 | 87 | 478 | 369.3 | 477.5 | 100.6 | 2443 | 4.7 | 2021 | 2018 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.9 | 73.4 | - | - | - | - | - | 70.1
STUDY | SINGLE 215 | 304163 | MILB115 | 304174 | I-PERSTO | 1 | 304137 | METHOD 115.00 | 304153 | TRYON HILLS 115.00 | 1 | 304137-304153-1 | 108 | 108 | 56.2 | 97.6 | 95.1 | 3 | 108 | 61.2 | 97.6 | 94 | 174 | -1.1 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 95.1 | - | - | - | - | - | - | 56.5
STUDY | SINGLE 422 | 304348 | ROCKHM23 | 304361 | WESTND23 | 1 | 304360 | ELLERBE 230.00 | 304361 | WESTND230 TT230.00 | 1 | 304360-304361-1 | 507 | 507 | 265.7 | 475.8 | 94.6 | 1 | 507 | 231.1 | 417.2 | 82.1 | 25 | -12.5 | 2022 | 2031 | 9 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.6 | - | - | - | - | - | - | -
STUDY | LEE-BELFAST1 | 304030 | LEE 1-3F | 304281 | BELFAST |  | 304239 | GOLD CTY TAP115.00 | 304285 | SEYMOUR JOHN115.00 | 1 | 304239-304285-1 | 201 | 201 | 73 | 192 | 94.6 | 1 | 201 | 76.2 | 198.1 | 97.6 | 25 | 3 | 2022 | 2020 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.6 | - | - | - | - | - | - | -
STUDY | GODBEY | 836 | 8WOODLF | 850 | 8PL GRDN | 1 | 2511 | BADIN 100.00 | 2513 | TUCKERTN 100.00 | 1 | 2511-2513-1 | 116 | 116 | 76.8 | 108.4 | 94.3 | 18 | 116 | 99.5 | 134.5 | 113.9 | 434 | 19.6 | 2022 | 2018 | -4 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.3 | - | - | - | - | - | - | -
STUDY | SINGLE 659 | 304563 | LELAND I | 304568 | DELCO | 1 | 304035 | SUT 1-2F 115.00 | 304560 | I-ASMPCS 115.00 | 1 | 304035-304560-1 | 159 | 159 | 73.1 | 151.2 | 94.1 | 2 | 159 | 77.3 | 151.2 | 94.1 | 50 | 0 | 2022 | 2022 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 94.1 | - | - | - | - | - | - | -
STUDY | AB_STEEL_W_S | 331 | 6ALLEN | 545 | 6WOODLWN | 2 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 1 | 331-545-1 | 717 | 717 | 447.5 | 654.5 | 93.6 | 1 | 717 | 454.9 | 665.7 | 95.8 | 26 | 2.2 | 2023 | 2021 | -2 |  | 717 | 717 | 717 | STEELBERRY WH | 230 kV Line | 792.617 | 996.5466 | 792.617 | - | - | - | - | - | - | 93.6 | - | 65.7 | - | - | - | 60.6 | 58.1
STUDY | AB_STEEL_B_S | 331 | 6ALLEN | 545 | 6WOODLWN | 1 | 331 | 6ALLEN 230.00 | 545 | 6WOODLWN 230.00 | 2 | 331-545-2 | 717 | 717 | 447.5 | 654.4 | 93.6 | 3 | 717 | 454.9 | 665.6 | 95.8 | 76 | 2.2 | 2023 | 2021 | -2 |  | 717 | 717 | 717 | STEELBERRY BL | 230 kV Line | 792.617 | 996.5466 | 792.617 | 717 | 444.2 | 658.7 | 93.6 | -4.3 | 0 | 93.6 | - | - | - | - | - | - | -
STUDY | RICHMOND | 337 | 8NEWPORT | 304377 | RICH500 | 1 | 836 | 8WOODLF 500.00 | 850 | 8PL GRDN 500.00 | 1 | 836-850-1 | 1904.3 | 1904.3 | 1644.3 | 1811.4 | 93.2 | 239 | 1904.3 | 1702.6 | 1876.4 | 95.3 | 5939 | 2.1 | 2023 | 2022 | -1 |  | 1904.3 | 1904.3 | 1904.3 | GODBEY | 500 kV Line | 3739.388 | 4717.968 | 3739.388 | 1904.3 | 1478.9 | 1641.2 | 81.8 | 170.2 | 11.4 | 93.2 | 83.6 | 90.9 | - | - | 85 | 81.3 | 69.2
STUDY | SADLER4 | 718 | 6SADLER | 2673 | SADLE 4 | 4 | 790 | SADLER 100.00 | 2679 | SADLE 3 1.0000 | 3 | 790-2679-3 | 553.7 | 553.7 | 279.2 | 515.4 | 93.1 | 1 | 553.7 | 329.8 | 601.1 | 108.6 | 25 | 15.5 | 2023 | 2018 | -5 |  | 530.3 | 555.5 | 553.7 | SADLER TIE 03 | 230/100/44 kV Transformer | 530.3 | 555.5 | 555.5 | 553.7 | 217.1 | 415.9 | 75.1 | 99.5 | 18 | 93.1 | - | 59.3 | - | - | - | - | -
STUDY | BASE CASE | 0 |  | 0 |  |  | 304615 | BARN CRK E 230.00 | 304616 | BARNARD 115.00 | 1 | 304615-304616-1 | 150 | 150 | 139.4 | 139.4 | 92.9 | 2 | 150 | 139.4 | 139.4 | 92.9 | 50 | 0 | 2023 | 2023 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.9 | 91.6 | - | - | - | 80.4 | - | 80.4
STUDY | SINGLE 252 | 304196 | ERWIN | 304389 | P2-FAY E | 1 | 304408 | BEARD 115.00 | 304427 | SLOC TAP 115.00 | 1 | 304408-304427-1 | 119 | 119 | 80.2 | 107.8 | 92.2 | 18 | 119 | 73.4 | 99.6 | 84.5 | 80 | -7.7 | 2024 | 2029 | 5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 92.2 | - | - | - | - | - | - | 59.9
STUDY | SINGLE 207 | 304162 | MILB230 | 304163 | MILB115 | 1 | 304162 | MILB230 TT 230.00 | 304163 | MILB115 TT 115.00 | 2 | 304162-304163-2 | 300 | 300 | 203.8 | 275.3 | 91.8 | 30 | 300 | 202.4 | 271.5 | 90.5 | 399 | -1.3 | 2024 | 2025 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.8 | - | - | - | - | - | - | -
STUDY | SINGLE 878 | 304761 | I-SOUTHE | 304762 | ENKA SW | 1 | 304790 | VANDERBILT 115.00 | 304791 | W ASHEVILE 115.00 | 1 | 304790-304791-1 | 123 | 123 | 74.2 | 112.5 | 91.7 | 10 | 123 | 81.3 | 122.5 | 100 | 314 | 8.3 | 2024 | 2018 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.7 | - | - | - | - | - | - | -
STUDY | BR1-BARCK230 | 304022 | BRUN 1 N | 304614 | BARN CRK |  | 304550 | CASTLE HAYNE230.00 | 304577 | MURRAYVL 230.00 | 1 | 304550-304577-1 | 590 | 590 | 122.4 | 535.6 | 91.3 | 1 | 590 | 122.9 | 545 | 93.1 | 25 | 1.8 | 2024 | 2023 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 91.3 | - | - | - | - | - | - | -
STUDY | CPL6 | 304183 | WAKE 500 | 304391 | CUMB500 | 1 | 304196 | ERWIN 230.00 | 304389 | P2-FAY EAST 230.00 | 1 | 304196-304389-1 | 478 | 478 | 324 | 426 | 90.9 | 94 | 478 | 309.3 | 418.2 | 88.3 | 147 | -2.6 | 2025 | 2026 | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.9 | - | - | - | - | - | - | 55.7
STUDY | SINGLE 64 | 304046 | WSPN230 | 304387 | P1-FAY | 1 | 304406 | ST PAULS 115.00 | 304412 | FLOR DUP SW 115.00 | 1 | 304406-304412-1 | 119 | 119 | 81.2 | 104.9 | 90.4 | 23 | 119 | 82.8 | 106.2 | 90.9 | 594 | 0.5 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90.4 | - | - | - | - | - | - | 54.9
STUDY | SINGLE 30 | 304022 | BRUN 1 N | 304354 | I-ROCKY | 1 | 304556 | TOPSAIL TAP 230.00 | 304564 | SCOTT TAP 230.00 | 1 | 304556-304564-1 | 478 | 478 | 323 | 426.4 | 90 | 25 | 478 | 340.3 | 447.9 | 94.8 | 1571 | 4.8 | 2025 | 2022 | -3 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 90 | - | - | - | - | - | - | 65.2
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint
|  |  | Screening limit set at 70% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 2 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 116.2 | 113.1 | 2 | 102.7 | - | 110.6 | 107.7 | 50 | -5.4 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 84.2 | 82 | 32 | 31.1 | 127 | 113.1 | 113.1 | - | - | 99.9 | 95.8 | 85.6
STUDY | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 121.5 | 118.3 | 1 | 102.7 | - | 115.8 | 112.8 | 25 | -5.5 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.9 | 86.6 | 32.6 | 31.7 | 131.7 | 118.3 | 118.2 | - | - | 104.5 | 100.4 | 89.7
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year
2008 | Annual Screening Year |  | GenMaint+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 0 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 0 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaint+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls | [26 empty] | -- | [5 empty] | - | - | - | - | - | 0 | -
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+LineCont
|  |  | Screening limit set at 70% or greater. | [21 empty] | 21 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for transformers contingencies. 12 Hour rate for line contingencies. | [21 empty] | 15 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 36 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+LineCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | GenMaintVRS
|  |  | Screening limit set at 70% or greater. | [21 empty] | 6 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | Cont rate for generator maintenance. | [21 empty] | 5 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 11 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | GenMaintVRS
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Voltage | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
ALL4GMHAR1VRS | - | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.7 | 105.4 | 702 | 50 | - | 73.3 | 146.6 | 650 | 41.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 141 | 147 | - | - | - | 105.4 | - | 105.2
OCO1GMROX4VRS | - | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 102.6 | 99.9 | 702 | 102.7 | - | 114.5 | 111.5 | 650 | 11.6 | 2019 | 2018 | -1 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 88.6 | 86.3 | 14 | 13.6 | 127 | 113.1 | 113.1 | - | - | 99.9 | 95.8 | 85.6
OCO1GMROX4VRS | - | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 107.3 | 104.5 | 351 | 102.7 | - | 119.7 | 116.6 | 325 | 12.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 93.4 | 90.9 | 13.9 | 13.6 | 131.7 | 118.3 | 118.2 | - | - | 104.5 | 100.4 | 89.7
OCO1GMASH1VRS | - | - | - | - | - | - | 269 | LAWSONFK | 290 | PINEWOOD | 1 | 269-290-1 | 126.4 | 126.4 | - | 114.1 | 90.3 | 351 | 126.4 | - | 117.2 | 92.7 | 325 | 2.4 | 2025 | 2023 | -2 |  | 126.4 | 139.4 | 126.4 | PINEWOOD | 100 kV Line | 126.436 | 139.426 | 126.436 | 126.4 | - | 98.8 | 78.1 | 15.3 | 12.2 | - | 89.7 | 93 | - | - | 90.3 | 89.4 | 80.6
BUG1GMASH1VRS | - | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.8 | 351 | 22.2 | - | 21.8 | 97.8 | 325 | 7 | 2025 | 2020 | -5 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.3 | - | 95.9 | 95.9 | - | - | 90.8 | 90.7 | 74.9
BEL1GMAMW1VRS | - | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120 | 120 | - | 115.7 | 96.4 | 351 | 120 | - | 114.7 | 95.6 | 325 | -0.8 | 2021 | 2021 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120 | - | 109.8 | 91.5 | 5.9 | 4.9 | - | 94.5 | 94.6 | - | - | 96.4 | 96.3 | 89.1
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101 | 98.3 | 350 | 102.7 | - | 116.7 | 113.6 | 325 | 15.3 | 2020 | 2018 | -2 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.6 | 113.9 | - | - | 98.3 | 98.7 | 78.7
BUG1GMVCS1VRS | - | - | - | - | - | - | 737 | DAN RIV | 810 | WENTWRTH | 1 | 737-810-1 | 86.6 | 86.6 | - | 84.4 | 97.5 | 325 | 86.6 | - | 87 | 100.5 | 299 | 3 | 2020 | 2018 | -2 |  | 86.6 | 94.7 | 86.6 | DAN RIVER WH | 100 kV Line | 102.7076 | 113.1 | 102.7076 | - | - | - | - | - | - | - | 100.8 | 102.1 | - | - | 97.5 | 89.3 | 81.2
RIV7GMHAR1VRS | - | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 98.7 | 96.1 | 336 | 102.7 | - | 113.7 | 110.7 | 325 | 14.6 | 2021 | 2018 | -3 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.7 | 111 | - | - | 96.1 | 96.4 | 76.6
ALL4GMAMW1VRS | - | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 351 | - | - | - | - | - | - | 2023 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
RIV7GMHAR1VRS | - | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 94.7 | 92.2 | 262 | 102.7 | - | 108.5 | 105.6 | 325 | 13.4 | 2024 | 2018 | -6 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.6 | 105.9 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+GenCont
|  |  | Screening limit set at 50% or greater. | [21 empty] | 5 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | LTE rate for generator contingencies. | [21 empty] | 4 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 9 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+GenCont
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | MCG2 | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.5 | 674 | 31 | - | 28.1 | 90.6 | 622 | 0.1 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.7 | 80.4 | 81.8 | - | - | 89.1 | 90.5 | 90.8
STUDY | THRP | - | - | - | - | - | 777 | REIDST B | 897 | GLEN RVN | 1 | 777-897-1 | 102.7 | 102.7 | - | 98.4 | 95.8 | 674 | 102.7 | - | 114.3 | 111.3 | 622 | 15.5 | 2021 | 2018 | -3 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 81.8 | 79.6 | 16.6 | 16.2 | 127 | 113.1 | 113.1 | - | - | 99.9 | 95.8 | 85.6
STUDY | THRP | - | - | - | - | - | 897 | GLEN RVN | 10777 | REIDST W | 1 | 897-10777-1 | 102.7 | 102.7 | - | 103.1 | 100.4 | 337 | 102.7 | - | 119.6 | 116.5 | 311 | 16.1 | 2018 | 2018 | 0 |  | 102.7076 | 113.1 | 102.7076 | ELON | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | 102.7 | - | 86.5 | 84.3 | 16.6 | 16.1 | 131.7 | 118.3 | 118.2 | - | - | 104.5 | 100.4 | 89.7
STUDY | THRP | - | - | - | - | - | 1411 | 1BRDRV 4 | 1479 | 1INMAN | 1 | 1411-1479-1 | 22.2 | 22.2 | - | 20.2 | 90.7 | 337 | 22.2 | - | 21.6 | 97.2 | 311 | 6.5 | 2025 | 2020 | -5 |  | 22.2504 | 26.8 | 22.2504 | CAMPOBELLO B | 44 kV Line | 0 | 0 | 0 | 22.2 | - | 17.9 | 80.5 | 2.3 | 10.2 | - | 95.9 | 95.9 | - | - | 90.8 | 90.7 | 74.9
STUDY | BEL1 | - | - | - | - | - | 875 | DURHAM | 941 | DACIANTB | 1 | 875-941-1 | 120.4 | 120.4 | - | 115.9 | 96.3 | 337 | 120.4 | - | 115 | 95.5 | 311 | -0.8 | 2021 | 2021 | 0 |  | 120 | 129.9 | 120.4 | DACIAN AVE | 100 kV Line | 183.9384 | 228.1044 | 183.9384 | 120.4 | - | 110.2 | 91.5 | 5.7 | 4.8 | - | 94.5 | 94.6 | - | - | 96.4 | 96.3 | 89.1
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 10680 | BFORDRET | 1 | 611-10680-1 | 102.7 | 102.7 | - | 101.3 | 98.7 | 337 | 102.7 | - | 117.1 | 114 | 311 | 15.3 | 2019 | 2018 | -1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 110.6 | 113.9 | - | - | 98.3 | 98.7 | 78.7
STUDY | RIV7 | - | - | - | - | - | 611 | LAKEWOOD | 652 | RIVERBEN | 2 | 611-652-2 | 102.7 | 102.7 | - | 99 | 96.4 | 337 | 102.7 | - | 114.1 | 111.1 | 311 | 14.7 | 2021 | 2018 | -3 |  | 102.7 | 110.8 | 102.7 | LONG CREEK WH | 100 kV Line | 102.7076 | 113.0996 | 102.7076 | - | - | - | - | - | - | - | 107.7 | 111 | - | - | 96.1 | 96.4 | 76.6
STUDY | THRP | - | - | - | - | - | 265 | 6RIVERVW | 10316 | 6BRECBL2 | 2 | 265-10316-2 | 556.9 | 556.9 | - | 521.2 | 93.6 | 337 | - | - | - | - | - | - | 2023 | - | - |  | 556.9 | 617.5 | 556.9 | BROAD RIVER EC BUS LINE 2 | 230 kV Bus Line | 556.9 | 617.5 | 556.9 | - | - | - | - | - | - | - | - | - | - | - | 93.6 | 93.6 | 84.4
STUDY | RIV7 | - | - | - | - | - | 652 | RIVERBEN | 10680 | BFORDRET | 1 | 652-10680-1 | 102.7 | 102.7 | - | 95 | 92.5 | 337 | 102.7 | - | 108.8 | 105.9 | 311 | 13.4 | 2023 | 2018 | -5 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 102.6 | 105.9 | - | - | 92.2 | 92.5 | 73.1
1.6 | % Yearly Load Growth |  | Base 2018 with PEC HrDnTRM | [6 empty] | Directory: | P:\NC PWG\2008 Study\Thermal Screening results\PECTRM\duk18s_PEC_Final-HrDnTRM\
2018 | Study Year |  | Thermal Screening | [6 empty] | File: | 2018HrDnTRM.xls
2018 | Implementation Year |  |  |  |  | Don't do VRS for TRM cases
2008 | Annual Screening Year |  | StudyVRS+Whitewater
|  |  | Screening limit set at 50% or greater. | [21 empty] | 2 | > 5% worse | [16 empty] | Worst-Case Post-Cont Percent Loading
|  |  | 12 Hour rate for Whitewater line contingency. | [21 empty] | 0 | Not in original screening | [16 empty] | Post-Cont Percent Loading Exceeds
[25 empty] | 2 | Total over screen |  |  | Facility Ratings |  |  |  |  | Major Component Ratings | [8 empty] | StudyVRS+Whitewater
|  | Outaged Branch |  |  |  |  | Overloaded Branch |  |  |  |  | Branch | Base 2018 with PEC HrDnTRM | [5 empty] | 2018 Summer Screening (2008 NCPWG Study Base Case) | [5 empty] | Over | Over | Accel. |  | Summer Ratings |  |  | Overloaded Branch |  | Summer Ratings |  |  | 2008 Summer Screening |  |  |  | Difference |  | Base 2018 with PEC HrDnTRM |  |  |  | Base 2018 with PEC HrDnTRM
Case Name | Contingency | From Bus | Name | To Bus | Name | Circuit | From Bus | Name | To Bus | Name | Circuit | Identifier | New Rating | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | Rating | Pre-Cont | Post-Cont | Percent | Occurrences | % Diff. | Study | Base | Years | Comments | Cont | 12 Hour | LTE | Name | Branch Type | Cont | 12 Hour | LTE | Rating | Pre-Cont | Post-Cont | Percent | Post-Cont | Percent | GmLc | Gm | GmGc | GmWh | VRSLc | GmVRS | VRSGc | VRSWh
STUDY | BADX | - | - | - | - | - | 304106 | WAKE FOR | 304107 | E18-WAKE | 1 | 304106-304107-1 | 50 | 50 | - | 52.6 | 105.2 | 26 | 50 | - | 73.2 | 146.4 | 26 | 41.2 | 2018 | 2018 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 141 | 147 | - | - | - | 105.4 | - | 105.2
STUDY | BADX | - | - | - | - | - | 304004 | TIL 1-4H | 304891 | TILL #4 | 1 | 304004-304891-1 | 31 | 31 | - | 28.1 | 90.8 | 26 | 31 | - | 28.1 | 90.8 | 26 | 0 | 2025 | 2025 | 0 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | 77.7 | 80.4 | 81.8 | - | - | 89.1 | 90.5 | 90.8
Populate Summary Worksheet