NC Transmission Planning Collaborative

Planning Work Group (PWG)

Meeting Minutes

July 9, 2008

Conference Call

10:00 AM – 11:15 AM Eastern

Attendees:

Denise Roeder						ElectriCities

Laura Lee 							Duke Energy

Bob Pierce							Duke Energy

Bob Beadle							NCEMC

James Manning						NCEMC

Mark Byrd							Progress Energy

Lee Adams							Progress Energy

Joey West							Progress Energy

Rick Anderson						Fayetteville PWC

Rich Wodyka							Accenture

Pam Kozlowski						Accenture

Frank Gaffney						R.W. Beck

- ADMINISTRATIVE

- Bob Beadle called the meeting to order at 10:01 AM.

- Pam Kozlowski reported that she had emailed a draft NCTPC update on major projects out to the group for review, with the intent of finalizing it for an update at the August OSC meeting. Frank Gaffney asked whether it would make sense to separate the “underway” status into “under construction” or “under design”. Lee Adams responded that Progress Energy doesn’t typically get updates from the project engineering group and tracking this information down on an ongoing basis would require some time and effort. The group agreed to delete the Duke Reconductor London Creek 230kV lines project from the list as it was listed as deferred for both the 2007 Supplemental Plan and the July 2008 Update. Pam clarified that the update is generally done (3) times a year.

- Pam also provided an updated 2008 work plan. The TAG meeting has been moved back to September (scheduled back to back with the OSC meeting), and TAG meeting materials would need to be put together at the August meeting. Bob Beadle agreed to email a draft agenda for the TAG meeting in advance of the August PWG meeting.

- Pam also emailed a revised TAG Voting Member Confidentiality Agreement with a suggested paragraph added to clarify what steps TAG members would need to take before being given access to confidential information.

- Bob Beadle asked if everyone had reviewed the June PWG draft meeting minutes. The group concluded that an additional clarification should be added to describe the additional screening of the Yadkin OPG.

ACTION ITEMS: Bob Beadle will request the OSC at its August meeting to provide direction for future updates on whether the “underway” status on the major projects table provides the appropriate level of detail. Bob Beadle will add a short summary of the Yadkin screening to the June minutes. When completed, Pam will post the meeting minutes to the PWG site. Bob will also draft a proposed agenda for the September TAG meeting and email it to the PWG in advance of the next PWG meeting. PWG members will also review the workplan, confidentiality agreement, and major project update and advise Pam of any other requested changes.

- TRANSFORMER STUDY UPDATE

- Joey West reported that Progress Energy has been in contact with the internal employee about speeding up the study, but no results or conclusions are available yet.

- Joey also indicated that he has not reached any conclusions yet on the Falls/Wake Forest area study, but noticed that the NCEMC load forecast had increased by 20 MVA from last year to this year. Bob Beadle responded that this area has had some very rapid growth of late.

ACTION ITEMS: Bob Beadle to work with Joey West to provide additional load information to help with the Falls/Wake Forest area study.

- 2008 STUDY

- Joey West reported that he had posted the results of the 2018 wind sensitivity case. No new thermal overloads were uncovered by the runs. Western area losses went from 12 MW to roughly 6 MW due to the effect of the dispersed wind generation locations. Eastern area loadings were positively impacted by the dispersed wind generation locations and eastern area losses were reduced by 25 MW. Bob Pierce reported similar results for the Duke wind sensitivity case. Bob Beadle agreed to put together a summary paragraph describing the results of the wind sensitivity for the August PWG meeting, with the intent to use it as the basis for inclusion in the 2008 study report.

- Bob Pierce mentioned that he was concerned about not including paired elements at the 230kV level between Duke and Progress Energy, given the numerous 230kV interties between Duke and Progress Energy in the Raleigh area and suggested running a paired contingency file for the N-2 contingencies that covered 230kV as well as 500kV elements.

- Laura Lee clarified that the Duke screenings had a thermal loading cutoff of 70% for the case results. The contingencies were screened at 85% as some items at this level can have an effect on various scenarios. The final report will have thermal loadings truncated at 90% for contingencies. Bob Pierce added that a project may be initiated for the Norman 230kV line (McGuire-Riverbend) before 2014 as it has been showing up in conjunction with operational issues.

ACTION ITEMS: Joey West and Bob Pierce (Brian Moss) to work on developing a paired contingency file for 230kV as well as 500kV elements. Bob Beadle will complete a summary of wind sensitivity results for the next PWG meeting.

- South Carolina Regional Transmission Planning (SCRTP) Meeting and Southeast Inter-Regional Participation Process (SIRPP) Meeting Study Requests

- Bob Beadle reported that the study requests for the SCRTP submitted on behalf of the NCTPC have been accepted. Bob also confirmed that the study requests submitted on behalf of the NCTPC to the SIRPP have been received. He will attend the 7/10/08 meeting, and advise the PWG of the studies accepted by the SIRPP.

ACTION ITEM: Bob Beadle will attend the 7/10/08 SIRPP meeting and advise the PWG of the studies selected.

- OTHER ITEMS

- Frank Gaffney requested a change of the August meeting date to 8/21 (same time and location), due to a scheduling conflict. PWG members reviewed calendars and agreed to the change, pending a check by the Progress Energy members.

- Joey West indicated that a PEC western area study update should be available for the August PWG meeting and should be provided by Duke. Bob/Pam agreed to add it to the agenda.

- Bob Beadle adjourned the meeting at approximately 11:15 AM.