NC Transmission Planning Collaborative

Planning Work Group (PWG)

Meeting Minutes

June 8, 2009

Greensboro, NC – Duke Operations Center

10:00 AM – 3:00 PM Eastern

Attendees:

Denise Roeder						ElectriCities

Laura Lee							Duke Energy

Bob Pierce							Duke Energy

Orvane Piper							Duke Energy

Bob Beadle							NCEMC

James Manning						NCEMC

Lee Adams							Progress Energy

Joey West							Progress Energy

Rich Wodyka							Accenture

- ADMINISTRATIVE

- Bob Beadle started the meeting at 10:03 AM.

- The May 13, 2009 PWG meeting minutes were approved with one minor grammatical change.

- Bob Beadle and Rich Wodyka updated the group on the developments at the previous OSC conference call on May 19th.

- 2009 STUDY-BASE CASE RESULTS REVIEW

- James Manning asked what was finally concluded regarding the interchange tables. Joey West responded that the goal should be to make sure all transmission requests are included. Rich Wodyka added that it is intended to reflect the best guess at the time—the study input needs to be finalized at some point prior to running the base cases. Bob Pierce indicated that what happened this time was that they built the models and had changes come in a few weeks later. The best approach might be to build the base case and then run a cross check on the most current information Duke and Progress have regarding requests. Rich added that if the changes are substantial enough, a sensitivity analysis could also be done.

- Joey West reported on the status of the Progress Energy base case results, adding that the loadings were up slightly but the contingencies were all previously identified issues and either had an operating procedure identified or an upgrade project already planned. Joey also mentioned that he had used a 2% growth assumption in the loads.

- Joey West mentioned that the PEC western area load was 100-120 MW less in summer than winter, making the winter case much worse due to load even though the equipment ratings are typically higher.

- Bob Pierce mentioned that their analysis has indicated that the hydro units at some sites don’t quite operate in real time the way they had thought, sometimes letting water out in the morning for kayakers and then are not available for the afternoon peak hours.

- Joey West asked why the Pisgah 115/100kV transformers were limited to a rating of 104 MW. Bob Pierce responded that it was established a long time ago and was not set by the relaying (Duke owns bank 9, PEC owns bank 10). Bob indicated that a CT on the 100kV side limits the parallel rating to 208MW (104 each).

- Joey reported that Progress Energy has a project to replace all of the ancillary equipment at the Pisgah-Asheville 230kV tie in 2010, which should take care of the 230kV contingency from their side.

- Joey West agreed to follow up on how the ECC would import power/serve load if both coal units were down.

ACTION ITEM: Joey West to check with PEC Operations on Asheville area procedures.

- Joey West mentioned that Progress Energy is interested in raising the 230kV winter ratings at the Pisgah-Asheville tie. Bob Pierce responded that Duke currently has a limit of 1200A (CT). The conductor rating is 534 MW, and the equipment also needs to be checked. Bob confirmed that the summer limit is the conductor.

- Joey West reported that most of the summer 2019 base case contingencies were normal loading issues, adding that operating procedures were available for all overloads above 100%. Joey added that Progress Energy doesn’t own the GE-Florence 115kV tap line showing up as an overload.

- Laura Lee reported that Duke has had some problems running the cases. The 2019 summer results are done, but haven’t been compiled yet. Joey West added that he had run across some issues with mismodeled items and issues with remote buses in the SIRPP models.

- Laura mentioned that the 2014 base case results did not produce any new contingencies that had not already been previously identified. A 1.6% growth rate was used, and the generation upgrades at Buck and Dan River were included in the base cases.

- Bob Pierce asked whether further analysis is needed regarding the Yadkin generation, such as looking at it during peak conditions. Since the generation sales are all on a short term non-firm basis, the models are not really reflecting the real time operation. Bob agreed to do some further investigation, and suggested bringing the issue to the OSC.

- AUGUST TAG PRESENTATION

- Bob Beadle went over the proposed August TAG meeting topics, mainly an update on the status of the 2009 study, and update of the NCTPC transmission project plan, and regional study update. Rich Wodyka added that the TAG update of the collaborative plan projects is now a FERC requirement.

ACTION ITEM: Bob Beadle to start draft framework for the TAG presentation.

- OTHER ITEMS

- Bob Beadle and Rich Wodyka confirmed that the 2009 study process is still on schedule. All suggested a conference call for the originally scheduled PWG meeting date of July 9th to discuss how the case runs are going.

ACTION ITEM: Bob Beadle agreed to set up a conference call for July 9th, at 10am.

- Bob Beadle adjourned the meeting at approximately 2:00 PM.