NC Transmission Planning Collaborative

Planning Work Group (PWG)

Meeting Minutes

February 4, 2010

Conference Call

10:00 AM – 12:00 PM Eastern

Attendees:

Denise Roeder						ElectriCities

Bob Pierce							Duke Energy

Orvane Piper							Duke Energy

Bob Beadle							NCEMC

James Manning						NCEMC

Mark Byrd							Progress Energy

Lee Adams							Progress Energy

Kai Zai							Progress Energy

Rich Wodyka    						Accenture

Rick Anderson						FPWC

- ADMINISTRATIVE

- The January 7, 2010 PWG meeting minutes were approved without modification.

- Rich Wodyka updated the group on the 1/19/10 OSC meeting and feedback from the TAG.

- The request for TAG input on Enhanced Transmission Access scenarios has been sent out.

- The 2010 Work Plan was reviewed.  Any comments should be sent to Rich.

- The action item status was reviewed.

- 2010 STUDY SCOPE

- No feedback has been received from the TAG on the 2010 study scope and the OSC has approved it.

- A Duke University graduate student contacted Rich about possible participation in the study.  Bob Pierce will contact the student to discuss his intentions.

- PEC and Duke are now at the point in their internal model development that interchange can be coordinated for the NCTPC study.  In all cases, wind resources will be allocated between Duke and Progress at a 60/40 % ratio respectively.  This is based on load ratio share at peak.  There have been no recent changes in LSE resources.

- Mark Byrd presented PEC’s strawman for connecting the offshore wind resources to the transmission system.  Offshore collector stations are proposed near Bayboro, Morehead City and Southport.  Off peak, Bayboro would receive 1125 MW, Morehead City 1500 MW, and Southport 375 MW for a net of 3000 MW.  New 230 kV and 500 kV lines and stations are proposed to tie these stations to the existing CPLE system.  Mark explained that the strawman did not allow for import of all 3000 MW under N-1 transmission system conditions.  The group agreed that for the purpose of this study the new transmission added to the model for integration of the wind energy should meet N-1 criteria.  The need to evaluate local area generation dispatch impact on the lines was discussed.  PEC will evaluate the strawman to develop changes so that N-1 criteria are met.  All PWG members are asked to comment on the PEC proposal.

ACTION ITEM:  Bob Pierce to contact Duke University graduate student to discuss his intentions.

ACTION ITEM Lee Adams and Orvane Piper to coordinate interchange.

ACTION ITEM:  PEC will evaluate the strawman to develop changes so that N-1 criteria are met.

ACTION ITEM:  All PWG members are asked to comment on the PEC proposal.

- OTHER ITEMS

- Discussed NERC Reliability Standards CIP-002-4 which is out for informal comment to assist the SDT and TPL-001-0 which is up for ballot.

- Developed topics relating to the NCTPC interface with PJM for discussion during the next joint meeting tentatively scheduled for 3/11/10 in Greensboro.

- Next PWG meeting is scheduled for 3/10/10, 10 AM at the Greensboro Fairfax Operating Center.  Possible that the meeting may be a conference call based on the actual agenda.

ACTION ITEM LOG

| Action Item | Responsibility | Status |
| --- | --- | --- |
| Supply contact information for Kai to the PWG. | Mark Byrd | Complete |
| Supply contact information for Orvane to the PWG. | Bob Pierce | Complete |
| Develop an exact list of unscrubbed generation to be retired. | Bob Pierce | Complete |
| Develop an exact list of unscrubbed generation to be retired. | Lee Adams | Complete |
| Provide 2015S peak load information for determining load ratio share allocation of wind energy to each area. | Bob Pierce | Complete |
| Provide 2015S peak load information for determining load ratio share allocation of wind energy to each area. | Lee Adams | Complete |
| Determine time of day for maximum capacity factor for off shore wind. | Orvane Piper | Complete |
| Determine off peak load level to be studied based on information from Orvane on time of day for maximum off shore wind capacity factor. | Bob Pierce |  |
| Determine off peak load level to be studied based on information from Orvane on time of day for maximum off shore wind capacity factor. | Lee Adams |  |
| Develop a strawman representing the infrastructure associated with bringing the energy onshore. | Mark Byrd | Complete |
| Review the revised 2010 Study Scope document and submit any additional revisions by 1/11/10. | All PWG members | Complete |
| Contact Duke University graduate student to discuss 2010 Study. | Bob Pierce |  |
| Coordinate interchange for models. | Lee Adams Orvane Piper |  |
| PEC will evaluate the strawman to develop changes so that N-1 criteria are met. | Mark Byrd |  |
| Comment on the PEC strawman proposal. | All PWG members |  |