NC Transmission Planning Collaborative

Planning Work Group (PWG)

Meeting Minutes

Fairfax Ops Center

July 12, 2010

10:00 AM – 3:00 PM Eastern

Attendees:

Denise Roeder						ElectriCities

Bob Pierce							Duke Energy

Orvane Piper							Duke Energy

James Manning						NCEMC

Joey West							Progress Energy

Lee Adams							Progress Energy

Rich Wodyka    						Accenture

- ADMINISTRATIVE

- The June 15, 2010 PWG meeting minutes were approved with a modification regarding the wind study strawman.

- Rich Wodyka updated the group on the 6/18/10 OSC meeting.

- The 2010 Work Plan was reviewed.  The PWG has caught up and may be slightly ahead of schedule.

- The action item status was reviewed and updated – see attached.  Because of the volume of completed action items, the existing action item list will be archived and only the new action items will be carried forward.

- 2010 STUDY

- PEC and Duke reviewed their enhanced access and unscrubbed coal retirement case scenario screening results.  No unusual or unexpected results were identified on either system.  With modification of in-service dates for existing projects, the existing transmission system plans should be effective for meeting reliability requirements under these scenarios for the next 10 years.  The changes in in-service dates are relatively small.  The exceptions are the third 230 kV line between Lilesville and Rockingham and the McGuire 500/230 kV transformer in the enhanced access cases.  A third 230 kV line between Lilesville and Rockingham needs to be evaluated in the Cleveland County to CPLE 1000 MW case to relieve increased contingency loading on the existing Lilesville to Rockingham 230 kV lines.  The McGuire 500/230 kV transformer moves into year 2020 from outside the planning horizon for the SOCO to CPLE 1000 MW enhanced access scenario.  A reactor at McGuire would be a likely solution versus construction of a complete new 500/230 kV station.

ACTION ITEM:  Orvane Piper and Joey West to rerun the Cleveland County to CPLE 1000 MW enhanced access scenario to examine the impact of the third Lilesville to Rockingham 230 kV line.

- The Wind Study results were presented for both the 230 kV (S1) and 500 kV (S2) strawman scenarios.  Neither of the scenarios indicates the need for additional transmission infrastructure to transfer the energy across CPLE to Duke.  However, the S1 scenario indicates the needs for significant additional transmission infrastructure near the coast for the off peak wind case or required curtailment of wind generation for contingency conditions.  An evaluation needs to be done of the maximum amount of firm energy that can be delivered from the coast under the S1 scenario considering curtailment of wind with the modeled infrastructure.  The on-peak wind case may have a conservative error in the Duke interchange that would require re-run of the scenario, but is not expected to result in additional facilities being identified.  The S2 scenario indicates that no additional infrastructure would be required to accommodate the level of offshore wind modeled.  The modeled infrastructure is estimated to be ~ $1.2 B.

ACTION ITEM:  Joey West to evaluate the maximum amount of firm energy that can be delivered from the coast in the S1 scenario considering curtailment of wind with the modeled infrastructure.

ACTION ITEM:  Orvane Piper to check on peak wind model interchange and re-run screening if necessary.

- COLLABORATIVE PLAN UPDATE

The updated plan was reviewed and discussed.  Additional explanation should be provided for the changes that have been identified.

ACTION ITEM:  Joey West and Bob Pierce are to provide brief descriptions for the changes to the 2009 Collaborative Plan for posting with the updated plan.

- OTHER ITEMS

- Discussed TPL-001-1 drafting team work

- Discussed status of new FAC-013-2 standard on transfer capability in the planning horizon.

- Discussed FERC Technical Conference on reliability standards development.

- Discussed the status of SERC LTSG, SIRPP and EIPC work

ACTION ITEM LOG

| Action Item | Responsibility | Status |
| --- | --- | --- |
| Rerun the Cleveland County to CPLE 1000 MW enhanced access scenario to examine the impact of the third Lilesville to Rockingham 230 kV line. | Orvane Piper Joey West |  |
| Evaluate the maximum amount of firm energy that can be delivered from the coast in the S1 scenario considering curtailment of wind with the modeled infrastructure. | Joey West |  |
| Check on peak wind model interchange and re-run screening if necessary. | Orvane Piper |  |
| Provide brief descriptions for the changes to the 2009 Collaborative Plan for posting with the updated plan. | Joey West Bob Pierce |  |

ARCHIVED ACTION ITEM LOG (7/12/10)

| Action Item | Responsibility | Status |
| --- | --- | --- |
| Supply contact information for Kai to the PWG. | Mark Byrd | Complete |
| Supply contact information for Orvane to the PWG. | Bob Pierce | Complete |
| Develop an exact list of unscrubbed generation to be retired. | Bob Pierce | Complete |
| Develop an exact list of unscrubbed generation to be retired. | Lee Adams | Complete |
| Provide 2015S peak load information for determining load ratio share allocation of wind energy to each area. | Bob Pierce | Complete |
| Provide 2015S peak load information for determining load ratio share allocation of wind energy to each area. | Lee Adams | Complete |
| Determine time of day for maximum capacity factor for off shore wind. | Orvane Piper | Complete |
| Determine off peak load level to be studied based on information from Orvane on time of day for maximum off shore wind capacity factor. | Bob Pierce | Complete |
| Determine off peak load level to be studied based on information from Orvane on time of day for maximum off shore wind capacity factor. | Lee Adams | Complete |
| Develop a strawman representing the infrastructure associated with bringing the energy onshore. | Mark Byrd | Complete |
| Review the revised 2010 Study Scope document and submit any additional revisions by 1/11/10. | All PWG members | Complete |
| Contact Duke University graduate student to discuss 2010 Study. | Bob Pierce | Complete |
| Coordinate interchange for models. | Lee Adams Orvane Piper | Complete |
| PEC will evaluate the strawman to develop changes so that N-1 criteria are met. | Mark Byrd | Complete |
| Comment on the PEC strawman proposal. | All PWG members | Complete |
| Update the Work Plan to account for the Southern Power Enhanced Access Request. | Rich Wodyka Orvane Piper | Complete |
| Send the interchange tables to all PWG members. | Orvane Piper | Complete |
| Review the interchange table for accuracy. | All PWG members | Complete |
| Exchange load duration curve data and determine the specific load level in each area for modeling in the off peak case. | Mark Byrd Bob Pierce | Complete |
| Provide PEC models and contingency files to Orvane Piper for compiling joint models and contingency file. | Joey West | Complete |
| Begin screening of joint models. | Joey West Orvane Piper | Complete |
| Develop PEC TRM cases and provide to Orvane Piper for screening. | Joey West | Complete |
| Contact PJM for market dispatch information and idevs for update of MAPP and PATH projects which have been delayed. | James Manning | Complete |
| Send revised interchange tables to all PWG members for review. | Orvane Piper | Complete |
| Coordinate interchange for the off peak wind generation model and verify correct dispatch. | Joey West Orvane Piper James Manning Denise Roeder | Complete |
| Create off peak case. | Orvane Piper | Complete |
| Provide idevs for placing infrastructure identified in the strawman in the models. | Joey West | Complete |
| Create wind generation models and verify correct dispatch. | Joey West Orvane Piper | Complete |
| Evaluate the configuration at Pisgah, the facility ratings and the appropriate operating procedure following a bank failure. | Joey West Orvane Piper | Complete |
| Coordinate dispatch and finalize Enhanced Access Request cases. | Joey West Orvane Piper | Complete |